## Sheet1
| ViolationComment | TEAMCODE | FULLNAME
2 | REMOVE COMBUSTIBLES FROM AROUND BUILDING | HighRise | LISA KIMBALL
3 | PROVIDE A 911 BOX TO ENABLE ENTRY TO THE STRUCTURE THROUGH THE GATED AND PADLOCKED DRIVE, THE ENCLOSED ENTRY AT THE REAR OF THE BUILDING AND THE DOOR CONTAINED WITHIN THE SECURED GATE | HighRise | LISA KIMBALL
4 | INSPECTION OF THE BUILDING FOUND SEVERAL POINTS OF ENTRY (UNSECURED PLYWOOD REMOVED WITH THE AID OF A PHILLIPS SCREWDRIVER), CLOTHING, BEDDING AND A RECENTLY DATED NEWSPAPER INDICATING AN UNSAFE VACANT BUILDING - BUILDING MUST BE MORE SECURE AGAINST UNAUTHORIZED ENTRY AND HABITATION | HighRise | LISA KIMBALL
5 | NoData | HighRise | LISA KIMBALL
6 | NoData | HighRise | LISA KIMBALL
7 | THE USE OF LOCKING OR DECKING SCREWS TO SECURE PLYWOOD (AS OPPOSED TO PHILLIPS HEAD SCREWS) IS SUGGESTED TO INHIBIT ENTRY BY UNAUTHORIZED PERSONS INTO THE BUILDING | HighRise | LISA KIMBALL
8 | PLYWOOD SECURING AN OPENING ON THE NORTH SIDE OF BUILDING WAS REMOVED (INITIALLY DISCOVERED ON THE 14TH JANUARY 2018 AT 14:18) AND BUILDING WAS NOT SECURED TO UNAUTHORIZED ACCESS CREATING REASONABLE BELIEF THIS BUILDING WAS BREACHED AND THEREFORE UNSAFE | HighRise | LISA KIMBALL
9 | NoData | HighRise | LISA KIMBALL
10 | SCATTERED FURNISHINGS AND AN ABUNDANCE OF COMBUSTIBLE WASTE WERE FOUND PRIMARILY IN THE BASEMENT, 1ST, 2ND AND 3RD FLOORS - REMOVE ALL FURNISHINGS AND COMBUSTIBLES FROM ALL FLOORS OF THE BUILDING IMMEDIATELY | HighRise | LISA KIMBALL
11 | THE EXIT FROM THE CATWALK HAS BEEN ELIMINATED AND PERMANENTLY OBSTRUCTED WITH 2X4 BARRICADES FROM THE 1115 CONGRESS SIDE - A SAFE AND SECURE SOLUTION MUST BE EXPLORED WITH THE BUILDING DEPARTMENT | HighRise | LISA KIMBALL
12 | THE BUILDING AT THIS ADDRESS MUST CONFORM TO THE 2012 INTERNATIONAL FIRE CODE, CHAPTER 33 'FIRE SAFETY DURING CONSTRUCTION AND DEMOLITION' | HighRise | LISA KIMBALL
13 | NO EVIDENCE OF THE LAST INSPECTION OF THE EXTERIOR FIRE ESCAPE HAS BEEN PROVIDED | HighRise | LISA KIMBALL
14 | THE CATWALK ACCESS HAS BEEN OBSTRUCTED AT THE 1115 CONGRESS SIDE - AN ALTERNATIVE TO 2X4s PERMANENTLY SEALING OFF THE EGRESS WAY MUST BE FOUND TO ALLOW ACCESS WHILE ALSO PROVIDING SECURITY | HighRise | LISA KIMBALL
15 | CEILING TILES HAVE BEEN REMOVED THROUGHOUT THE BUILDING EXPOSING FRIABLE ASBESTOS WRAPPED PIPING, ASBESTOS LADEN TILES AND ALLOWING CABLES, WIRES, FLEXIBLE A/C DUCTING, ETC TO CREATE SAFETY AND HEATH HAZARDS FPM ON SITE HAVE NO KNOWLEDGE OF STATE REQUIRED O & M (ASBESTOS OPERATION AND MAINTENANCE) DOCUMENTATION | HighRise | LISA KIMBALL
16 | A SUSPECTED FLAMMABLE LIQUID WAS FOUND SEEPING FROM A BARREL IN THE BASEMENT - CLEAN UP AND REMOVE RESIDUAL LIQUID FROM THE BUILDING | HighRise | LISA KIMBALL
17 | NoData | HighRise | LISA KIMBALL
18 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE VACANT PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
19 | NoData | HighRise | LISA KIMBALL
20 | NoData | HighRise | LISA KIMBALL
21 | NoData | HighRise | LISA KIMBALL
22 | NoData | HighRise | LISA KIMBALL
23 | UNSPRINKLERED BUILDING - NO FIRE PROTECTION IN PLACE THE HOSE CABINETS HAVE BEEN REMOVED, PIPES HAVE BEEN SEVERED AND FIRE PUMPS (YELLOW TAGGED IN JANUARY 2006) TAKEN OUT OF SERVICE PRIOR TO COMBUSTIBLE MATERIALS AND DEBRIS BEING REMOVED FROM THE BUILDING | HighRise | LISA KIMBALL
24 | ALL PUMPS AND TANKS FROM THE FDC APPEAR TO HAVE OPEN CONNECTIONS AND VALVES; ALL HOSES AND CABINETS HAVE BEEN REMOVED LEAVING SEVERED PIPES WITHOUT CONNECTIONS AT THE WALL IN THE BASEMENT AND ALL STORIES THROUGHOUT THE BUILDING | HighRise | LISA KIMBALL
25 | NoData | HighRise | LISA KIMBALL
26 | NoData | HighRise | LISA KIMBALL
27 | THE STANDPIPE MAY NEED TO BE MAINTAINED AND OPERABLE PRIOR TO AND DURING DEMOLITION OF THE BUILDING FPM STATED BUILDING IS TO BE ABATED AND DEMOLISHED THIS SUMMER - PROVIDE A LETTER OF INTENT AND ACTION PLAN CONCERNING DEMOLITION | HighRise | LISA KIMBALL
28 | FDC IS STILL IN PLACE - STICKERED TO WARN FIREFIGHTING COMPANIES OF POSSIBLE IMPAIRMENTS OR INOPERATIVE SYSTEM | HighRise | LISA KIMBALL
29 | PLACARDS MUST REMAIN IN PLACE TO WARN THE HOUSTON FIRE DEPARTMENT OF THE UNUSABLE FDC AND SEVERED CONNECTIONS IN THE BUILDING | HighRise | LISA KIMBALL
30 | NoData | HighRise | LISA KIMBALL
31 | HOUSEKEEPING IS REQUIRED IN THE ELEVATOR ROOM | HighRise | LISA KIMBALL
32 | REPLACE MISSING DOOR IS REPLACED ON THE ELECTRICAL PANEL IN THE ELECTRICAL ROOM PROVIDE J BOX COVERS FOR OPEN BOXES IN THE ELEVATOR ROOM IN THE HOAR OFFICE | HighRise | LISA KIMBALL
33 | EMERGENCY EXIT SIGNS ARE OUT ON THE 8TH FLOOR (STAIR B, C & D), THE 7TH FLOOR (STAIR B, C & D), THE 6TH FLOOR (STAIR A, B, C & D), THE 5TH FLOOR (STAIR A, C & D), THE 4TH FLOOR (STAIR A, C & D), THE 3RD FLOOR (STAIR A, B & C), THE 2ND FLOOR (STAIR A, B & C) - CALL SERVICE COMPANY IMMEDIATELY TO REPAIR OR REPLACE COMPONENTS EMERGENCY EGRESS LIGHTING MUST BE TESTED - LIGHTS WILL NOT ILLUMINATE ON THE 4TH FLOOR (STAIR A, B & C), THE 3RD FLOOR (STAIR A, B & C) AND THE 2ND FLOOR (STAIR A, B &C) - CALL SERVICE COMPANY IMMEDIATELY TO REPAIR OR REPLACE COMPONENTS SEVERAL EXIT LIGHTS IN THE 1313 SPACE ARE NOT FUNCTIONING/ILLUMINATING AND NEED TO BE REPLACED/REPAIRED AN EXIT SIGN WAS REMOVED/IS MISSING FROM THE 2ND FLOOR NEXT TO THE ELECTRICAL/MECHANICAL ROOM AND MUST BE REPLACED | HighRise | LISA KIMBALL
34 | THE TANK IS YELLOW TAGGED AND PAST DUE FOR INSPECTION (27JUL15) - CALL SERVICE COMPANY IMMEDIATELY TO SERVICE AND CORRECT ANY DEFICIENCIES FIRE ALARM IN THE VACANT 1313 IS DISPLAYING 'TROUBLE' AND PAST DUE FOR INSPECTION (2016) | HighRise | LISA KIMBALL
35 | LOCATE AND IDENTIFY FIRE DEPARTMENT TEST CONNECTIONS | HighRise | LISA KIMBALL
36 | ENSURE THAT UL APPROVED RED CAN IN THE ELEVATOR ROOMS ARE EMPTIED DAILY | HighRise | LISA KIMBALL
37 | STAIRWELL SIGNS ARE MISSING AND NEED TO BE REPLACED FOR THE B STAIRWELL ON THE 7TH, 6TH, 5TH AND 4TH FLOORS | HighRise | LISA KIMBALL
38 | NoData | HighRise | LISA KIMBALL
39 | Facility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system must be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - N/A " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - PAST DUE; CONDUCTED MARCH 2015 " Fire Alarm System Test - Annual - REQUIRED; CONDUCTED 11/28/17 " Fire Extinguishers - Annual - REQUIRED; TESTED OCT 2017 " Fire Hoses - Annual REQUIRED; TESTED OCT 2017 " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 5 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - PAST DUE; YELLOW TAGGED 2012 " Boiler Permit - REQUIRED IF ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE COMPLIANCE WITHIN 60 CALENDAR DAYS. | HighRise | LISA KIMBALL
40 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
41 | REMOVE SAND BAGS AT THE TOP OF STAIR A ON THE 8TH FLOOR REMOVE TRASH CAN FROM STAIR A ON THE 8TH FLOOR - TRASH CANS MUST NOT BE PLACED INSIDE STAIRWELLS | HighRise | LISA KIMBALL
42 | SPRINKLERS MAY BE REQUIRED IN ALL ENCLOSED AREAS OF THE PARKING GARAGE - CONTACT YOUR SPRINKLER COMPANY NO SPRINKLERS FOUND IN THE HOAR OFFICE (CONNECTED TO 1313) OR PARKING GARAGE OFFICE | HighRise | LISA KIMBALL
43 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE ELECTRICAL ROOM | HighRise | LISA KIMBALL
44 | NoData | HighRise | LISA KIMBALL
45 | PERMITS THE INSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS: Key Box Permit Flammable and Combustible Permit Fire Alarm Permit - REQUIRED FOR GARAGE & 1313 MAIN; NONE FOUND ON SITE Elevator Operating Permit - REQUIRED FOR 4 TRAC & 1 HYDRO; NEEDS RENEWAL Boiler Permit Other - Assembly, Access Gates, Batteries, etc. Certificate of Occupancies Fire Depository Box / Key Boxes These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
46 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
47 | SUBMIT A LETTER TO THE FIRE MARSHALS OFFICE FROM A LICENSED SPRINKLER COMPANY DETAILING THE CURRENT PERCENTAGE OF SPRINKLER COVERAGE FOR THE BUILDING ADDRESSED - INCLUDE ANY DETAILS REGARDING PLANS FOR OBTAINING 100% COVERAGE IF THE TOTAL SQUARE FOOTAGE OF THE BUILDING IS NOT CURRENTLY EQUIPPED WITH AN AUTOMATIC SPRINKLER SYSTEM IN THE ACCORDANCE WITH THE HOUSTON FIRE CODE AND NFPA 13 SUBMIT THIS SIGNED LETTER AND A SIGNED LETTER OF INTENT (ATTACHED) TO THE FIRE INSPECTOR WITHIN 10 DAYS | HighRise | LISA KIMBALL
48 | REMOVE AND DISCONTINUE USE OF THE LOCKING BAR ON THE HOAR OFFICE | HighRise | LISA KIMBALL
49 | ALL ELECTRICAL CIRCUIT BREAKERS IN ELECTRICAL PANELS MUST BE CLEARLY AND CORRECTLY LABELED | HighRise | LISA KIMBALL
50 | SUPPLY KEYS FOR THE EXTERIOR DOORS, THE HOAR OFFICE SPACE, ELEVATOR ROOMS AND THE 1313 MAIN SPACE (AND LOCKED ROOMS WITHIN THIS SPACE) IN 911 KEY BOX THE 911 BOX FALCON LOCK WAS RUSTED SHUT; IT WAS PRIED OPEN AND SPRAYED WITH WD40. TREAT LOCK WITH WD40 TO ENSURE IT WILL CONTINUE TO RUST AND NEED A REPLACEMENT | HighRise | LISA KIMBALL
51 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
52 | THE FIRE ALARM IN THE 1313 SITE IS DISPLAYING "TROUBLES" AND WAS LAST INSPECTED IN 2016 - CALL A CERTIFIED ALARM COMPANY TO SERVICE AND CONDUCT ANNUAL INSPECTION | HighRise | LISA KIMBALL
53 | NoData | HighRise | LISA KIMBALL
54 | NoData | HighRise | LISA KIMBALL
55 | ALL FIRE EXTINGUISHERS MUST BE HUNG - NOT STORED ON THE FLOOR - HANG EXTINGUISHER IN THE ELEVATOR ROOM, THE HOAR OFFICE ELEVATOR ROOM AND IN THE MECHANICAL/ELECTRICAL ROOM IN THE 1313 SPACE | HighRise | LISA KIMBALL
56 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
57 | FIRE EXTINGUISHERS ARE REQUIRED IN ALL AREAS, LOCATIONS AND WITHIN DISTANCES REQUIRED BY THE CODE - CABINETS (MIDDLE) FOUND MISSING FIRE EXTINGUISHERS ON THE 4TH, 3RD AND 2ND FLOORS | HighRise | LISA KIMBALL
58 | SUPPLY ADDITIONAL ELEVATOR HOISTWAY DOOR KEY (TOTAL OF 2 NEEDED) INDEPENDENT SERVICE KEYS ARE NEEDED (AND TO BE HUNG OUTSIDE OF THE FIRE DEPOSITORY BOX) SUPPLY KEYS TO THE HOAR OFFICE SPACE, THE 1313 MAIN SPACE, AND LOCKED UTILITY ROOMS IN THE 1313 SPACE | HighRise | LISA KIMBALL
59 | NoData | HighRise | LISA KIMBALL
60 | REMOVE AND DISCONTINUE USE OF UNAPPROVED EXTENSION CORD IN THE OFFICE - ONLY UL APPROVED, SURGE PROTECTED CORDS ARE SAFE FOR TEMPORARY USE | HighRise | LISA KIMBALL
61 | NoData | HighRise | LISA KIMBALL
62 | NO LOCK OUT/ TAG OUT EQUIPTMENT WAS FORND IN THE ELEVATOR ROOMS; LOCK- OUT/TAG-OUT EQUIPMENT AND SETS MUST BE READILY ACCESSIBLE AND PROPERLY LABELED: PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS A MINIMUM TWO (2) LOCK-OUT/TAG-OUT SETS FOR 4 TO 6 ELEVATORS A MINIMUM THREE (3) LOCK-OUT/TAG-OUT SETS FOR 7 OR MORE ELEVATORS | HighRise | LISA KIMBALL
63 | NoData | HighRise | LISA KIMBALL
64 | ENGAGE THE SERVICES OF A FIRE PROTECTION ENGINEER OR A CERTIFIED SPRINKLER SERVICE COMPANY FOR ASSISTANCE IN THE CORRECT CALCULATION AND DETERMINATION OF THE CURRENT SPRINKLER COVERAGE OF THE HIGH-RISE GARAGE ADDRESSED | HighRise | LISA KIMBALL
65 | CABINETS CONTAINING FIRE FIGHTING EQUIPTMENT MUST INDICATE THE EQUIPTMENT CONTAINED THEREIN - "FIRE HOSE" AND/OR "FIRE EXTINGUISHER" - CHECK CABINETS ON THE 8TH, 6TH, 5TH, 4TH, 3RD AND 2ND FLOORS | HighRise | LISA KIMBALL
66 | NoData | HighRise | LISA KIMBALL
67 | NoData | HighRise | LISA KIMBALL
68 | NoData | HighRise | LISA KIMBALL
69 | PROVIDE A COVER PLATE FOR EXPOSED SOCKET IN THE MECHANICAL/ELECTICAL/ELEVATOR ROOM ON THE 10TH FLOOR | HighRise | LISA KIMBALL
70 | THE SUPPRESSION SYSTEM IS YELLOW TAGGED - A YELLOW TAG (5 YEAR TEST) WAS ISSUED JULY 17 AND MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
71 | LOCATE, IDENTIFY AND LABEL THE FIRE DEPARTMENT TEST CONNECTION ON THE ROOF | HighRise | LISA KIMBALL
72 | UPDATE THE MOBILITY IMPAIRED LIST IN THE FIRE DEPOSITORY BOX EVERY 6 MONTHS OR AS SOON AS CHANGES IN INFORMATION ARE REQUIRED | HighRise | LISA KIMBALL
73 | THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH | HighRise | LISA KIMBALL
74 | ENSURE THE LOCK-OUT/TAG-OUT EQUIPMENT ARE READILY ACCESSIBLE, PROPERLY LABELED AND STORED IN THE DESIGNATED LOCATION IN ALL ELEVATOR ROOMS: - PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS - A MINIMUM TWO (2) LOCK-OUT/TAG-OUT SETS FOR 4 TO 6 ELEVATORS - A MINIMUM THREE (3) LOCK-OUT/TAG-OUT SETS FOR 7 OR MORE ELEVATORS | HighRise | LISA KIMBALL
75 | NoData | HighRise | LISA KIMBALL
76 | ENSURE AT LEAST 18" OF CLEARANCE SPACE BETWEEN STORED OR SHELVED ITEMS AND THE SPRINKLER HEADS IN THE CAFETERIA CUPBOARD AND THROUGHOUT THE BUILDING CREATE A LINE OF DEMARCATION TO CLEARLY ESTABLISH THE SPACE OF AN 18" CLEARANCE FROM THE CEILING WITH TAPE OR PAINT IF ENCROACHMENT ON THE NECESSARY CEILING CLEARANCE IS A CHRONIC ISSUE - A VISUAL REMINDER WILL HELP ALLEVIATE THIS RECURRING VIOLATION | HighRise | LISA KIMBALL
77 | ALL FIRE EXTINGUISHERS MUST HAVE A CURRENT TAG INDICATING DATE OF LAST ANNUAL INSPECTION OR SERVICE/MAINTENANCE MOST EXTINGUISHERS WERE LAST INSPECTED AND TAGGED AUG 2016 EXTINGISHERS IN THE BASEMENT GARAGE, ELEVATOR ROOMS AND THE CAFETERIA WERE LAST INSPECTED AND TAGGED AUG 2015 | HighRise | LISA KIMBALL
78 | PROVIDE 5 SETS OF 'HIGH RISE SURVEY FORMS' IN THE BINDER OR 5 SETS IN 5 BINDERS | HighRise | LISA KIMBALL
79 | SUBMIT A LETTER TO THE FIRE MARSHALS OFFICE FROM A LICENSED SPRINKLER COMPANY DETAILING THE CURRENT PERCENTAGE OF SPRINKLER COVERAGE FOR THE BUILDING ADDRESSED - INCLUDE ANY DETAILS REGARDING PLANS FOR OBTAINING 100%COVERAGE IF THE TOTAL SQUARE FOOTAGE OF THE BUILDING IS NOT CURRENTLY EQUIPPED WITH AN AUTOMATIC SPRINKLER SYSTEMIN THE ACCORDANCE WITH THE HOUSTON FIRE CODE AND NFPA 13 SUBMIT THIS SIGNED LETTER AND A SIGNED LETTER OF INTENT (ATTATCHED) TO THE FIRE INSPECTOR WITHIN 10 DAYS | HighRise | LISA KIMBALL
80 | NoData | HighRise | LISA KIMBALL
81 | SUPPLY A TOTAL OF 6 RED FIREFIGHTER PHONES TO BE STORED IN THE CABINET - ONLY 3 PRESENT - ENSURE THAT ALL PHONES ARE TESTED AND LOCATION OF CALL IS CORRECTLY DISPLAYED ON FIRE ALARM PANEL | HighRise | LISA KIMBALL
82 | THE CLASS K EXTINGUISHER IN THE CAFETERIA NEEDS AN ANNUAL INSPECTION | HighRise | LISA KIMBALL
83 | THE FACILITY MUST PROVIDE INSPECTOR WITH THE FOLLOWING REPORT DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF A CURRENT REPORT REVEALS A TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE INSPECTOR SIGNING OFF ON THE SAFETY SURVEY. IN ADDITION TO THE TEST REPORTS, A BRIEF LETTER MUST BE PROVIDED FROM THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANY STATING: TESTING OR INSPECTION WAS COMPLETED IF THE SYSTEM IS ACCEPTABLE, RED TAGGED, YELLOW TAGGED, PASSED OR FAILED DO NOT PROVIDE BILLING INVOICES OR CHECKS PAID LONG TERM DEFICIENCIES WILL REQUIRE A LETTER OF INTENT WITH A TIMELINE ARRIVED AT AFTER CONSULTATION WITH THE FIRE INSPECTOR. MANAGEMENT SHALL OBTAIN AN ACCEPTABILITY LETTER FOR 3-5 YEAR TESTS THAT DO NOT HAVE A LETTER CURRENTLY ON FILE: " Certificate of Occupancy: Core of Building C of O only " Active Fire Permits: Up to date and paid. " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation. " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards. " Fire Alarm Permit (current and paid) " Sprinkler Percentage Letter and Form (provided in email attachment) " Building System Test Documentation (LSB # 2) " Electronic Locks- Semi Annual " Sprinkler System- Annual " Fire Alarm System Test- Annual " Fire Extinguishers- Annual " Fire Hoses- Annual " Fire Pumps Flow Test- Annual " Emergency Power & Lighting- Annual " Generator Test (ATS)- Annual " Fire Alarm Audibility Test- 3 Year " Fire Hose Pressure Test- 3 year " Fire Dampers- 4 Year " Fire Alarm Sensitivity- 5 Year " FDC Test (Building & Garage)- 5 Year " PRV / PRD Test- 5 Year " Stair pressurization Test- 5 Year " Standpipe System- 5 Year " Water Supply Tank Inspection- 5 Year " Boiler Permit " Elevator Permit- Annual " Dry Partial or Full Trip Test " Gas Test- 5 Year COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
84 | 5 YEAR TEST ON SUPPRESION SYSTEM IS NEEDED | HighRise | LISA KIMBALL
85 | THE MOBILITY IMPAIRED LIST WAS LAST UPDATED ON 04/14 - THIS LIST MUST BE UPDATED EVERY 6 MONTHS LABEL ALL KEY SETS IN COLORS AND TITLES IN ACCORDANCE WITH LSB STANDARD 6 ONLY 3 PHONES WERE PROVIDED IN THE FDB - ENSURE A COMPLETE SET OF PHONES IS AVAILABLE AND ALL PHONES AND JACKS ARE TESTED AND FUNCTIONAL (CAPABLE OF SENDING AND RECIEVING MESSAGES AND CORRECTLY IDENTIFY LOCATION OF CALL ON THE PANEL) REVIEW LSB 6 AND ENSURE ALL KEYS ARE SUPPLIED AND CORRECTLY LABELED | HighRise | LISA KIMBALL
86 | NoData | HighRise | LISA KIMBALL
87 | NoData | HighRise | LISA KIMBALL
88 | ALL FIRE EXTINGUISHERS MUST BE HUNG AT LEAST 4 INCHES FROM THE FLOOR (AT THE BASE) BUT NO HIGHER THAN 5 FEET (AT THE TOP) | HighRise | LISA KIMBALL
89 | THE LOCATION OF ALL MECHANICAL ROOMS AND ELEVATOR ROOMS MUST BE IDENTIFIED AND LABELED AS SUCH | HighRise | LISA KIMBALL
90 | SPRINKLER ORDINANCE CHECK POINT PROCEDURES As part of our scheduled high rise inspections, we will implement the following procedures by inquiring management as to the percentage of sprinkler coverage in their building in accordance with City of Houston, High Rise Sprinkler Ordinance No. 2005-1267, Appendix J, in particular our upcoming compliance check point no. (2): STEP 1 If management indicates that they have accomplished less than 100% of the floors, then no action on our part will be required, other than informing and encouraging them to keep diligently working on meeting their approaching 2018 check point STEP 2 If management has accomplished at least 50% of their floors, they can check the appropriate box, completely fill out and sign, our "Sprinkler Ordinance Check Points" form. If management has accomplished 100% of their floors (total square footage), they can check the appropriate box, completely fill out and sign, our "Sprinkler Ordinance Check Points" form. STEP 3 In order for the fire inspector to validate and confirm that either the 50% check point or the 100% check point has been met, management must provide an acceptable "Letter of Confirmation" from their building's fire protection contractor. The fire protection contractor's "Letter of Confirmation" will need to include all of the following information: " Written on their company's letterhead " addressed to the building owner/representative " the body of the letter shall state that either: " 50% of the floors are sprinklered per NFPA 13 and indicate the exact floors, or total square footage of the building is sprinklered per NFPA 13 " provide the building address " printed name and signature of authorized person confirming letter Once these two documents are received by our office, the appropriate status on the building will be recorded into our files. These procedures are being implemented as part of maintaining compliance with the Compliance Check Points Schedule, in accordance with Appendix J. THE SPRINKLER ORDINANCE CHECK POINTS LETTER CAN BE FOUND IN THE ATTACHMENTS OF THE ORIGINAL APPOINTMENT EMAIL LETTER Owner / Property Manager / Representative shall fill out the "Sprinkler Ordinance Check Points" form and the form shall be submitted to the Houston Fire Marshal's Office within 7 business days of receiving this notice Owner / Property Manager / Representative shall submit a Letter of Confirmation to the Houston Fire Marshal's Office, authored within the year 2017, which will be provided by a licensed sprinkler company, stating the current percentage and the exact number of sprinklered floors An Action Plan shall be submitted within 7 business days to the Houston Fire Marshal's Office. The Action Plan shall detail the time line of sprinkler installation stages, installation details regarding specific floors and percentages, target dates, etc. The Action Plan shall be clear and readable, subject to approval by the Houston Fire Marshal's Office The Owner / Property Manager / Representative is subject to a Re- inspection Fee every 7th business day for failure of submitting the three aforementioned items as prescribed herein COMPLIANCE WITHIN 7 DAYS | HighRise | LISA KIMBALL
91 | PERMITS WHICH HAVE BEEN ISSUED AND/OR REQUIRED COUD BE ANY OR ALL OF THE FOLLOWING: " Certificates of Occupancy - REQUIRED " Key Box Permit - EXPIRED 14JUN13 " Fire Depository Box Permit - EXPIRED 14JUN13 & H3 EXPIRED 31MAR17 " Flammable and Combustibles Permit - EXPIRED 6APR17 " Fire Alarm Permit - REQUIRED " Elevator Operating Permit - REQUIRED " Boiler Permit " Assembly - EXPIRED 06APR17 Other: Access Gates, Batteries, etc. THIS IS A PARTIAL LIST OF PERMITS OBTAINED THROUGH THE HOUSTON PERMITTING CENTER. PRESENT ALL PERMITS WHICH APPLY TO THE FACILITY ADDRESS LISTED ON NOTICE COMPLIANCE WITHIN 60 CALENDAR DAYS. | HighRise | LISA KIMBALL
92 | ENGAGE THE SERVICES OF A FIRE PROTECTION ENGINEER OR A CERTIFIED SPRINKLER SERVICE COMPANY FOR ASSISTANCE IN THE CORRECT CALCULATION AND DETERMINATION OF SPRINKLER COVERAGE OF THE HIGH-RISE BUILDING | HighRise | LISA KIMBALL
93 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS | HighRise | LISA KIMBALL
94 | EMERGENCY EXIT SIGNS ARE OUT ABOVE THE FRONT ENTRANCE DOORS - CALL SERVICE COMPANY IMMEDIATELY TO TEST, REPAIR OR REPLACE COMPONENTS PROVIDE EVIDENCE OF ANNUAL TESTING OF THE EMERGENCY ILLUMINATION AND ALL EMERGENCY EXIT LIGHTS OR MOST RECENT SERVICE OR REPAIR AND MAINTAIN ON SITE AT ALL TIMES | HighRise | LISA KIMBALL
95 | REVIEW LEGEND CARD - ONLY ONE LAMINATED CARD REQUIRED | HighRise | LISA KIMBALL
96 | NoData | HighRise | LISA KIMBALL
97 | FIRE EXTINGUISHERS IN THE ELEVATOR ROOMS MUST BE HUNG - NOT STORED ON THE FLOOR | HighRise | LISA KIMBALL
98 | VENT HOODS MUST BE CLEANED AT TIMELY INTERVALS - ALL CLEANINGS MUST BE RECORDED AND DOCUMENTS KEPT ON SITE - THE VENT HOOD WAS SCHEDULED TO BE CLEANED JUNE 2017 | HighRise | LISA KIMBALL
99 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE ELEVATOR ROOMS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
100 | PROVIDE UL APPROVED OILY RAG CANS IN ELEVATOR ROOMS | HighRise | LISA KIMBALL
101 | THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
102 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
103 | PROVIDE EVIDENCE OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP THIS INFORMATION ON SITE PROVIDE DOCUMENTATION OF ELEVATOR INSPECTION AND PERMIT - KEEP POSTED ON SITE WITH ALL OTHER PERMITS, WITHIN THE ELEVATOR CAR OR WITHIN 10 FEET OF THE CALL BUTTONS | HighRise | LISA KIMBALL
104 | PROVIDE A COVER FOR OPEN JUNCTION BOX IN THE MECHANICAL ROOM ON THE 2ND FLOOR | HighRise | LISA KIMBALL
105 | EMERGENCY EXIT SIGNS ARE OUT NEAR SUITE 1561 (LIGHT #028) AND 1534 (LIGHT #025) - CALL SERVICE COMPANY IMMEDIATELY TO REPAIR OR REPLACE COMPONENTS EMERGENCY EGRESS LIGHTING MUST BE TESTED - CALL SERVICE COMPANY IMMEDIATELY TO TEST AND REPAIR OR REPLACE NON-FUNCTIONING COMPONENTS PROVIDE EVIDENCE OF ANNUAL TESTING OF THE EMERGENCY ILLUMINATION AND ALL EMERGENCY EXIT LIGHTS OR MOST RECENT SERVICE OR REPAIR AND MAINTAIN ON SITE AT ALL TIMES | HighRise | LISA KIMBALL
106 | A YELLOW TAG WAS FOUND ON THE STAIR B RISER AND ON A TAMPER - ENSURE THAT BOTH SYSTEMS ARE REPAIRED AND RETAGGED | HighRise | LISA KIMBALL
107 | THE TEST CONNECTION ON THE ROOF MUST BE LABELED | HighRise | LISA KIMBALL
108 | STAIR C SIGN ON THE 15TH FLOOR IS MISSING AND SHOULD BE REPLACED | HighRise | LISA KIMBALL
109 | Facility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system must be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only " Active Fire Permits: Up to date and Paid. " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation. " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards. " Fire Alarm Permit - Annual " Sprinkler Percentage Letter and Form (included in report) " Electronic Locks -Semi Annual " Sprinkler System - Annual " Fire Alarm System Test - Annual " Fire Extinguishers - Annual " Fire Hoses - Annual " Fire Pumps Flow Test - Annual " Emergency Power & Lighting - Annual " Generator Test (ATS) - Annual " Fire Alarm Audibility Test - 3 Year " Fire Hose Pressure Test - 3 year " Fire Dampers - 4 Year " Fire Alarm Sensitivity - 5 Year " FDC Test (Bldg. & Garage) - 5 Year " PRV / PRD Test - 5 Year " Stair pressurization Test - 5 Year " Standpipe System - 5 Year " Water Supply Tank Inspection - 5 Year " Boiler Permit " Elevator Permit - Annual " Dry Partial or Full Trip Test " Gas Test - 5 Year COMPLIANCE WITHIN 60 CALENDAR DAYS. | HighRise | LISA KIMBALL
110 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
111 | REMOVE AND DISCONTINUE STORAGE IN EXIT ACCESSES, EXITS OR EXIT DISCHARGES - DISCARDED BOXES FOUND BLOCKING STAIR C EXIT ON THE 15TH FLOOR - KEEP ALL OF THESE AREAS FREE FROM OBSTRUCTIONS AT ALL TIMES THE BUILDING IS OCCUPIED | HighRise | LISA KIMBALL
112 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN UTILITY ROOMS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR - COVERS WHERE MISSING IN THE GENERATOR ROOM | HighRise | LISA KIMBALL
113 | POST THE CERTIFICATE OF OCCUPANCY AND ALL REQUIRED PERMITS (f7 AND k1) IN THE FIRE ALARM ROOM | HighRise | LISA KIMBALL
114 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
115 | ENSURE ALL KEYS IN 911 KEY BOX ARE CURRENT | HighRise | LISA KIMBALL
116 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
117 | LABEL RISER ROOMS ON EACH FLOOR (NEXT TO STAIR C) ON ALL LEVELS OF THE GARAGE | HighRise | LISA KIMBALL
118 | REVIEW LSB #2 SECTION 2.5.4.3 TO REVISE THE FDC SIGN WITH NECESSARY CORRECTIONS | HighRise | LISA KIMBALL
119 | NoData | HighRise | LISA KIMBALL
120 | ALL FIRE EXTINGUISHERS (ONE LOCATED ON THE FLOOR OF THE ELEVATOR/MECHANICAL ROOM) MUST BE HUNG AND NOT STORED ON THE FLOOR | HighRise | LISA KIMBALL
121 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
122 | PROVIDE ACCESS TO THE MECHANICAL ROOM ON THE ROOF - THE KEY ON THE FDB KEY RING WOULD NOT ALLOW ACCESS READ THROUGH LSB #6 AND SUPPLY ALL MISSING COMPONENTS OF THE FIRE DEPOSITORY BOX INCLUDING: -One complete binder with all necessary tabs and contents -5 copies of Survey -Supplemental Information sheet -Mobility Impaired list, dated (updated every six months) -Elevator operating instructions -Elevator Diagram showing required information -Elevator Hoist way Door Keys / Tools (min. 2 of each type) -Minimum of 3 maps, identifying equipment, per Standard -One 8x11 inch laminated Legend Card -Independent Service Keys HFS A2.3.3 / Tag outside FD Box. -Emergency Stop Keys -properly label and with quick release | HighRise | LISA KIMBALL
123 | ENSURE ALL FIRE PHONES ARE PROVIDED IN THEIR CRADLES (ONLY 2 PRESENT) | HighRise | LISA KIMBALL
124 | ENSURE A 36" CLEARANCE BETWEEN COMBUSTIBLES AND ALL HEAT PRODUCING DEVICES IN THE STORAGE/BOOKS/ARCHIVE ROOM | HighRise | LISA KIMBALL
125 | THE FIRE DEPARTMENT CONNECTION MUST BE IDENTIFIED AND SUPPLIED WITH A SIGN CONTAINING ALL SYSTEM INFORMATION AND PHYSICAL DETAILS AS PRESCIBED BY THE FIRE CODE | HighRise | LISA KIMBALL
126 | RE-INSPECTION FEES OR CITATIONS WILL ACCRUE AND IMPAIRMENT PLACARDS WILL BE POSTED FOR CONTINUED NON-COMPLIANCE OF APPENDIX J PAST THE DEADLINE OF DECEMBER 31ST, 2017 A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
127 | THE CERTIFICATE OF OCCUPANCY AND ALL REQUIRED PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUILDING AT ALL TIMES | HighRise | LISA KIMBALL
128 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION SPRINKLER ORDINANCE CHECK POINT PROCEDURES As part of our scheduled high rise inspections, we will implement the following procedures by inquiring about the percentage of sprinkler coverage in the building in accordance with City of Houston, High Rise Sprinkler Ordinance No. 2005-1267, Appendix J. STEP 1 If management indicates that they have accomplished 50% of the floors, then no action on our part will be required, other than informing and encouraging them to keep diligently working on meeting the December 31st, 2017 check point. STEP 2 If management has accomplished at least 50% of their floors, they can check the appropriate box, completely fill out and sign the "Sprinkler Ordinance Check Points" form. If management has accomplished 100% of their floors (total square footage), then check the appropriate box, completely fill out and sign the "Sprinkler Ordinance Check Points" form. STEP 3 In order to validate and confirm that either the 50% check point or the 100% check point has been met, management must provide an acceptable "Letter of Confirmation" from the building's fire protection contractor which MUST INCLUDE ALL OF THE FOLLOWING INFORMATION: " Written on their company's letterhead " addressed to the building owner/representative " the body of the letter shall state that either: " the CURRENT percentage of floors sprinklered per NFPA 13 and indicate the exact floors, or total square footage of the building which has sprinkler coverage per NFPA 13 " provide the building address " printed name and signature of authorized person confirming letter Once these two documents are received by our office, the appropriate status on the building will be recorded into our files. THE SPRINKLER ORDINANCE CHECK POINTS LETTER CAN BE FOUND IN THE ATTACHMENTS OF THE ORIGINAL APPOINTMENT EMAIL LETTER (unless signed during delivery of this report). Owner / Property Manager / Representative shall fill out the "Sprinkler Ordinance Check Points" form and the form shall be submitted to the Houston Fire Marshal's Office within 7 business days of receiving this notice Owner / Property Manager / Representative shall submit a Letter of Confirmation to the Houston Fire Marshal's Office, authored within the year 2017, which will be provided by a licensed sprinkler company, stating the current percentage and the exact number of sprinklered floors If the building has less than 100% sprinkler coverage, an Action Plan shall be submitted within 7 business days to the Houston Fire Marshal's Office. The Action Plan shall detail the time line of sprinkler installation stages, installation details regarding specific floors and percentages, target dates, etc. The Action Plan shall be clear and readable, subject to approval by the Houston Fire Marshal's Office The Owner / Property Manager / Representative is subject to a Re- inspection Fee every 7th business day for failure of submitting the two required items as prescribed herein COMPLIANCE WITHIN 10 BUSINESS DAYS | HighRise | LISA KIMBALL
129 | THE RISER/STANDPIPE ANNUAL INSPECTION IS PAST DUE (CONDUCTED SEPTEMBER 2011) AND REQUIRES AN INSPECTION THE 5 YEAR INSPECTION IS PAST DUE (CONDUCTED IN 2010) AND IS REQUIRED HOSE TEST (CONDUCTED 2016) IS REQUIRED FIRE EXTINGUISHERS ARE PAST DUE FOR INSPECTION (CONDUCTED 2016) | HighRise | LISA KIMBALL
130 | ENSURE ALL FIRE EXTINGUISHERS ARE NOT MISSING FROM DESIGNATED/MARKED LOCATIONS | HighRise | LISA KIMBALL
131 | ENSURE ALL EMPLOYEES HAVE HAD EVACUATION TRAINING | HighRise | LISA KIMBALL
132 | NoData | HighRise | LISA KIMBALL
133 | THE LOCK-OUT/TAG-OUT EQUIPMENT AND SETS MUST BE READILY ACCESSIBLE AND PROPERLY LABELED PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS A MINIMUM TWO (2) LOCK-OUT/TAG-OUT SETS FOR 4 TO 6 ELEVATORS A MINIMUM THREE (3) LOCK-OUT/TAG-OUT SETS FOR 7 OR MORE ELEVATORS | HighRise | LISA KIMBALL
134 | MAG LOCKS ON THE FRONT DOORS MUST BE TESTED, INSPECTED, STICKERED (BY THE BUILDING DEPARTMENT), MAINTAINED AND FULLY/PROPERLY FUNCTIONING | HighRise | LISA KIMBALL
135 | NoData | HighRise | LISA KIMBALL
136 | OBTAIN ALL REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER THE CERTIFICATE OF OCCUPANCY WAS LOCATED ON HFDs ILMS RECORD - OBTAIN CERTIFICATE OF OCCUPANCY FROM THE HOUSTON PERMITTING CENTER TO POST ON SITE THE FIRE ALARM PERMIT AND KEY BOX (K1) PERMIT HAVE EXPIRED - RENEW PERMITS ASSEMBLY PERMITS ARE REQUIRED FOR EACH COURTROOM - APPLY AND OBTAIN PERMITS FROM THE HOUSTON PERMITTING CENTER | HighRise | LISA KIMBALL
137 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
138 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - EXIT LIGHTS WERE NON-OPERABLE ON THE ROOF AND AT THE FRIONT ENTRANCE | HighRise | LISA KIMBALL
139 | SUBMIT A LETTER TO THE FIRE MARSHALS OFFICE FROM A LICENSED SPRINKLER COMPANY DETAILING THE CURRENT PERCENTAGE OF SPRINKLER COVERAGE FOR THE BUILDING ADDRESSED - INCLUDE ANY DETAILS REGARDING PLANS FOR OBTAINING 100% COVERAGE IF THE TOTAL SQUARE FOOTAGE OF THE BUILDING IS NOT CURRENTLY EQUIPPED WITH AN AUTOMATIC SPRINKLER SYSTEM IN THE ACCORDANCE WITH THE HOUSTON FIRE CODE AND NFPA 13 SUBMIT THIS SIGNED LETTER AND A SIGNED LETTER OF INTENT (ATTACHED) TO THE FIRE INSPECTOR WITHIN 10 DAYS | HighRise | LISA KIMBALL
140 | NoData | HighRise | LISA KIMBALL
141 | NoData | HighRise | LISA KIMBALL
142 | NoData | HighRise | LISA KIMBALL
143 | NoData | HighRise | LISA KIMBALL
144 | LOCATE AND IDENTIFY FIRE DEPARTMENT TEST CONNECTIONS | HighRise | LISA KIMBALL
145 | ALL ELECTRICAL CIRCUIT BREAKERS IN ELECTRICAL PANELS MUST BE CLEARLY AND CORRECTLY LABELED THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH SUGGESTION: LABEL AND SECURE OR CAGE MASTER LIGHT SWITCH ON 4TH FLOOR | HighRise | LISA KIMBALL
146 | BUILDING IS NOT COMPLIANT WITH APPENDIX J - TRAIN ALL EMPLOYEES ON FIRE PREVENTION, FIRE SAFETY AND EVACUATION | HighRise | LISA KIMBALL
147 | PROVIDE YOUR OWN "TEMPORARY FIRE WATCH" SIGN AND COMPLETE FIRE WATCH ASSIGNMENT AGREEMENT | HighRise | LISA KIMBALL
148 | BUILDING IS NOT IN COMPLIANCE WITH THE 50% SPRINKLER ORDINANCE (APPROXIMATELY 10% COVERAGE) - COMPLY WITH OBLIGATORY FIRE WATCH AND COMPLETE A 'FIRE WATCH ASSIGNMENT AGGREEMENT' AN INTERVENTION FORM HAS BEEN COMPLETED AND HAS BEEN PROCESSED UP THE CHAIN OF COMMAND TO THE FIRE MARSHAL - TO COMPLY WITH A FIRE WATCH CONDUCTED BY THE HCFMO, A LIST AND DETAILED SCHEDULE MUST BE PROVIDED OF FIRE WATCH DETAIL | HighRise | LISA KIMBALL
149 | PROVIDE DOCUMENTATION OF ELEVATOR INSPECTION AND PERMIT - KEEP POSTED ON SITE WITH ALL OTHER PERMITS, WITHIN THE ELEVATOR CAR OR WITHIN 10 FEET OF THE CALL BUTTONS | HighRise | LISA KIMBALL
150 | FIRE PUMPS (TESTED 2015) REQUIRE AN ANNUAL INSPECTION | HighRise | LISA KIMBALL
151 | NoData | HighRise | LISA KIMBALL
152 | Facility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only " Active Fire Permits: Up to date and Paid - K1, A4 " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation. " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards. " Fire Alarm Permit - Annual " Sprinkler Percentage Letter and Form " Electronic Locks - Semi Annual " Sprinkler System - Annual " Fire Alarm System Test - Annual " Fire Extinguishers - Annual " Fire Hoses - Annual " Fire Pumps Flow Test - Annual " Emergency Power & Lighting - Annual " Generator Test (ATS) - Annual " Fire Alarm Audibility Test - 3 Year " Fire Hose Pressure Test - 3 year " Fire Dampers - 4 Year " Fire Alarm Sensitivity - 5 Year " FDC Test (Bldg. & Garage) - 5 Year " PRV / PRD Test - 5 Year " Stair pressurization Test - 5 Year " Standpipe System - 5 Year " Water Supply Tank Inspection - 5 Year " Boiler Permit " Elevator Permit - Annual " Dry Partial or Full Trip Test " Gas Test - 5 Year COMPLIANCE WITHIN 60 CALENDAR DAYS. | HighRise | LISA KIMBALL
153 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN UTILITY ROOMS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
154 | THE TEST CONNECTION ON THE ROOF MUST BE LABELED UPDATE FDC SIGN - IT MUST ALSO INDICATE ADDRESS AND SUITES OR WHICH FLOORS/PORTION OF BUILDING ARE SERVED BY THE FIRE DEPARTMENT CONNECTION - REFER TO LSB #2 | HighRise | LISA KIMBALL
155 | ENFORCE ALL DETAILS PERTAINING TO RESPONSIBILITES ASSOCIATED WITH A FIRE WATCH | HighRise | LISA KIMBALL
156 | ENGAGE THE SERVICES OF A FIRE PROTECTION ENGINEER OR A CERTIFIED SPRINKLER SERVICE COMPANY FOR ASSISTANCE IN THE CORRECT CALCULATION AND DETERMINATION OF THE CURRENT SPRINKLER COVERAGE OF THE HIGH-RISE BUILDING ADDRESSED | HighRise | LISA KIMBALL
157 | PROVIDE DOCUMENTATION OF ELEVATOR INSPECTION AND PERMIT - KEEP POSTED ON SITE WITH ALL OTHER PERMITS, WITHIN THE ELEVATOR CAR OR WITHIN 10 FEET OF THE CALL BUTTONS | HighRise | LISA KIMBALL
158 | PROVIDE UL APPROVED OILY RAG CANS IN ELEVATOR ROOMS | HighRise | LISA KIMBALL
159 | NoData | HighRise | LISA KIMBALL
160 | THE EXTERIOR DOOR WHICH ALLOWS ACCESS TO THE ELEVATOR ROOM IS LOCKED AND NO KEY IS NOT AVAILABLE ON SITE - PROVIDE A KEY FOR EMERGENCY ACCESS | HighRise | LISA KIMBALL
161 | THE FACILITY MUST PROVIDE INSPECTOR WITH THE FOLLOWING REPORT DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF A CURRENT REPORT REVEALS A TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE INSPECTOR SIGNING OFF ON THE SAFETY SURVEY. IN ADDITION TO THE TEST REPORTS, A BRIEF LETTER MUST BE PROVIDED FROM THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANY STATING: TESTING OR INSPECTION WAS COMPLETED IF THE SYSTEM IS ACCEPTABLE, RED TAGGED, YELLOW TAGGED, PASSED OR FAILED DO NOT PROVIDE BILLING INVOICES OR CHECKS PAID LONG TERM DEFICIENCIES WILL REQUIRE A LETTER OF INTENT WITH A TIMELINE ARRIVED AT AFTER CONSULTATION WITH THE FIRE INSPECTOR. MANAGEMENT SHALL OBTAIN AN ACCEPTABILITY LETTER FOR 3-5 YEAR TESTS THAT DO NOT HAVE A LETTER CURRENTLY ON FILE: -Certificate of Occupancy: Core of Building C of O only -Active Fire Permits: Up to date and paid. -Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation. -Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards. -Fire Alarm Permit (current and paid) -Sprinkler Percentage Letter and Form (provided in email attachment) -Building System Test Documentation (LSB # 2) -Electronic Locks-Semi Annual -Sprinkler System- Annual -Fire Alarm System Test- Annual -Fire Extinguishers- Annual -Fire Hoses- Annual -Fire Pumps Flow Test- Annual -Emergency Power & Lighting- Annual -Generator Test (ATS)- Annual -Fire Alarm Audibility Test- 3 Year -Fire Hose Pressure Test- 3 year -Fire Dampers- 4 Year -Fire Alarm Sensitivity- 5 Year -FDC Test (Building & Garage)- 5 Year -PRV / PRD Test- 5 Year -Stair pressurization Test- 5 Year -Standpipe System- 5 Year -Water Supply Tank Inspection- 5 Year -Boiler Permit -Elevator Permit- Annual -Dry Partial or Full Trip Test -Gas Test- 5 Year COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
162 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS | HighRise | LISA KIMBALL
163 | ALL FIRE EXTINGUISHERS MUST BE HUNG - NOT STORED ON THE FLOOR | HighRise | LISA KIMBALL
164 | NO FIRE DEPOSITORY BOX FOUND ON SITE - SUPPLY A FIRE DEPOSITORY BOX IN THE GARAGE OFFICE OR IN THE FIRE COMMAND ROOM REVIEW LSB 6 AND ENSURE ALL KEYS, DOCUMENTS, INFORMATION, ETC. ARE SUPPLIED AND CORRECTLY LABELED | HighRise | LISA KIMBALL
165 | ALL ELEVATOR CAR NUMBERS MUST BE POSTED IN ACCORDANCE WITH THE FIRE CODE | HighRise | LISA KIMBALL
166 | ALL FIRE EXTINGUISHERS MUST HAVE A CURRENT TAG INDICATING DATE OF LAST ANNUAL INSPECTION OR SERVICE/MAINTENANCE - EXTINGUISHERS WERE LAST INSPECTED AND TAGGED IN JUNE AND AUGUST 2016 EXTINGUISHER IN STORAGE AREA ON THE 12TH FLOOR WAS LAST INSPECTED IN MAY 2014 - ENSURE ALL FIRE EXTINGUISHERS ON SITE ARE INSPECTED AND NOT OVERLOOKED FOR ANNUAL INSPECTION | HighRise | LISA KIMBALL
167 | NoData | HighRise | LISA KIMBALL
168 | NoData | HighRise | LISA KIMBALL
169 | ALL ELECTRICAL CIRCUIT BREAKERS IN ELECTRICAL PANELS MUST BE CLEARLY AND CORRECTLY LABELED THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH | HighRise | LISA KIMBALL
170 | CERTIFICATE OF OCCUPANCY IS POSTED IN THE OFFICE POST 911 BOX/KNOX BOX PERMIT, FIRE DEPOSITORY BOX PERMIT AND FUEL PERMIT (IF LIQUID FUELED GENERATOR IS ON SITE) IN THE PARKING GARAGE OFFICE OR IN THE FIRE COMMAND ROOM | HighRise | LISA KIMBALL
171 | EMERGENCY EXIT SIGNS ARE OUT IN THE ELEVATOR LOBBY - CALL SERVICE COMPANY IMMEDIATELY TO REPAIR OR REPLACE COMPONENTS PROVIDE EVIDENCE OF ANNUAL TESTING OF THE EMERGENCY ILLUMINATION AND ALL EMERGENCY EXIT LIGHTS OR MOST RECENT SERVICE OR REPAIR AND MAINTAIN ON SITE AT ALL TIMES | HighRise | LISA KIMBALL
172 | ALL OF THE ELEVATOR'S DISCONNECT SWITCHES MUST BE CLEARLY LABELED | HighRise | LISA KIMBALL
173 | NoData | HighRise | LISA KIMBALL
174 | HOSES IN CABINETS NEAR R102 AND R116 WERE LAST INSPECTED AND TAGGED IN MAY 2015 HOSE CABINET DOOR HANDLE IS MISSING ON A HOSE CABINET IN THE BASEMENT AND MUST BE REPAIRED TO BE FUNCTIONAL | HighRise | LISA KIMBALL
175 | ENSURE ALL INFORMATION IS INCLUDED AND CORRECT ON THE FDC | HighRise | LISA KIMBALL
176 | NoData | HighRise | LISA KIMBALL
177 | MAG LOCKS MUST BE TESTED, INSPECTED, MAINTAINED AND FULLY/PROPERLY FUNCTIONING | HighRise | LISA KIMBALL
178 | PROVIDE A FIRE EXTINGUISHER FOR THE PARKING GARAGE OFFICE AND ELEVATOR ROOM | HighRise | LISA KIMBALL
179 | THE LOCATION OF THE FIRE PUMP ROOM (BASEMENT) AND ELEVATOR ROOM (ROOF) MUST BE IDENTIFIED AND LABELED AS SUCH ALL ELECTRICAL ROOMS, HVAC ROOMS, MECHANICAL ROOMS, GENERATOR ROOM (IF ONE IS LOCATED ON SITE) AND ELECTRICAL ROOM IN THE PARKING GARAGE OFFICE MUST BE LABELED | HighRise | LISA KIMBALL
180 | A 911 KEY BOX OR KNOX BOX IS REQUIRED TO ACCESS THE PROPERTY, ALARM ROOM, FIRE PUMP ROOM, FIRE COMMAND ROOM AND ELEVATOR ROOM IN CASE OF EMERGENCY NO 24 HOUR SECURITY; NO KEYHOLDER ON SITE - UPON ALARM OR EMERGENCY, AN OFFICER OR SECURITY IS DISPATCHED FROM CAROLINE AND PRESTON - A KEYHOLDER FROM PRECINCT 1 RESPONDS/ARRIVES WITHIN 5 MINUTES BY CAR, CART OR TRUCK | HighRise | LISA KIMBALL
181 | THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
182 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
183 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
184 | ENSURE THE LOCK-OUT/TAG-OUT EQUIPMENT ARE READILY ACCESSIBLE AND PROPERLY LABELED: - PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS - A MINIMUM TWO (2) LOCK-OUT/TAG-OUT SETS FOR 4 TO 6 ELEVATORS - A MINIMUM THREE (3) LOCK-OUT/TAG-OUT SETS FOR 7 OR MORE ELEVATORS | HighRise | LISA KIMBALL
185 | PROVIDE 2 SETS OF INDEPENDENT SERVICE KEYS - STORE OUTSIDE OF FIRE DEPOSITORY BOX | HighRise | LISA KIMBALL
186 | IDENTIFY AND LABEL THE FIRE DEPARTMENT TEST CONNECTION | HighRise | LISA KIMBALL
187 | ALL FIRE EXTINGUISHERS MUST BE HUNG AT LEAST 4 INCHES FROM THE FLOOR (AT THE BASE) BUT NO HIGHER THAN 5 FEET (AT THE TOP) | HighRise | LISA KIMBALL
188 | SUPPLY KEYS FOR THE ACCESS GATES, FIRE COMMAND ROOM, EXTERIOR DOORS, MECHANICAL ROOMS, ELECTRICAL ROOMS, ELEVATOR ROOM, ALARM ROOM, FIRE PUMP ROOM, HVAC, ETC IN 911 KEY BOX ALL KEYS IN THE 911 BOX ARE CURRENT, LABELED AND FUNCTION | HighRise | LISA KIMBALL
189 | AN F7 PERMIT IS REQUIRED TO MAINTAIN 6O GALLONS OR MORE OF FRY OIL ON SITE - OBTAIN A STORED OILS PERMIT FROM THE HOUSTON PERMITTING CENTER THIS PERMIT MUST BE PAID/RENEWED ANNUALLY | HighRise | LISA KIMBALL
190 | A K1 PERMIT IS REQUIRED TO INSTALL AND MAINTAIN A 911 KEY BOX - OBTAIN A 911 KEY BOX/KNOX BOX PERMIT FROM THE HOUSTON PERMITTING CENTER THIS PERMIT MUST BE PAID/RENEWED ANNUALLY | HighRise | LISA KIMBALL
191 | NoData | HighRise | LISA KIMBALL
221 | A CITATION WILL BE WRITTEN IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
222 | ATTEND FIRE WARDEN TRAINING AND OBTAIN A CERTIFICATE OF COMPLETION VISIT http://houstontx.gov/fire/HFMO/highrisecert.html TO SIGN UP FOR THE OPEN CLASS IN JANUARY 2020 (MUST LOG ON AND SIGN UP BEFORE THE DEADLINE) OR TAKE THE ONLINE CLASS THROUGH MR. DEAL OR MR. SALAZAR TENANT HAS NOT COMPLIED AFTER SEVERAL REQUESTS TO COMPLETE THE FIRE WARDEN TRAINING | HighRise | LISA KIMBALL
223 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
224 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRE CODE OFFICIAL IS DEPENDENT UPON SUCCESSFUL COMPLETION OF THREE COMPONENTS; ONE OF WHICH IS FIRE WARDEN HIGH-RISE CERTIFICATION CLASS | HighRise | LISA KIMBALL
225 | ATTENDANCE AT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS | HighRise | LISA KIMBALL
226 | CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
227 | MEMBERS OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
228 | NoData | HighRise | LISA KIMBALL
229 | NoData | HighRise | LISA KIMBALL
230 | ALL OCCUPANTS OF THE BUILDING SHALL PARTICIPATE IN THE FIRE DRILLS AS REQUIRED BY THE CODE OFFICIAL AND THE FIRE CODE | HighRise | LISA KIMBALL
231 | APPROVAL OF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFUL COMPLETION OF SEVERAL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF A COMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS | HighRise | LISA KIMBALL
232 | THE CERTIFICATE OF COMPLETION OF FIRE WARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
929 | A CITATION WILL BE WRITTEN IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
930 | THE CERTIFICATE OF OCCUPANCY AND ALL PERMITS SHOULD BE POSTED IN THE BUSINESS | HighRise | LISA KIMBALL
931 | OBTAIN A CERTIFICATE OF OCCUPANCY AND ANY REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER | HighRise | LISA KIMBALL
932 | ATTEND FIRE WARDEN TRAINING AND OBTAIN A CERTIFICATE OF COMPLETION | HighRise | LISA KIMBALL
933 | NoData | HighRise | LISA KIMBALL
934 | NoData | HighRise | LISA KIMBALL
935 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
936 | NoData | HighRise | LISA KIMBALL
937 | NoData | HighRise | LISA KIMBALL
938 | CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
939 | NoData | HighRise | LISA KIMBALL
940 | NoData | HighRise | LISA KIMBALL
941 | NoData | HighRise | LISA KIMBALL
942 | OCCUPANCY NAME (LANIER BUSINESS SYSTEMS) IS DIFFERENT FROM BUSINESS NAME - OBTAIN CERTIFICATE OF OCCUPANCY FROM THE HOUSTON PERMITTING CENTER WITH CURRENT INFORMATION | HighRise | LISA KIMBALL
943 | NoData | HighRise | LISA KIMBALL
944 | NoData | HighRise | LISA KIMBALL
945 | NoData | HighRise | LISA KIMBALL
1124 | NoData | HighRise | LISA KIMBALL
1221 | A CITATION WILL BE WRITTEN IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
1222 | THE CERTIFICATE OF OCCUPANCY AND ALL PERMITS SHOULD BE POSTED IN THE BUSINESS | HighRise | LISA KIMBALL
1223 | OBTAIN A CERTIFICATE OF OCCUPANCY AND ANY REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER | HighRise | LISA KIMBALL
1224 | ATTEND FIRE WARDEN TRAINING AND OBTAIN A CERTIFICATE OF COMPLETION VISIT http://houstontx.gov/fire/HFMO/highrisecert.html TO SIGN UP FOR THE OPEN CLASS IN JANUARY 2020 (MUST LOG ON AND SIGN UP BEFORE THE DEADLINE) OR TAKE THE ONLINE CLASS THROUGH MR. DEAL OR MR. SALAZAR TENANT HAS NOT COMPLIED AFTER SEVERAL REQUESTS TO COMPLETE THE FIRE WARDEN TRAINING | HighRise | LISA KIMBALL
1225 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
1226 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRE CODE OFFICIAL IS DEPENDENT UPON SUCCESSFUL COMPLETION OF THREE COMPONENTS; ONE OF WHICH IS FIRE WARDEN HIGH-RISE CERTIFICATION CLASS | HighRise | LISA KIMBALL
1227 | ATTENDANCE AT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS | HighRise | LISA KIMBALL
1228 | CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
1229 | MEMBERS OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
1230 | NoData | HighRise | LISA KIMBALL
1231 | NoData | HighRise | LISA KIMBALL
1232 | ALL OCCUPANTS OF THE BUILDING SHALL PARTICIPATE IN THE FIRE DRILLS AS REQUIRED BY THE CODE OFFICIAL AND THE FIRE CODE | HighRise | LISA KIMBALL
1233 | OCCUPANCY NAME IS DIFFERENT FROM BUSINESS NAME - OBTAIN A CURRENT CERTIFICATE OF OCCUPANCY FROM THE HOUSTON PERMITTING CENTER WITH CURRENT INFORMATION | HighRise | LISA KIMBALL
1234 | APPROVAL OF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFUL COMPLETION OF SEVERAL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF A COMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS | HighRise | LISA KIMBALL
1235 | THE CERTIFICATE OF COMPLETION OF FIRE WARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
1470 | NoData | HighRise | LISA KIMBALL
1679 | NoData | HighRise | LISA KIMBALL
2036 | A CITATION WILL BE WRITTEN IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
2037 | THE CERTIFICATE OF OCCUPANCY AND ALL PERMITS SHOULD BE POSTED IN THE BUSINESS | HighRise | LISA KIMBALL
2038 | OBTAIN A CERTIFICATE OF OCCUPANCY AND ANY REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER | HighRise | LISA KIMBALL
2039 | ATTEND FIRE WARDEN TRAINING AND OBTAIN A CERTIFICATE OF COMPLETION | HighRise | LISA KIMBALL
2040 | NoData | HighRise | LISA KIMBALL
2041 | NoData | HighRise | LISA KIMBALL
2042 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
2043 | NoData | HighRise | LISA KIMBALL
2044 | NoData | HighRise | LISA KIMBALL
2045 | CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
2046 | NoData | HighRise | LISA KIMBALL
2047 | NoData | HighRise | LISA KIMBALL
2048 | NoData | HighRise | LISA KIMBALL
2049 | OCCUPANCY NAME (MECHAEL OJO) IS DIFFERENT FROM BUSINESS NAME - OBTAIN CERTIFICATE OF OCCUPANCY FROM THE HOUSTON PERMITTING CENTER WITH CURRENT INFORMATION | HighRise | LISA KIMBALL
2050 | NoData | HighRise | LISA KIMBALL
2051 | NoData | HighRise | LISA KIMBALL
2052 | NoData | HighRise | LISA KIMBALL
2392 | A CITATION WILL BE WRITTEN IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
2393 | ATTEND FIRE WARDEN TRAINING AND OBTAIN A CERTIFICATE OF COMPLETION | HighRise | LISA KIMBALL
2394 | NoData | HighRise | LISA KIMBALL
2395 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
2396 | NoData | HighRise | LISA KIMBALL
2397 | NoData | HighRise | LISA KIMBALL
2398 | CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
2399 | NoData | HighRise | LISA KIMBALL
2400 | NoData | HighRise | LISA KIMBALL
2401 | NoData | HighRise | LISA KIMBALL
2402 | NoData | HighRise | LISA KIMBALL
2403 | NoData | HighRise | LISA KIMBALL
3530 | A CITATION WILL BE WRITTEN IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
3531 | THE CERTIFICATE OF OCCUPANCY AND ALL PERMITS SHOULD BE POSTED IN THE BUSINESS | HighRise | LISA KIMBALL
3532 | OBTAIN CERTIFICATE OF OCCUPANCY AND ANY REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER | HighRise | LISA KIMBALL
3533 | ATTEND FIRE WARDEN TRAINING AND OBTAIN A CERTIFICATE OF COMPLETION | HighRise | LISA KIMBALL
3534 | NoData | HighRise | LISA KIMBALL
3535 | NoData | HighRise | LISA KIMBALL
3536 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
3537 | NoData | HighRise | LISA KIMBALL
3538 | NoData | HighRise | LISA KIMBALL
3539 | CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
3540 | NoData | HighRise | LISA KIMBALL
3541 | NoData | HighRise | LISA KIMBALL
3542 | NoData | HighRise | LISA KIMBALL
3543 | OCCUPANCY NAME (HAMMERMAN & GAINER) IS DIFFERENT FROM BUSINESS NAME - OBTAIN CERTIFICATE OF OCCUPANCY FROM THE HOUSTON PERMITTING CENTER WITH CURRENT INFORMATION | HighRise | LISA KIMBALL
3544 | NoData | HighRise | LISA KIMBALL
3545 | NoData | HighRise | LISA KIMBALL
3546 | NoData | HighRise | LISA KIMBALL
3714 | INSPECTION CONDUCTED 5 FEBRUARY 20 - ONE VIOLATION FOUND ON SITE | HighRise | LISA KIMBALL
3715 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED | HighRise | LISA KIMBALL
3716 | REMOVE AND DISCONTINUE USE OF UNAPPROVED LOCKING/SECURITY DEVICE (DEADBOLT ON NORTH EXIT) ON EMERGENCY EXIT DOOR | HighRise | LISA KIMBALL
3717 | NoData | HighRise | LISA KIMBALL
3718 | CERTIFICATE OF OCCUPANCY IS POSTED ON SITE FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - AUGUST 2019 | HighRise | LISA KIMBALL
3719 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
3720 | NoData | HighRise | LISA KIMBALL
3731 | NoData | HighRise | LISA KIMBALL
3828 | A CITATION WILL BE WRITTEN IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
3829 | THE CERTIFICATE OF OCCUPANCY AND ALL PERMITS SHOULD BE POSTED IN THE BUSINESS | HighRise | LISA KIMBALL
3830 | OBTAIN A CERTIFICATE OF OCCUPANCY AND ANY REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER | HighRise | LISA KIMBALL
3831 | ATTEND FIRE WARDEN TRAINING AND OBTAIN A CERTIFICATE OF COMPLETION | HighRise | LISA KIMBALL
3832 | NoData | HighRise | LISA KIMBALL
3833 | NoData | HighRise | LISA KIMBALL
3834 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
3835 | NoData | HighRise | LISA KIMBALL
3836 | NoData | HighRise | LISA KIMBALL
3837 | CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
3838 | NoData | HighRise | LISA KIMBALL
3839 | NoData | HighRise | LISA KIMBALL
3840 | NoData | HighRise | LISA KIMBALL
3841 | OCCUPANCY AND SUITE NUMBER ARE NOT LISTED IN ILMS COMPUTER SYSTEM - OBTAIN CERTIFICATE OF OCCUPANCY FROM THE HOUSTON PERMITTING CENTER WITH CURRENT INFORMATION | HighRise | LISA KIMBALL
3842 | NoData | HighRise | LISA KIMBALL
3843 | NoData | HighRise | LISA KIMBALL
3844 | NoData | HighRise | LISA KIMBALL
3857 | THE EMERGENCY EXIT LIGHT AT THE FRONT DOOR IS OUT - REPLACE OR REPAIR IMMEDIATELY EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOST RECENT TEST | HighRise | LISA KIMBALL
3858 | NoData | HighRise | LISA KIMBALL
3859 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED | HighRise | LISA KIMBALL
3860 | FIRE ALARM PANEL IS BLUE TAGGED - 1JAN18 FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - OCT 2019 EMERGENCY ESCAPE MAPS ARE ALL POSTED IN PLACE IN EACH CLASSROOM ALL FIRE DRILLS CONDUCTED MONTHLY IN 2019; LAST DRILL CONDUCTED JAN 2020 | HighRise | LISA KIMBALL
3861 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
3862 | CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
3898 | THE SPRINKLER SYSTEM IS YELLOW TAGGED - A YELLOW TAG WAS ISSUED ON 20JUL19 AND MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
3899 | NoData | HighRise | LISA KIMBALL
3900 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
3901 | IF GAS IS ON SITE: CONTACT A CERTIFIED PLUMBER TO CONDUCT A GAS TEST IF GAS TEST WAS CONDUCTED MORE THAN TWO YEARS AGO PROVIDE EVIDENCE OF LAST GAS TEST AND KEEP DOCUMENTS/PROOF OF TESTING ON SITE AND READY FOR INSPECTION AT ALL TIMES | HighRise | LISA KIMBALL
3902 | NoData | HighRise | LISA KIMBALL
3903 | KEY BOX (K1) IS POSTED ON SITE - EXP 29JUL19 FIRE ALARM PERMIT IS POSTED ON SITE - ISSUED 15AUG19 FIRE ALARM PANEL IS BLUE TAGGED - 27JUL19 FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - SEP19 ANSUL SYSTEM IS BLUE TAGGED - SEP19 | HighRise | LISA KIMBALL
3904 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
3905 | NoData | HighRise | LISA KIMBALL
3906 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
3907 | A PERMIT AND A LICENSED PLUMBER MUST BE OBTAINED PRIOR TO CONDUCTING A GAS TEST - CONTACT THE HOUSTON PERMITTING CENTER 832.394.8811 FOR MORE INFORMATION | HighRise | LISA KIMBALL
3908 | PROVIDE A SIGN ON THE ENTRANCE TO ROOM C4 WHICH INDICATES THE FIRE SPRINKLER RISER ROOM'S (FIRE CONNECTION CLOSET) LOCATION | HighRise | LISA KIMBALL
3977 | KEEP RECORDS OF MONTHLY FIRE DRILLS ON SITE FOR AT LEAST 3 YEARS | HighRise | LISA KIMBALL
3978 | THE EXIT DOOR (FANNIN SIDE) MUST BE IDENTIFIED AND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS AND ADD "NOT AN ENTRANCE" OR "EMERGENCY EXIT" WITH AN ARROW INDICATING THE DIRECTION TOWARDS THE ENTRANCE | HighRise | LISA KIMBALL
3979 | CORRECTED YELLOW AND RED TAGS ON FIRE ALARM PANEL 11OCT19 - NO FURTHER ACTION NEEDED | HighRise | LISA KIMBALL
3980 | NoData | HighRise | LISA KIMBALL
3981 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
3982 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION FIRE EXTINGUISHERS WERE INSPECTED IN JANUARY 2019 - NO FURTHER ACTION NEEDED | HighRise | LISA KIMBALL
3983 | FIRE DRILLS ARE CONDUCTED MONTHLY | HighRise | LISA KIMBALL
3984 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
3985 | ENSURE THE FIRE CONTROL ROOM (WHERE MAIN FIRE ALARM PANEL IS LOCATED) IS CORRECTLY LABELED AS SUCH | HighRise | LISA KIMBALL
3986 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
3987 | CURTAINS HUNG IN THE COMMON AREA ARE TREATED WITH AN APPROVED FIRE- RETARDANT COATING AND APPLIED TO COMPLY WITH NFPA 703 - NO FURTHER ACTION NEEDED | HighRise | LISA KIMBALL
3988 | PLACE A SIGN ABOVE SECONDARY FIRE ALARM PANEL INSIDE THE DAYCARE "MAIN FIRE ALARM PANEL LOCATED INSIDE FIRE CONTROL ROOM" WITH A MAP WHICH SHOWS ITS LOCATION | HighRise | LISA KIMBALL
3989 | THE LOCATION MUST HAVE A NUMERICAL ADDRESS WHICH IS VISIBLE FROM THE STREET - '1001 McKINNEY' MUST BE CONSPICUOUSLY POSTED AT THE FRONT ENTRANCE WHEN CALLING 911 FOR ANY EMERGENCY, DIAL 9 THEN 911 - THIS WAS TESTED DURING THE FMA; THE ADDRESS THE DISPATCHER RECEIVED WAS 1001 McKINNEY | HighRise | LISA KIMBALL
3990 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOST RECENT TEST | HighRise | LISA KIMBALL
4040 | THE FIRE ALARM SYSTEM IS YELLOWTAGGED - THE TAG WAS ISSUED 08/19/19 BY CLS TECHNOLOGY LICENSE #2393826 (NAME IS SKYLER?) AND SYSTEM MUST BE SERVICED OR REPAIRED IMMEDIATELY THIS YELLOW TAG WAS PLACED ON THE FIRE ALARM | HighRise | LISA KIMBALL
4041 | NoData | HighRise | LISA KIMBALL
4042 | NoData | HighRise | LISA KIMBALL
4043 | NoData | HighRise | LISA KIMBALL
4044 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
4410 | NoData | HighRise | LISA KIMBALL
4573 | NoData | HighRise | LISA KIMBALL
4735 | THE ALARM SYSTEM IS YELLOW AND RED TAGGED - BOTH TAGS WERE ISSUED 04/17/18 AND SYSTEM MUST BE SERVICED OR REPAIRED IMMEDIATELY BUILDING MANAGER WAS NOT AWARE OF ANY PROBLEMS WITH THE FIRE ALARM SYSTEM; SHE WAS SHOWN THE IMPAIRMENT TAGS AND INSTRUCTED TO BE AWARE OF TAGS WHICH ARE ANY COLOR OTHER THAN BLUE (BLUE INDICATING AN 'ACCEPTABLE STATE' AND YELLOW OR RED INDICATING PROBLEMS OR IMPAIRMENT) MUST BE TENDED TO IMMEDIATELY | HighRise | LISA KIMBALL
4736 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
4737 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
4738 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
4739 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
4780 | INSPECTION CONDUCTED 13 FEB 2020 - NO VIOLATIONS FOUND ON SITE | HighRise | LISA KIMBALL
4781 | CERTIFICATE OF OCCUPANCY IS POSTED ON SITE FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - OCT19 NO FURTHER ACTIONS NEEDED - FIRE MARSHAL APPROVAL | HighRise | LISA KIMBALL
4782 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
4808 | INSPECTION CONDUCTED 13 FEB 2020 - NO VIOLATIONS FOUND ON SITE | HighRise | LISA KIMBALL
4809 | CERTIFICATE OF OCCUPANCY IS POSTED ON SITE FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - OCT19 NO FURTHER ACTIONS NEEDED - FIRE MARSHAL APPROVAL | HighRise | LISA KIMBALL
4810 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
5365 | INSPECTION CONDUCTED 5 FEBRUARY 20 - ONE VIOLATION FOUND ON SITE | HighRise | LISA KIMBALL
5366 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED | HighRise | LISA KIMBALL
5367 | REMOVE AND DISCONTINUE USE OF UNAPPROVED LOCKING/SECURITY DEVICE (DEADBOLT ON NORTH EXIT) ON EMERGENCY EXIT DOOR | HighRise | LISA KIMBALL
5368 | NoData | HighRise | LISA KIMBALL
5369 | CERTIFICATE OF OCCUPANCY IS POSTED ON SITE FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - AUGUST 2019 | HighRise | LISA KIMBALL
5370 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
5371 | NoData | HighRise | LISA KIMBALL
5658 | NoData | HighRise | LISA KIMBALL
9912 | INSPECTION CONDUCTED 20 MARCH 2018 - NO VIOLATIONS FOUND ON SITE | HighRise | LISA KIMBALL
9913 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
9914 | CofO POSTED ON SITE FIRE ALARM PERMIT IS POSTED ON SITE - ISSUED 1JUL19 FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - FEB20 EMERGENCY ESCAPE MAPS ARE ALL POSTED IN PLACE IN EACH CLASSROOM ALL FIRE DRILLS CONDUCTED MONTHLY IN 2019 AND 2020; LAST DRILL CONDUCTED JANUARY THE FIRE ALARM SYSTEM WAS FOUND TO BE IN COMPLIANCE, IN ACCEPTABLE CONDITION AND CURRENT ANNUAL INSPECTIONS (11/15/19) CONDUCTED AND BLUE TAGGED - NO FURTHER COMPLIANCE NEEDED | HighRise | LISA KIMBALL
10242 | NoData | HighRise | LISA KIMBALL
10474 | NoData | HighRise | LISA KIMBALL
10647 | YOURATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THECITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THEADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS.ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCEOF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF ACITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUECITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFESAFETY HAZARD | HighRise | LISA KIMBALL
10648 | ALL FIRE EXTINGUISHERS THROUGHOUT THE FACILITY WERE LAST TAGGED/INSPECTEDJAN 2019 - OVERDUE FOR INSPECTION - CALL EXTINGUISHER INSPECTION COMPANY IMMEDIATELY TO INSPECT AND TAG ALL FIRE EXTINGUISHERS FIRE EXTINGUISHERS MUST BE INSPECTED AND TAGGED ANNUALLY | HighRise | LISA KIMBALL
10649 | WHERE LOCAL FIRE MARSHAL APPROVALS AREREQUIRED BY REGULATORY AGENCIES, APPROVED FIRE SAFETY AND EVACUATION PLANSSHALL BE PREPARED, MAINTAINED AND POSTED IN GROUP E OCCUPANCIES | HighRise | LISA KIMBALL
10650 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOST RECENT TEST SEVERAL EMERGENCY EXIT SIGNS AND EGRESS LIGHTS WERE NOT ILLUMINATED OR FUNCTIONING - REPAIR OR REPLACE IMMEDIATELY PROVIDE AN EMERGENCY EXIT SIGN ABOVE THE EXIT DOOR IN ROOM #7 | HighRise | LISA KIMBALL
10651 | FIRE ALARM PERMIT IS POSTED ON SITE - 17029375 FIRE ALARM PANEL IS BLUE TAGGED - 3/4/20 ALL FIRE DRILLS CONDUCTED MONTHLY IN 2020 AND 2019 SMOKE DETECTOR IN THE WORKSPACE BATHROOM IS CHIRPING - REPLACE BATTERY OR DETECTOR | HighRise | LISA KIMBALL
10724 | NoData | HighRise | LISA KIMBALL
10758 | THE ALARM SYSTEM HAS MULTIPLE RED TAGS - ALL TAGS WERE ISSUED 2/19/20 AND SYSTEM MUST BESERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
10812 | YOURATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THECITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THEADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS.ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCEOF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF ACITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUECITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFESAFETY HAZARD | HighRise | LISA KIMBALL
10813 | YOURATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THECITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THEADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS.ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCEOF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF ACITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUECITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFESAFETY HAZARD | HighRise | LISA KIMBALL
10814 | ALL FIRE EXTINGUISHERS THROUGHOUT THE FACILITY WERE LAST TAGGED/INSPECTEDJAN 2019 - OVERDUE FOR INSPECTION - CALL EXTINGUISHER INSPECTION COMPANY IMMEDIATELY TO INSPECT AND TAG ALL FIRE EXTINGUISHERS FIRE EXTINGUISHERS MUST BE INSPECTED AND TAGGED ANNUALLY | HighRise | LISA KIMBALL
10815 | ALL FIRE EXTINGUISHERS THROUGHOUT THE FACILITY WERE LAST TAGGED/INSPECTEDJAN 2019 - OVERDUE FOR INSPECTION - CALL EXTINGUISHER INSPECTION COMPANY IMMEDIATELY TO INSPECT AND TAG ALL FIRE EXTINGUISHERS FIRE EXTINGUISHERS MUST BE INSPECTED AND TAGGED ANNUALLY | HighRise | LISA KIMBALL
10816 | WHERE LOCAL FIRE MARSHAL APPROVALS AREREQUIRED BY REGULATORY AGENCIES, APPROVED FIRE SAFETY AND EVACUATION PLANSSHALL BE PREPARED, MAINTAINED AND POSTED IN GROUP E OCCUPANCIES | HighRise | LISA KIMBALL
10817 | WHERE LOCAL FIRE MARSHAL APPROVALS AREREQUIRED BY REGULATORY AGENCIES, APPROVED FIRE SAFETY AND EVACUATION PLANSSHALL BE PREPARED, MAINTAINED AND POSTED IN GROUP E OCCUPANCIES | HighRise | LISA KIMBALL
10818 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOST RECENT TEST SEVERAL EMERGENCY EXIT SIGNS AND EGRESS LIGHTS WERE NOT ILLUMINATED OR FUNCTIONING - REPAIR OR REPLACE IMMEDIATELY PROVIDE AN EMERGENCY EXIT SIGN ABOVE THE EXIT DOOR IN ROOM #7 | HighRise | LISA KIMBALL
10819 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOST RECENT TEST SEVERAL EMERGENCY EXIT SIGNS AND EGRESS LIGHTS WERE NOT ILLUMINATED OR FUNCTIONING - REPAIR OR REPLACE IMMEDIATELY PROVIDE AN EMERGENCY EXIT SIGN ABOVE THE EXIT DOOR IN ROOM #7 | HighRise | LISA KIMBALL
10820 | FIRE ALARM PERMIT IS POSTED ON SITE - 17029375 FIRE ALARM PANEL IS BLUE TAGGED - 3/4/20 ALL FIRE DRILLS CONDUCTED MONTHLY IN 2020 AND 2019 SMOKE DETECTOR IN THE WORKSPACE BATHROOM IS CHIRPING - REPLACE BATTERY OR DETECTOR | HighRise | LISA KIMBALL
10821 | FIRE ALARM PERMIT IS POSTED ON SITE - 17029375 FIRE ALARM PANEL IS BLUE TAGGED - 3/4/20 ALL FIRE DRILLS CONDUCTED MONTHLY IN 2020 AND 2019 SMOKE DETECTOR IN THE WORKSPACE BATHROOM IS CHIRPING - REPLACE BATTERY OR DETECTOR | HighRise | LISA KIMBALL
10822 | NoData | HighRise | LISA KIMBALL
11091 | THE FIRE ALARM SYSTEM IS YELLOW TAGGED - SYSTEM MUST BE SERVICED OR REPAIRED IMMEDIATELY FIRST FLOOR FIRE ALARM SPEAKERS DO NOT SOUND/WORK UPON ACTIVATION - CALL ALARM COMPANY IMMEDIATELY TO REPAIR SYSTEM THE JOCKEY PUMP MUST BE REPLACED - NOTIFY OEC WHEN SYSTEM IS OUT OF SERVICE DUE TO REPAIRS | HighRise | LISA KIMBALL
11092 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRESUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALSAND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ONSITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
11093 | FIRST FLOOR FIRE ALARM SPEAKERS DO NOT SOUND/WORK UPON ACTIVATION - CALL ALARM COMPANY IMMEDIATELY TO REPAIR SYSTEM THE JOCKEY PUMP MUST BE REPLACED - NOTIFY OEC WHEN SYSTEM IS OUT OF SERVICE DUE TO REPAIRS | HighRise | LISA KIMBALL
11096 | CANDLES SHOULD BE USED WITH CAUTION AND MAY BE PROHIBITED IN THIS ATRIUM BUILDING - CONSULT WITH MANAGEMENT BEFORE USE A C1 PERMIT ISREQUIRED FOR USE OF CANDLES AND OPEN FLAMES - OBTAIN A CANDLE/OPENFLAME PERMIT FROM THE HOUSTON PERMITTING CENTER THIS PERMIT MUST BEPAID/RENEWED ANNUALLY | HighRise | LISA KIMBALL
11097 | NoData | HighRise | LISA KIMBALL
11098 | OBTAIN A CERTIFICATEOF OCCUPANCY AND ANY REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER | HighRise | LISA KIMBALL
11099 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THEPROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THEPREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEALALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURINGSUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIREDPRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THEFIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THATARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
11100 | THE CERTIFICATE OF OCCUPANCY AND ANY REQUIRED PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES COPIES OF PERMITS AND CERTIFICATE OF OCCUPANCY FOR RESPECTIVE BUSINESSES/TENANTS MAY BE KEPT IN THE LEASING OFFICE | HighRise | LISA KIMBALL
11101 | ALL FIRE EXTINGUISHERSMUST BE HUNG AT LEAST 4 INCHES FROM THE FLOOR (AT THE BASE) BUT NO HIGHER THAN5 FEET (AT THE TOP) | HighRise | LISA KIMBALL
11102 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSIONEQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED- ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIREMARSHAL INSPECTION | HighRise | LISA KIMBALL
11103 | NoData | HighRise | LISA KIMBALL
11104 | NoData | HighRise | LISA KIMBALL
11105 | NoData | HighRise | LISA KIMBALL
11106 | NoData | HighRise | LISA KIMBALL
11107 | NoData | HighRise | LISA KIMBALL
11108 | NoData | HighRise | LISA KIMBALL
11109 | NoData | HighRise | LISA KIMBALL
11128 | NoData | HighRise | LISA KIMBALL
11493 | NoData | HighRise | LISA KIMBALL
11538 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11539 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11540 | EXIT SIGNS WERE FOUND OUT/NOT ILLUMINATED ON THE 8TH FLOOR (SOUTHWEST CORNER), 7TH FLOOR (STAIR A), 6TH FLOOR (SOUTH CORNER) AND 3RD FLOOR (NEAR STAIR A) - REPAIR OR REPLACE THEM IMMEDIATELY | HighRise | LISA KIMBALL
11541 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11542 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11543 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11544 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIRE A LETTER - PROVIDE A PHOTOCOPY OF THESE PERMITS. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - CONDUCTED; PASSED OR FAILED? " Fire Alarm System Test - Annual " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED; FAILED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year " Water Supply Tank Inspection - 5 Year " Boiler Permit - N/A " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test " Gas Test - 5 Year - REQUIRED IF GAS ON SITE " FireFighter Phones or Emergency Responder Radio Coverage IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
11545 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED | HighRise | LISA KIMBALL
11546 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11547 | POST PERMITS DURING DEMOLITION | HighRise | LISA KIMBALL
11548 | NoData | HighRise | LISA KIMBALL
11549 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
11550 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
11551 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11552 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11553 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
11554 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11555 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11556 | BUILDING IS DUE FOR DEMOLITION IN 2020 | HighRise | LISA KIMBALL
11557 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11558 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11559 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11560 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11561 | PERTAINING TO THE HIGH-RISE WHICH IS TO BE DEMOLISHED AFTER JANUARY 31, 2020 | HighRise | LISA KIMBALL
11562 | PROVIDE 2 ELEVATOR INDEPENDENT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX | HighRise | LISA KIMBALL
11563 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT OR SERVICE TO THE OWNER/OCCUPANT AND TO THE JURISDICTION - BY PHONE 713.884.3143 AND EMAIL AT HFD.DISPATCH3@houstontx.gov THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
11882 | YOURATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THECITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THEADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS.ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCEOF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF ACITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUECITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFESAFETY HAZARD | HighRise | LISA KIMBALL
11883 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY -PROVIDE EVIDENCE OF MOST RECENT TEST THE EMERGENCY EXIT SIGN ABOVE THE BACK DOOR IS NOT ILLUMINATED OR FUNCTIONING - REPAIR OR REPLACE IMMEDIATELY | HighRise | LISA KIMBALL
11884 | FIRE ALARM PERMIT IS POSTED ON SITE FIRE ALARM PANEL IS BLUE TAGGED - 6MAR20 FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - MAR20 EMERGENCY ESCAPE MAPS ARE ALL POSTED IN PLACE IN EACH CLASSROOM ALL FIRE DRILLS CONDUCTED MONTHLY IN 2019 AND 2020 | HighRise | LISA KIMBALL
12365 | NoData | HighRise | LISA KIMBALL
13696 | NoData | HighRise | LISA KIMBALL
14936 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
14937 | THE CERTIFICATE OF OCCUPANCY, FIRE ALARM PERMIT AND ANY OTHER NECESSARY PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES | HighRise | LISA KIMBALL
14938 | ENSURE NO PARKED CARS, ETC. ARE BLOCKING ANY OF THE EMERGENCY EXIT DOORS THE BACK EXIT DOOR IN THE GYM IS STICKING; REPAIR THE DOOR TO ENSURE IT OPENS EASILY | HighRise | LISA KIMBALL
14939 | ENSURE ELECTRICAL ROOM, HVACROOM, FIRE SPRINKLER RISER ROOM, OFFICE DOOR WHERE FIRE ALARM IS LOCATED AND FIRE SPRINKLER RISER ROOMS MUST BE LABELED AS SUCH FOR READYIDENTIFICATION REMOVE "BOILER ROOM" SIGN WHERE THE BOILER HAS BEEN REMOVED | HighRise | LISA KIMBALL
14940 | NoData | HighRise | LISA KIMBALL
14941 | ALL OF THE BACK EXIT DOORS MUST BE IDENTIFIED AND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS | HighRise | LISA KIMBALL
14942 | INFORMATION TO BE INCLUDED IN FIREEVACUATION PLANS | HighRise | LISA KIMBALL
14943 | WHERE LOCAL FIRE MARSHAL APPROVALS AREREQUIRED BY REGULATORY AGENCIES, APPROVED FIRE SAFETY AND EVACUATION PLANSSHALL BE PREPARED, MAINTAINED AND POSTED IN GROUP E OCCUPANCIES | HighRise | LISA KIMBALL
14944 | THE FIRE ALARM DOES NOT HAVE ANY TAGS POSTED (INSTALLATION OR INSPECTION); HAVE A CERTIFIED INSPECTION COMPANY INSPECT AND TAG THE FIRE ALARM SYSTEM AS SOON AS POSSIBLE | HighRise | LISA KIMBALL
14945 | EXTINGUISHERS ARE ALL ACCEPTABLE AND BLUE TAGGED IN JANUARY 2020 THE FIRE SPRINKLER RISER WAS BLUE TAGGED IN JANUARY 2020 NO FURTHER ACTION REQUIRED | HighRise | LISA KIMBALL
16195 | NoData | HighRise | LISA KIMBALL
16217 | THE ALARM SYSTEM IS RED TAGGED WITH 2 TAGS - TAGS WERE ISSUED 05/03/19 BY JOHNSON CONTROLS (KYLE C. PRUIT? LISC# 1793879) AND 07/26/19 BY TYCO (BOYD? LISC# 2273899) - SYSTEM MUST BE SERVICED OR REPAIRED IMMEDIATELY THE OWNER/OCCUPANT AND JURISDICTION MUST BE NOTIFIED WITHIN 3 BUSINESS DAYS ANY TIME A RED TAG IS ISSUED - THE JURISDICTION WAS NOT NOTIFIED BY TYCO OR JOHNSON CONTROLS - MANAGER BRANDON VEAL WAS CONTACTED AND WARNED THAT CITATIONS WILL BE ISSUED IF NOTIFICATION TO THE JURISDICTION (BY STATE LAW) IS NOT COMPLIED WITH | HighRise | LISA KIMBALL
16218 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
16219 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
16220 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
16221 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
16313 | THE FIRE ALARM SYSTEM IS YELLOW TAGGED - SYSTEM MUST BESERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
16314 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRESUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALSAND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ONSITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
16315 | NoData | HighRise | LISA KIMBALL
16317 | NoData | HighRise | LISA KIMBALL
16410 | NoData | HighRise | LISA KIMBALL
16443 | NoData | HighRise | LISA KIMBALL
16453 | NoData | HighRise | LISA KIMBALL
16483 | NoData | HighRise | LISA KIMBALL
16491 | NoData | HighRise | LISA KIMBALL
16497 | NoData | HighRise | LISA KIMBALL
16499 | NoData | HighRise | LISA KIMBALL
16503 | NoData | HighRise | LISA KIMBALL
16534 | NoData | HighRise | LISA KIMBALL
16541 | NoData | HighRise | LISA KIMBALL
16542 | NoData | HighRise | LISA KIMBALL
16616 | NoData | HighRise | LISA KIMBALL
16653 | NoData | HighRise | LISA KIMBALL
16657 | NoData | HighRise | LISA KIMBALL
16665 | NoData | HighRise | LISA KIMBALL
17039 | PROVIDE DOCUMENTATION OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP POSTED ON SITE WITH ALL OTHER PERMITS, WITHIN THE ELEVATOR CAR OR WITHIN 10 FEET OF THE CALL BUTTONS | HighRise | LISA KIMBALL
17040 | HOUSEKEEPING IS REQUIRED IN THE PENTHOUSE ELEVATOR ROOM | HighRise | LISA KIMBALL
17041 | PROVIDE AN EXIT SIGN ON THE ROOF TO INDICATE PRESENCE OF STAIR A | HighRise | LISA KIMBALL
17042 | FIRE EXTINGUISHERS ARE NEEDED IN THE PARKING GARAGE | HighRise | LISA KIMBALL
17043 | ENSURE ALL FIRE EXTINGUISHERS ARE CONSPICUOUSLY LOCATED AND READILY AVAILABLE FOR USE - DO NOT DISGUISE OR ATTEMPT TO CONCEAL FIRE EXTINGUISHERS | HighRise | LISA KIMBALL
17044 | PROVIDE A COVER FOR OPEN JUNCTION BOX IN THE ROOF/PENTHOUSE ELEVATOR ROOM, THE 1OTH FLOOR ELECTRICAL ROOM (PANEL IS MISSING DOOR), THE 7TH FLOOR STAIRWELL, THE GROUND FLOOR MECHANICAL ROOM, THE GARAGE NEAR THE PUMPS AND IN THE FUTURE FOODA FOOD COURT PROVIDE BLANKS OR COVERS FOR MISSING TEETH, CIRCUITS OR VOIDS IN THE ELECTRICAL PANEL IN THE ELECTICAL ROOM ON THE GROUND FLOOR | HighRise | LISA KIMBALL
17045 | EMERGENCY EXIT SIGNS ARE OUT ON THE 10TH, 9TH, 8TH, 7TH, 3RD, 2ND FLOORS AND IN THE PARKING GARAGE - CALL SERVICE COMPANY IMMEDIATELY TO REPAIR OR REPLACE COMPONENTS | HighRise | LISA KIMBALL
17046 | THE BACK EXIT DOOR OF THE FUTURE FOODA FOOD COURT MUST BE IDENTIFIED AND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS | HighRise | LISA KIMBALL
17047 | REMOVE THE TAPE WRAPPED AROUND THE SMOKE DETECTOR ON THE 10TH FLOOR NEAR STAIR A - ALWAYS REMOVE COVERS AND OR TAPE AT THE END OF DAY | HighRise | LISA KIMBALL
17048 | FYI PER MR. PARRA'S REQUEST | HighRise | LISA KIMBALL
17049 | THE SPRINKLER SYSTEM WAS FOUND WITH SEVERAL YELLOW TAGS IN THE PUMP ROOM AND MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY THE FIRE HOSES ARE RED TAGGED - TAGS WERE ISSUED 2013, 2016 AND 2017 AND SYSTEM MUST BE SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
17050 | FYI | HighRise | LISA KIMBALL
17051 | SECURE ALL COMPRESSED GAS CYLINDERS WITH A CHAIN IN THE FUTURE FOODA COURT | HighRise | LISA KIMBALL
17052 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
17053 | ENSURE THAT UL APPROVED RED CAN IN THE ELEVATOR ROOM (ROOF/PENTHOUSE ELEVATOR ROOM IS EMPTIED DAILY | HighRise | LISA KIMBALL
17054 | A EMERGENCY "RE-ENTRY" BUTTON COULD NOT BE LOCATED ON THE FIRE ALARM PANEL - ENSURE ONE IS SUPPLIED, LOCATED AND CONSPICIOUSLY LABELED | HighRise | LISA KIMBALL
17055 | Facility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system must be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form - RECIEVED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 5 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - N/A - REQUIRED IF BOILERS ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
17056 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
17057 | FYI | HighRise | LISA KIMBALL
17058 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN STAIR A BETWEEN THE 9TH AND 10TH FLOOR, THE 10TH FLOOR, 9TH FLOOR, 8TH FLOOR STAIR A, 6TH FLOOR, 4TH FLOOR STAIR B, 3RD FLOOR STAIR B, THE FIRE COMMAND ROOM AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
17059 | FYI | HighRise | LISA KIMBALL
17060 | THE CERTIFICATE OF OCCUPANCY AND ALL PERMITS SHOULD BE POSTED IN THE FIRE CONTROL ROOM/OFFICE | HighRise | LISA KIMBALL
17061 | OBTAIN CERTIFICATE OF OCCUPANCY, K1 PERMIT (KEY BOX), F7 PERMIT (FUEL) AND FIRE ALARM PERMIT FROM THE HOUSTON PERMITTING CENTER | HighRise | LISA KIMBALL
17062 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
17063 | FYI PERTAINING TO DISTANCE AND PLACEMENT OF FIRE EXTIGUISHERS IN THE PARKING GARAGE | HighRise | LISA KIMBALL
17064 | FYI PER MR. PARRA'S REQUEST | HighRise | LISA KIMBALL
17065 | REPAIR ANY OPENINGS IN THE CIELING (REPLACE CIELING TILES) IN THE FUTURE FOODA FOOD COURT, THE MECHANICAL ROOM ON THE GROUND FLOOR, THE FIRE COMMAND ROOM AND THROUGHOUT THE BUILDING | HighRise | LISA KIMBALL
17066 | REMOVE AND DISCONTINUE UNACCEPTABLE LOCKING DEVICE FROM THE STAIRWELLS A AND B ON THE 7TH FLOOR | HighRise | LISA KIMBALL
17067 | ALL ELECTRICAL CIRCUIT BREAKERS IN ELECTRICAL PANELS MUST BE CLEARLY AND CORRECTLY LABELED ON THE 10TH FLOOR AND THE GROUND FLOOR ELECTRICAL ROOMS ALL ELECTRICAL ROOMS MUST BE IDENTIFIED AND LABELED AS SUCH | HighRise | LISA KIMBALL
17068 | PROVIDE SIGN ON THE DOOR OF THE FIRE PUMP ROOM IN THE GARAGE TO INDICATE THE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
17069 | KEYS MUST BE UPDATED IN THE 911 BOX | HighRise | LISA KIMBALL
17070 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
17071 | NoData | HighRise | LISA KIMBALL
17072 | NoData | HighRise | LISA KIMBALL
17073 | THE FDC SIGN MUST BE UPDATED TO INCLUDE SPRINKLER SYSTEMS WHICH HAVE BEEN ISTALLED IN THE HIGH-RISE REVIEW LSB #2 SECTION 2.5.4.3 TO REVISE THE FDC SIGN WITH NECESSARY CORRECTIONS AND ENSURE ALL PERTINENT INFORMATION IS INCLUDED Approved signs of weather-resistant materials, with not less than one inch high legible block lettering on a highly contrasting background, shall be placed on or immediately adjacent to all fire department connections and provide the following information: 1. Type of system - STANDPIPE, SPRINKLER, STANDPIPE / SPRINKLER, DRY PIPE SPRINKLER, etc. 2. Which building or structure, or what portion, zone, and floors of the building or structure the FDC serve. i. Ex: FLOORS B1 - 12; LEVELS 1 - 8; HIGH ZONE FLRS 21 - 40; etc. 3. On standpipe and combination standpipe/sprinkler systems - whether there are pressure regulating valves (PRV) or pressure reducing devices (PRD) on the system. System pressures shall also be indicated on all wet standpipe and combination standpipe/sprinkler systems. Examples: NO PRV/PRD (System Pres. 100 PSI) PRD Levels 1 - 7 (System Pres. 150 PSI) PRV Floors 1 - 10 (System Pres. 175 PSI) | HighRise | LISA KIMBALL
17074 | THE DOORS ON THE 9TH FLOOR, 6TH FLOOR AND GROUND FLOOR DO NOT LATCH CLOSED - ENSURE ALL STAIRWELL DOORS LATCH AND SHUT CLOSED | HighRise | LISA KIMBALL
17075 | FYI | HighRise | LISA KIMBALL
17076 | ALL FIRE EXTINGUISHERS MUST BE HUNG IN THE MECHANICAL ROOMS AND THE PARKING GARAGE - NOT STORED ON THE FLOOR | HighRise | LISA KIMBALL
17077 | PLEASE CONTACT INSPECTOR JUAN GARCIA BY EMAIL AT Juan.Garcia3@houstontx.gov OR 281.896.7084 IF YOU HAVE QUESTIIONS CONCERNING EVACUATION DRILLS, FIRE WARDEN TRAINING, ETC | HighRise | LISA KIMBALL
17078 | PLEASE CONTACT INSPECTOR JUAN GARCIA BY EMAIL AT Juan.Garcia3@houstontx.gov OR 281.896.7084 IF YOU HAVE QUESTIIONS CONCERNING EVACUATION DRILLS, FIRE WARDEN TRAINING, ETC | HighRise | LISA KIMBALL
17079 | CHEVRONS ON THE EXIT SIGNS ARE FACING THE WRONG DIRECTION ON THE 8TH FLOOR (NEAR 800), 5TH FLOOR, 4TH FLOOR (NEAR 416 AND 420), AND THE 3RD FLOOR (LAEDING TO STAIR B) - MAKE SURE CHEVRONS ARE POINTING THE WAY TO THE EXIT DOOR | HighRise | LISA KIMBALL
17080 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
17081 | THE MOBILITY IMPAIRED LIST WAS LAST UPDATED IN 2016 - THIS LIST MUST BE UPDATED EVERY 6 MONTHS THE BINDER NEEDS TABS THE FALCON LOCK IS PROVIDED - A SECONDARY LOCK IS NEEDED TO PROPERLY SECURE THE FDB CONTENTS EMERGENCY CONTACTS MUST BE UPDATED READ AND REVIEW LSB STANDARD 6; FULL COMPLIANCE OF PROVIDING A PROPERLY SUPPLIED FIRE DEPOSITORY BOX IS REQUIRED IMMEDIATELY THE ELEVATOR MASTER KEY DOESN'T UNLOCK THE ROOFTOP/PENTHOUSE ELEVATOR ROOM - PROVIDE ACCESS TO THIS ROOM | HighRise | LISA KIMBALL
17082 | PROVIDE DOCUMENTATION OR LETTER TO ENSURE ALL FIREPHONES HAVE BEEN TESTED BY AN APPROVED, CERTIFIED FIRE PROTECTION COMPANY AND FUNCTIONING PROPERLY - 5 OF THE 6 PHONES ON SITE WERE WORKING CORRECTLY; REMOVE THE NON-FUNCTIONING PHONE FROM THE CABINET | HighRise | LISA KIMBALL
17083 | PLEASE CONTACT INSPECTOR JUAN GARCIA BY EMAIL AT Juan.Garcia3@houstontx.gov OR 281.896.7084 IF YOU HAVE QUESTIIONS CONCERNING EVACUATION DRILLS, FIRE WARDEN TRAINING, ETC | HighRise | LISA KIMBALL
17084 | NoData | HighRise | LISA KIMBALL
17085 | REMOVE AND DISCONTINUE USE OF UNAPPROVED EXTENSION CORDS IN THE MECHANICAL/ELECTRICAL ROOM ON THE 10TH ROOM AND THE COMPUTER ROOM ON THE 7TH FLOOR - ONLY UL APPROVED EXTENSION CORDS WITH A SURGE PROTECTOR ARE SAFE FOR USE ON A TEMPORARY BASIS | HighRise | LISA KIMBALL
17086 | FYI | HighRise | LISA KIMBALL
17087 | ENSURE THAT SIGN POSTED NEXT TO THE CALL BUTTONS IN THE ELEVATOR LOBBY ON THE 10TH FLOOR AND THROUGHOUT THE BUILDING INCLUDES A PICTORIAL OR DIAGRAM OF A MAP SHOWING THE FLOOR LAYOUT AND EXACT LOCATION OF THE EXITS IN RELATION TO THE ELEVATORS | HighRise | LISA KIMBALL
17088 | THE LOCK-OUT/TAG-OUT EQUIPMENT AND SETS MUST BE READILY ACCESSIBLE AND PROPERLY LABELED - A LOCK-OUT/TAG-OUT IS NEEDED IN THE ELEVATOR ROOM IN THE GARAGE PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS A MINIMUM TWO (2) LOCK-OUT/TAG-OUT SETS FOR 4 TO 6 ELEVATORS A MINIMUM THREE (3) LOCK-OUT/TAG-OUT SETS FOR 7 OR MORE ELEVATORS | HighRise | LISA KIMBALL
17089 | ENSURE A SET OF ELEVATOR HOISTWAY TOOLS ARE ON SITE (PREFERABLY IN THE FIRE DEPOSITORY BOX) AND ACCESSIBLE IF NEEDED FOR EMERGENCIES | HighRise | LISA KIMBALL
17090 | PLEASE CONTACT INSPECTOR JUAN GARCIA BY EMAIL AT Juan.Garcia3@houstontx.gov OR 281.896.7084 IF YOU HAVE QUESTIIONS CONCERNING EVACUATION DRILLS, FIRE WARDEN TRAINING, ETC | HighRise | LISA KIMBALL
17091 | FYI | HighRise | LISA KIMBALL
17092 | FYI | HighRise | LISA KIMBALL
17093 | FIRE FIGHTING EQUIPMENT SHALL NOT BE BLOCKED OR OBSCURED FROM USE - FIRE HOSES ARE BLOCKED AND HIDDEN BY PARKED CARS IN THE PARKING GARAGE - ENSURE ADEQUATE SPACE IS PROVIDED AROUND FIRE HOSES | HighRise | LISA KIMBALL
17094 | PROVIDE SIGNS TO INDICATE THE LOCATION OF FIRE HOSE AND FIRE EXTINGUISHERS IN THE GARAGE | HighRise | LISA KIMBALL
17095 | FYI ON PLACEMENT AND VISIBILITY OF FIRE EXTINGUISHERS | HighRise | LISA KIMBALL
17096 | PLEASE CONTACT INSPECTOR JUAN GARCIA BY EMAIL AT Juan.Garcia3@houstontx.gov OR 281.896.7084 IF YOU HAVE QUESTIIONS CONCERNING EVACUATION DRILLS, FIRE WARDEN TRAINING, ETC | HighRise | LISA KIMBALL
17097 | PLEASE CONTACT INSPECTOR JUAN GARCIA BY EMAIL AT Juan.Garcia3@houstontx.gov OR 281.896.7084 IF YOU HAVE QUESTIIONS CONCERNING EVACUATION DRILLS, FIRE WARDEN TRAINING, ETC | HighRise | LISA KIMBALL
17098 | FYI PER MR. PARRA'S REQUEST | HighRise | LISA KIMBALL
17099 | PROVIDE ASHTRAYS IN THE 'SMOKING AREA' | HighRise | LISA KIMBALL
17100 | A TAMPER FLOW WAS FOUND IN THE STAIRWELL ON THE 7TH FLOOR WHICH APPEARS TO BE DISABLED - ENSURE THAT ALL SUPPRESSION AND DETECTION SYSTEM ELEMENTS ARE FULLY FUNCTIONING OR REMOVED THE ANSUL SYSTEM IN THE FUTURE FOODA FOOD COURT WAS LAST INSPECTED IN 2010 - ENSURE IT IS FULLY FUNCTIONING AND CURRENTLY TAGGED OR REMOVE | HighRise | LISA KIMBALL
17101 | ALL FIRE EXTINGUISHERS MUST BE INSPECTED AND TAGGED ANNUALLY - FIRE EXTINGUISHERS WERE FOUND WHICH HAVE EXPIRED INSPECTION TAGS: IN THE ROOF/PENTHOUSE ELEVATOR ROOM, THE FUTURE FOODA FOOD COURT, MECHANICAL ROOMS AND IN THE GARAGE | HighRise | LISA KIMBALL
17102 | FYI | HighRise | LISA KIMBALL
17103 | THE HOSES IN THE GARAGE WERE LAST INSPECTED AND TAGGED IN 2016 - ENSURE THE HOSES ARE TESTED ANNUALLY | HighRise | LISA KIMBALL
17104 | FYI PER MR. PARRA'S REQUEST | HighRise | LISA KIMBALL
17105 | FYI PER MR. PARRA'S REQUEST | HighRise | LISA KIMBALL
17106 | FYI PER MR. PARRA'S REQUEST | HighRise | LISA KIMBALL
17107 | CONNECTED BUT INDICATING "TROUBLE" - CONTACT SERVICE COMPANY TO RESOLVE THE ISSUE IMMEDIATELY | HighRise | LISA KIMBALL
17108 | ENSURE A SET OF INDEPENDENT SERVICE KEYS ARE ACCESSIBLE AND PROVIDED OUTSIDE OF THE FIRE DEPOSITORY BOX FOR EMERGENCIES | HighRise | LISA KIMBALL
17109 | POST "NO SMOKING" SIGNS IN THE GARAGE NEAR THE STAIRS - CIGARETTE BUTTS ARE LITTERED THROUGHOUT THE STAIRS IN THE GARAGE DESIGNATE A 'SMOKING AREA' WHICH SHOULD BE 25 (OR MORE) FEET AWAY FROM THE BUILDING EXITS | HighRise | LISA KIMBALL
17144 | NoData | HighRise | LISA KIMBALL
17184 | NoData | HighRise | LISA KIMBALL
17189 | NoData | HighRise | LISA KIMBALL
17190 | NoData | HighRise | LISA KIMBALL
17203 | NoData | HighRise | LISA KIMBALL
17204 | NoData | HighRise | LISA KIMBALL
17206 | NoData | HighRise | LISA KIMBALL
17208 | NoData | HighRise | LISA KIMBALL
17209 | NoData | HighRise | LISA KIMBALL
17210 | NoData | HighRise | LISA KIMBALL
17231 | NoData | HighRise | LISA KIMBALL
17282 | NoData | HighRise | LISA KIMBALL
17300 | NoData | HighRise | LISA KIMBALL
17344 | NoData | HighRise | LISA KIMBALL
17346 | NoData | HighRise | LISA KIMBALL
17347 | NoData | HighRise | LISA KIMBALL
17350 | NoData | HighRise | LISA KIMBALL
17384 | THE ALARM SYSTEM IS YELLOW AND RED TAGGED - A RED TAG WAS ISSUED ON 09/05/18 BY FIRE SAFE PROTECTION SERVICES (ILLEGIBLE #FAL 2882), A YELLOW TAG WAS ISSUED ON 07/17/18 BY FIRE SAFE PROTECTION SERVICES (JUAN ZAPON), A 2ND YELLOW TAG WAS ISSUED 09/03/18 BY FIRE SAFE PROTECTION SERVICES (ILLEGIBLE #1787293) AND MUST BE SERVICED OR REPAIRED IMMEDIATELY THE SPRINKLER SYSTEM IS YELLOW TAGGED - A YELLOW TAG WAS ISSUED ON 06/21/18 BY FIREWATER SERVICES (FRANK MANESCALCO) AND MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
17385 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
17386 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
17387 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
17388 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
17389 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT OR SERVICE THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
17390 | NoData | HighRise | LISA KIMBALL
17472 | NoData | HighRise | LISA KIMBALL
17474 | NoData | HighRise | LISA KIMBALL
17475 | NoData | HighRise | LISA KIMBALL
17477 | NoData | HighRise | LISA KIMBALL
17484 | NoData | HighRise | LISA KIMBALL
17558 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
17559 | THE CERTIFICATE OF OCCUPANCY, FIRE ALARM PERMIT AND ANY OTHER NECESSARY PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES | HighRise | LISA KIMBALL
17560 | ENSURE NO PARKED CARS, ETC. ARE BLOCKING ANY OF THE EMERGENCY EXIT DOORS THE BACK EXIT DOOR IN THE GYM IS STICKING; REPAIR THE DOOR TO ENSURE IT OPENS EASILY | HighRise | LISA KIMBALL
17561 | ENSURE ELECTRICAL ROOM, HVACROOM, FIRE SPRINKLER RISER ROOM, OFFICE DOOR WHERE FIRE ALARM IS LOCATED AND FIRE SPRINKLER RISER ROOMS MUST BE LABELED AS SUCH FOR READYIDENTIFICATION REMOVE "BOILER ROOM" SIGN WHERE THE BOILER HAS BEEN REMOVED | HighRise | LISA KIMBALL
17562 | NoData | HighRise | LISA KIMBALL
17563 | ALL OF THE BACK EXIT DOORS MUST BE IDENTIFIED AND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS | HighRise | LISA KIMBALL
17564 | INFORMATION TO BE INCLUDED IN FIREEVACUATION PLANS | HighRise | LISA KIMBALL
17565 | WHERE LOCAL FIRE MARSHAL APPROVALS AREREQUIRED BY REGULATORY AGENCIES, APPROVED FIRE SAFETY AND EVACUATION PLANSSHALL BE PREPARED, MAINTAINED AND POSTED IN GROUP E OCCUPANCIES | HighRise | LISA KIMBALL
17566 | THE FIRE ALARM DOES NOT HAVE ANY TAGS POSTED (INSTALLATION OR INSPECTION); HAVE A CERTIFIED INSPECTION COMPANY INSPECT AND TAG THE FIRE ALARM SYSTEM AS SOON AS POSSIBLE | HighRise | LISA KIMBALL
17567 | EXTINGUISHERS ARE ALL ACCEPTABLE AND BLUE TAGGED IN JANUARY 2020 THE FIRE SPRINKLER RISER WAS BLUE TAGGED IN JANUARY 2020 NO FURTHER ACTION REQUIRED | HighRise | LISA KIMBALL
17625 | NoData | HighRise | LISA KIMBALL
17672 | NoData | HighRise | LISA KIMBALL
17698 | NoData | HighRise | LISA KIMBALL
17705 | NoData | HighRise | LISA KIMBALL
17992 | NoData | HighRise | LISA KIMBALL
17997 | NoData | HighRise | LISA KIMBALL
18049 | NoData | HighRise | LISA KIMBALL
18091 | ENSURE ALL MOTORIZED EQUIPTMENT AND VEHICLES ARE REMOVED AWAY FROM THE EXIT STAIRWELLS AND DISCHARGES OF THE HIGH-RISE BUILDING | HighRise | LISA KIMBALL
18092 | REMOVE AND DISCONTINUE PARKING TRUCKS, WORK VEHICLES AND EQUIPMENT FROM UNDER THE NONSPRINKLERED EAVE/PROJECTION/OVERHANG OF THE HIGH-RISE BUILDING | HighRise | LISA KIMBALL
18093 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
18094 | REQUIRED EXIT ACCESSES, EXITS OR EXIT DISCHARGES SHALL BE CONTINUOUSLY MAINTAINED FREE FROM OBSTRUCTIONS OR IMPEDIMENTS TO FULL INSTANT USE - MAINTAIN A CLEAR PATH OF EGRESS FOR STAIRWELL B FROM THE HIGH-RISE BUILDING | HighRise | LISA KIMBALL
18095 | IMMEDIATELY CORRECT ALL VIOLATIONS NOTED IN THE SECTIONS BELOW - THIS NOTICE OF VIOLATION SERVES AS A WARNING - CONTINUED VIOLATIONS WILL BRING CITATIONS ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION - AND CONSTUCTION PERMITS - SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
18096 | ENSURE THAT FUELED EQUIPMENT AND VEHICLES ARE AT LEAST 25 FEET AWAY FROM THE OPENINGS AND EXITS OF THE HIGH-RISE BUILDING TO ENSURE EXHAUST FUMES DO NOT ENTER THE STRUCTURE | HighRise | LISA KIMBALL
18097 | NoData | HighRise | LISA KIMBALL
18098 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
18099 | THE HIGH-RISE BUILDING MUST BE SAFEGUARDED AND MAINTAINED DURING CONSTRUCTION | HighRise | LISA KIMBALL
18100 | NoData | HighRise | LISA KIMBALL
18101 | PARKED VEHICLES,AND EQUIPMENT TRUCKS WERE FOUND PARKED ON THE GROUND LEVEL OBSTRUCTING THE MEANS OF EGRESS - A CLEAR PATH OF EGRESS FROM THE HIGH-RISE BUILDING MUST BE MAINTAINED AT ALL TIMES - ABSTAIN FROM PARKING ANY EQUIPMENT OR VEHICLES IN AND AROUND ANY MEANS OF EGRESS | HighRise | LISA KIMBALL
18102 | NoData | HighRise | LISA KIMBALL
18103 | NoData | HighRise | LISA KIMBALL
18172 | NoData | HighRise | LISA KIMBALL
18176 | NoData | HighRise | LISA KIMBALL
18206 | NoData | HighRise | LISA KIMBALL
18211 | NoData | HighRise | LISA KIMBALL
18363 | NoData | HighRise | LISA KIMBALL
18479 | NoData | HighRise | LISA KIMBALL
18919 | NoData | HighRise | LISA KIMBALL
18925 | NoData | HighRise | LISA KIMBALL
18927 | NoData | HighRise | LISA KIMBALL
18940 | NoData | HighRise | LISA KIMBALL
18945 | NoData | HighRise | LISA KIMBALL
18964 | NoData | HighRise | LISA KIMBALL
18977 | NoData | HighRise | LISA KIMBALL
18980 | NoData | HighRise | LISA KIMBALL
19004 | NoData | HighRise | LISA KIMBALL
19017 | NoData | HighRise | LISA KIMBALL
19023 | NoData | HighRise | LISA KIMBALL
19025 | NoData | HighRise | LISA KIMBALL
19047 | NoData | HighRise | LISA KIMBALL
19071 | NoData | HighRise | LISA KIMBALL
19086 | NoData | HighRise | LISA KIMBALL
19094 | NoData | HighRise | LISA KIMBALL
19315 | NoData | HighRise | LISA KIMBALL
19316 | NoData | HighRise | LISA KIMBALL
19439 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
19440 | THE CERTIFICATE OF OCCUPANCY, FIRE ALARM PERMIT AND ANY OTHER NECESSARY PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES | HighRise | LISA KIMBALL
19441 | ENSURE NO PARKED CARS, ETC. ARE BLOCKING ANY OF THE EMERGENCY EXIT DOORS THE BACK EXIT DOOR IN THE GYM IS STICKING; REPAIR THE DOOR TO ENSURE IT OPENS EASILY | HighRise | LISA KIMBALL
19442 | ENSURE ELECTRICAL ROOM, HVACROOM, FIRE SPRINKLER RISER ROOM, OFFICE DOOR WHERE FIRE ALARM IS LOCATED AND FIRE SPRINKLER RISER ROOMS MUST BE LABELED AS SUCH FOR READYIDENTIFICATION REMOVE "BOILER ROOM" SIGN WHERE THE BOILER HAS BEEN REMOVED | HighRise | LISA KIMBALL
19443 | NoData | HighRise | LISA KIMBALL
19444 | ALL OF THE BACK EXIT DOORS MUST BE IDENTIFIED AND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS | HighRise | LISA KIMBALL
19445 | INFORMATION TO BE INCLUDED IN FIREEVACUATION PLANS | HighRise | LISA KIMBALL
19446 | WHERE LOCAL FIRE MARSHAL APPROVALS AREREQUIRED BY REGULATORY AGENCIES, APPROVED FIRE SAFETY AND EVACUATION PLANSSHALL BE PREPARED, MAINTAINED AND POSTED IN GROUP E OCCUPANCIES | HighRise | LISA KIMBALL
19447 | THE FIRE ALARM DOES NOT HAVE ANY TAGS POSTED (INSTALLATION OR INSPECTION); HAVE A CERTIFIED INSPECTION COMPANY INSPECT AND TAG THE FIRE ALARM SYSTEM AS SOON AS POSSIBLE | HighRise | LISA KIMBALL
19448 | EXTINGUISHERS ARE ALL ACCEPTABLE AND BLUE TAGGED IN JANUARY 2020 THE FIRE SPRINKLER RISER WAS BLUE TAGGED IN JANUARY 2020 NO FURTHER ACTION REQUIRED | HighRise | LISA KIMBALL
19698 | NoData | HighRise | LISA KIMBALL
19729 | NoData | HighRise | LISA KIMBALL
19741 | NoData | HighRise | LISA KIMBALL
19753 | NoData | HighRise | LISA KIMBALL
19775 | NoData | HighRise | LISA KIMBALL
19992 | NoData | HighRise | LISA KIMBALL
20035 | NoData | HighRise | LISA KIMBALL
20068 | NoData | HighRise | LISA KIMBALL
20091 | NoData | HighRise | LISA KIMBALL
20093 | NoData | HighRise | LISA KIMBALL
20112 | NoData | HighRise | LISA KIMBALL
20118 | NoData | HighRise | LISA KIMBALL
20131 | NoData | HighRise | LISA KIMBALL
20141 | "Electronic locks that unlock electronically from the egress side shall be fail safe and must be unlocked by a listed direct power interrupting device without time-delay" "An exit door from an elevator lobby may be controlled by an electronic lock with an emergency release device (direct inline power interrupting switch) on the lobby side, provided the building has an automatic fire alarm system, including smoke detectors, located in the lobby and corridors and/or a complete sprinkler system that is interconnected to the fire alarm system. The release device may be either a manual fire alarm pull station or a push button (minimum of 11/2 inch in size) located near the door with a sign stating: "PUSH/PULL TO RELEASE DOOR IN AN EMERGENCY". The locking device must release upon activation of the fire alarm or the sprinkler system and must be manually reset after being released." ENSURE THE FIRE ALARM PULL STATIONS INSIDE THE ELEVATOR LOBBY HAVE A SIGN STATING "PUSH/PULL TO RELEASE DOOR IN AN EMERGENCY" IN CASE OF AN EMERGENCY OR MAG LOCK MALFUNCTION TO AVOID CREATING A MANTRAP | HighRise | LISA KIMBALL
20142 | TENANT LEASING THE 14TH AND 15TH FLOORS OF 12 GREENWAY WISHES TO ADD A DEADBOLT LOCK TO THE ELEVATOR LOBBY DOORS (WHICH LEAD TO THE EMERGENCY EXIT STAIRWELLS) TO SECURE THE VACANT FLOORS - THE CODE MAINTAINS THAT REQUIRED EXIT ACCESSES, EXITS OR EXIT DISCHARGES SHALL BE CONTINUALLY MAINTAINED FREE FROM OBSTRUCTIONS OR IMPEDIMENTS - DEADBOLTS ON THE ELEVATOR LOBBY DOORS ARE CONSIDERED AN OBSTRUCTION AND AN IMPEDIMENT IN CASE OF A FIRE OR OTHER EMERGENCY WHERE THE ELEVATORS WOULD BE RECALLED TO THE LOBBY | HighRise | LISA KIMBALL
20143 | "Where means of egress doors are operated by power, such as doors with a photoelectric-actuated mechanism to open the door upon the approach of a person, or doors with power-assisted manual operation, the design shall be such that in the event of power failure, the door is capable of being opened manually to permit means of egress travel or closed where necessary to safeguard means of egress" | HighRise | LISA KIMBALL
20144 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
20145 | "It shall be unlawful to alter a building or structure in a manner that will reduce the capacity of the means of egress" | HighRise | LISA KIMBALL
20146 | "The path of egress travel along a means of egress shall not be interrupted by any building element other than a means of egress component as specified in this chapter" | HighRise | LISA KIMBALL
20147 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD TENANT LEASING THE 14TH AND 15TH FLOORS OF 12 GREENWAY WISHES TO ADD A DEADBOLT LOCK TO THE ELEVATOR LOBBY DOORS (WHICH LEAD TO THE EMERGENCY EXIT STAIRWELLS) TO SECURE THE VACANT FLOORS - THE FIRE CODE OPPOSES THE USE OF DEADBOLTS FOR USE IN THIS SITUATION THROUGHOUT CHAPTER 10 | HighRise | LISA KIMBALL
20148 | NoData | HighRise | LISA KIMBALL
20149 | NoData | HighRise | LISA KIMBALL
20150 | "Exits shall be unobstructed at all times." | HighRise | LISA KIMBALL
20151 | "An exit access shall not pass through a room that can be locked to prevent egress." | HighRise | LISA KIMBALL
20152 | "FAIL SAFE shall mean that the loss of power to the part of the system that locks the door shall automatically unlock the door" TENANT LEASING THE 14TH AND 15TH FLOORS OF 12 GREENWAY WISHES TO ADD A DEADBOLT LOCK TO THE ELEVATOR LOBBY DOORS (WHICH LEAD TO THE EMERGENCY EXIT STAIRWELLS) TO SECURE THE VACANT FLOORS - THE CODE ONLY ALLOWS A 'FAIL SAFE' LOCK ON THE ELEVATOR LOBBY DOORS | HighRise | LISA KIMBALL
20153 | "Whenever a building is occupied, egress doors shall be readily openable from the egress side without the use of a key or special knowledge or effort." | HighRise | LISA KIMBALL
20154 | Manually operated flush bolts or surface bolts that operate vertically are not permitted in buildings with occupancy Group B that have an occupant load of 10 more. | HighRise | LISA KIMBALL
20155 | "Where more than one means of egress is required by Section 1015.1 or 1019.1 from any accessible space, each accessible portion of the space shall be served by not less than two accessible means of egress" | HighRise | LISA KIMBALL
20355 | REMOVE DEADBOLT (PLAYGROUND EXIT) AND LOCKING DOOR HANDLE (FRONT ENTRY/EXIT) WHICH ARE BEING USED IN CONJUNCTION WITH PANIC HARDWARE | HighRise | LISA KIMBALL
20356 | NoData | HighRise | LISA KIMBALL
20357 | OBTAIN A CERTIFICATE OF OCCUPANCY AND ANY OTHER PERMITS REQUIRED PER THE CODE | HighRise | LISA KIMBALL
20358 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
20359 | INFORMATION TO BE INCLUDED IN FIRE SAFETYPLANS | HighRise | LISA KIMBALL
20360 | MISSING ILLUMINATED EMERGENCY EXIT SIGNS MUST BE INSTALLED AND TESTED | HighRise | LISA KIMBALL
20361 | THE CERTIFICATE OF OCCUPANCY AND ALLREQUIRED PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES | HighRise | LISA KIMBALL
20362 | POST ADDRESS CONSPICUOUSLY - THE LOCATION MUST HAVE A NUMERICAL ADDRESS WHICH IS CLEARLY VISIBLE FROM THE STREET | HighRise | LISA KIMBALL
20363 | INFORMATION TO BE INCLUDED IN FIRE EVACUATIONPLANS | HighRise | LISA KIMBALL
20364 | NoData | HighRise | LISA KIMBALL
20365 | WHERE LOCAL FIRE MARSHAL APPROVALS AREREQUIRED BY REGULATORY AGENCIES, APPROVED FIRE SAFETY AND EVACUATION PLANSSHALL BE PREPARED, MAINTAINED AND POSTED IN GROUP E OCCUPANCIES | HighRise | LISA KIMBALL
20366 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRESUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALSAND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ONSITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
22554 | NoData | HighRise | LISA KIMBALL
22557 | NoData | HighRise | LISA KIMBALL
22559 | NoData | HighRise | LISA KIMBALL
22563 | NoData | HighRise | LISA KIMBALL
22568 | NoData | HighRise | LISA KIMBALL
22619 | NoData | HighRise | LISA KIMBALL
22654 | NoData | HighRise | LISA KIMBALL
22661 | NoData | HighRise | LISA KIMBALL
22662 | NoData | HighRise | LISA KIMBALL
22663 | NoData | HighRise | LISA KIMBALL
22664 | NoData | HighRise | LISA KIMBALL
22665 | NoData | HighRise | LISA KIMBALL
22723 | NoData | HighRise | LISA KIMBALL
22805 | NoData | HighRise | LISA KIMBALL
22806 | NoData | HighRise | LISA KIMBALL
22811 | NoData | HighRise | LISA KIMBALL
22824 | NoData | HighRise | LISA KIMBALL
22829 | NoData | HighRise | LISA KIMBALL
22843 | NoData | HighRise | LISA KIMBALL
22847 | NoData | HighRise | LISA KIMBALL
22852 | NoData | HighRise | LISA KIMBALL
22861 | NoData | HighRise | LISA KIMBALL
23306 | NoData | HighRise | LISA KIMBALL
23313 | NoData | HighRise | LISA KIMBALL
23318 | NoData | HighRise | LISA KIMBALL
23319 | NoData | HighRise | LISA KIMBALL
23332 | NoData | HighRise | LISA KIMBALL
23347 | NoData | HighRise | LISA KIMBALL
23354 | NoData | HighRise | LISA KIMBALL
23355 | NoData | HighRise | LISA KIMBALL
23387 | NoData | HighRise | LISA KIMBALL
23389 | NoData | HighRise | LISA KIMBALL
23402 | NoData | HighRise | LISA KIMBALL
23410 | NoData | HighRise | LISA KIMBALL
23416 | NoData | HighRise | LISA KIMBALL
24367 | NoData | HighRise | LISA KIMBALL
24444 | THE DOWNTOWN TUNNEL (SUB GRADE/BASEMENT LEVEL) DISTRICT HAS MULTIPLE SECTIONS WHICH ARE NOT COMPLIANT WITH THE CODE CONCERNING EMERGENCY EGRESS, THEREFORE BY THE CODE, COULD "BECOME UNSAFE OR DEFICIENT BECAUSE OF INADEQUATE MEANS OF EGRESS" | HighRise | LISA KIMBALL
24445 | A PORTION OF THE TUNNEL DISTRICT WAS BEING REPAIRED - EXPOSED WALLS, WIRING AND AN OUTLET WERE EXPOSED - NO BUILDING DEPARTMENT PERMITS WERE POSTED | HighRise | LISA KIMBALL
24446 | THE DOWNTOWN TUNNEL (SUB GRADE/BASEMENT LEVEL) DISTRICT IS COMPARABLE TO AN "A" ASSEMBLY SHOULD COMPLY WITH TRAVEL DISTANCES TO AN EXIT AS SUCH | HighRise | LISA KIMBALL
24447 | NoData | HighRise | LISA KIMBALL
24448 | NoData | HighRise | LISA KIMBALL
24449 | NoData | HighRise | LISA KIMBALL
24450 | LOCKED GLASS DOORS LOCATED IN THE DOWNTOWN TUNNEL (SUB GRADE/BASEMENT LEVEL) DISTRICT OF 1500 LOUISIANA CREATED AN EXIT OBSTRUCTION TO OCCUPANTS - ALL OCCUPANTS WERE FORCED TO TURN AROUND AND TRAVEL SEVERAL HUNDRED FEET IN THE OPPOSITE DIRECTION TO LOCATE THE CLOSEST EGRESS AND SAFELY EXIT THE DOWNTOWN TUNNELS | HighRise | LISA KIMBALL
24451 | NoData | HighRise | LISA KIMBALL
24452 | SECTIONS OF THE DOWNTOWN TUNNEL DISTRICT WERE FOUND TO EXCEED 5O PEOPLE AT A TIME | HighRise | LISA KIMBALL
24453 | PANIC HARDWARE IS SUGGESTED TO ENABLE SAFE EGRESS TO EXIT STAIRWAYS THROUGHOUT THE DOWNTOWN TUNNEL (SUB GRADE/BASEMENT LEVEL) DISTRICT | HighRise | LISA KIMBALL
24454 | OBTAIN A CERTIFICATE OF OCCUPANCY/IES FOR THE DOWNTOWN TUNNEL/S WITHIN THE DOWNTOWN HOUSTON TUNNEL DISTRICT | HighRise | LISA KIMBALL
24455 | THE OWNER/OCCUPANT RESPONSIBILITY LIES WITH ALL OCCUPANCIES, ADDRESSES AND PROPERTY OWNERS (MUNICIPAL AND PRIVATE) WITHIN THE ENTIRE LENGTH OF THE DOWNTOWN TUNNEL (SUB GRADE/BASEMENT LEVEL) DISTRICT | HighRise | LISA KIMBALL
24456 | A CERTIFICATE OF OCCUPANCY MUST BE OBTAINED BEFORE A BUILDING OR STRUCTURE IS OCCUPIED | HighRise | LISA KIMBALL
24457 | NoData | HighRise | LISA KIMBALL
24458 | NoData | HighRise | LISA KIMBALL
24459 | NoData | HighRise | LISA KIMBALL
24460 | THE CODE REFERENCE TO "DEVICE, EQUIPMENT, SYSTEM, CONDITION, ARRANGEMENT, LEVEL OF PROTECTION OR ANY OTHER FEATURE" REQUIRING COMPLIANCE WITH THE PROVISIONS OF THIS CODE PERTAINS TO ALL ASPECTS THE ENTIRE DOWNTOWN TUNNEL (SUB GRADE/BASEMENT LEVEL) DISTRICT - THIS INCLUDES EGRESS WAYS, FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION SYSTEMS, EXITS, EMERGENCY PULL STATIONS, EMERGENCY POWER AND ILLUMINATION THE LIFE SAFETY SYSTEMS IN THE DOWNTOWN TUNNEL SYSTEM ARE NOT CONSCIOUSLY INSPECTED UNLESS THEY ARE TIED INTO A BUILDING (HIGH-RISE, HOTEL, GARAGE OR OTHERWISE) WHICH HAS PASSED INSPECTION | HighRise | LISA KIMBALL
24461 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
24462 | NoData | HighRise | LISA KIMBALL
24463 | NoData | HighRise | LISA KIMBALL
24464 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
24465 | ELECTRONIC LOCKS WERE FOUND ON DOORS IN THE DOWNTOWN TUNNEL SYSTEM WHICH PROHIBITED SAFE EGRESS FROM AND DID NOT HAVE AN EMERGENCY PULL STATION TO ALLOW ACCESS TO SAFETY OUTSIDE OF PREORDAINED HOURS | HighRise | LISA KIMBALL
24466 | FAIL SAFE DOORS ARE RECOMMENDED IN THE DOWNTOWN TUNNEL DISTRICT IN CONJUNCTION WITH PULL STATIONS TO ENABLE SAFE EGRESS | HighRise | LISA KIMBALL
24467 | LOCKED DOORS ARE COMMON IN THE DOWNTOWN TUNNEL (SUB GRADE/BASEMENT LEVEL) DISTRICT WHICH CREATE A DEAD-END; UNLOCKED DOORS, EMERGENCY PULL STATIONS, EMERGENCY RE-ENTRY PHONES OR PANIC/FIRE EXIT HARDWARE LEADING THROUGH A MEANS OF EGRESS TO AN EXIT WOULD ELIMINATE DEAD ENDS THE ENTIRE LENGTH OF THE DOWNTOWN TUNNEL (SUB GRADE/BASEMENT LEVEL) SYSTEM - WHICH IS COMPARABLE TO AN ASSEMBLY - SHOULD CONTAIN NO DEAD ENDS PER THE BUILDING CODE | HighRise | LISA KIMBALL
24468 | THE DOWNTOWN TUNNEL DISTRICT IS COMPARABLE TO A COVERED MALL AND EGRESS COMPONENTS SHOULD BE CONSIDERED TO BE EQUIVALENT | HighRise | LISA KIMBALL
24469 | NoData | HighRise | LISA KIMBALL
24470 | DOES THE DOWNTOWN TUNNEL DISTRICT HAVE AN ACTION PLAN FOR AN ACTIVE SHOOTER INCIDENT, BOMB THREAT OR SIMILAR EVENT? THE DOWNTOWN TUNNEL DISTRICT DOES NOT HAVE EVACUATION LOCATIONS FOR ASSISTED RESCUE OR ACCESSIBLE EXIT DISCHARGES WHICH LEAD DIRECTLY TO THE STREET LEVEL | HighRise | LISA KIMBALL
24471 | NoData | HighRise | LISA KIMBALL
24472 | A COMPLAINT WAS INVESTIGATED CONCERNING "A DISTINCT LIFE HAZARD" IN THE DOWNTOWN TUNNEL (SUB GRADE/BASEMENT LEVEL) DISTRICT - A DEAD-END CREATED BY LOCKED GLASS DOORS (AT 1500 LOUISIANA) AND A BLOCKED EXIT WHICH MADE FOR AN EGRESS ROUTE WITHOUT ANY EXITS WHICH EXTENDED SEVERAL HUNDRED FEET | HighRise | LISA KIMBALL
24473 | NoData | HighRise | LISA KIMBALL
24474 | NoData | HighRise | LISA KIMBALL
24475 | A BUILDING DEPARTMENT SENIOR INSPECTOR, BUILDING SECURITY AND A PROPERTY BUILDING ENGINEER WERE CONSULTED CONCERNING THE COMPLAINT; PHOTOS OF THE "SOUTH LOUISIANA TUNNEL" AND PORTIONS OF THE "DOWNTOWN TUNNEL LOOP" IN DOWNTOWN TUNNEL (SUB GRADE/BASEMENT LEVEL) DISTRICT WERE UPLOADED | HighRise | LISA KIMBALL
24476 | NoData | HighRise | LISA KIMBALL
24477 | ALL SECTIONS OF THE DOWNTOWN TUNNEL DISTRICT SHOULD HAVE ADDRESS NUMBERS TO FACILITATE EMERGENCY RESPONSE AN ADRESS NUMBER IS NEEDED TO OBTAIN A CERTIFICATE OF OCCUPANCY | HighRise | LISA KIMBALL
24478 | IS THE DOWNTOWN TUNNEL DISTRICT ADA COMPLAINT CONCERNING WHEELCHAIR EGRESS? | HighRise | LISA KIMBALL
25094 | NoData | HighRise | LISA KIMBALL
26405 | NoData | HighRise | LISA KIMBALL
26411 | NoData | HighRise | LISA KIMBALL
26447 | NoData | HighRise | LISA KIMBALL
26474 | NoData | HighRise | LISA KIMBALL
26492 | NoData | HighRise | LISA KIMBALL
26504 | NoData | HighRise | LISA KIMBALL
26522 | NoData | HighRise | LISA KIMBALL
26527 | NoData | HighRise | LISA KIMBALL
26540 | NoData | HighRise | LISA KIMBALL
26561 | NoData | HighRise | LISA KIMBALL
26563 | NoData | HighRise | LISA KIMBALL
26566 | NoData | HighRise | LISA KIMBALL
26575 | NoData | HighRise | LISA KIMBALL
26673 | NoData | HighRise | LISA KIMBALL
26698 | NoData | HighRise | LISA KIMBALL
26715 | NoData | HighRise | LISA KIMBALL
26736 | NoData | HighRise | LISA KIMBALL
26762 | NoData | HighRise | LISA KIMBALL
26772 | NoData | HighRise | LISA KIMBALL
26794 | NoData | HighRise | LISA KIMBALL
26797 | NoData | HighRise | LISA KIMBALL
26802 | NoData | HighRise | LISA KIMBALL
26808 | NoData | HighRise | LISA KIMBALL
26819 | NoData | HighRise | LISA KIMBALL
27156 | ADD RE-INSPECTION FEE FOR NON-COMPLIANCE.PAYMENT WAS REQUESTED 20APRIL20 | HighRise | LISA KIMBALL
27160 | NoData | HighRise | LISA KIMBALL
27164 | ADD RE-INSPECTION FEE FOR NON COMPLIANCE - DID NOT PAY PERMIT UPON REQUESTS IN APRIL AND MAY | HighRise | LISA KIMBALL
28108 | NoData | HighRise | LISA KIMBALL
28400 | NoData | HighRise | LISA KIMBALL
28484 | NoData | HighRise | LISA KIMBALL
28496 | NoData | HighRise | LISA KIMBALL
28510 | NoData | HighRise | LISA KIMBALL
28523 | NoData | HighRise | LISA KIMBALL
28530 | NoData | HighRise | LISA KIMBALL
28538 | NoData | HighRise | LISA KIMBALL
28542 | NoData | HighRise | LISA KIMBALL
28996 | THE FIRE ALARM WAS RED-TAGGED.ALL CORRECTIONS AND REPAIRS HAVE BEEN CONDUCTED AND RED TAG WAS REPLACED WITH A WHITE TAG.PICTURES ARE ATTACHED | HighRise | LISA KIMBALL
29069 | NoData | HighRise | LISA KIMBALL
29070 | NoData | HighRise | LISA KIMBALL
29770 | NoData | HighRise | LISA KIMBALL
29790 | NoData | HighRise | LISA KIMBALL
29797 | NoData | HighRise | LISA KIMBALL
29840 | NoData | HighRise | LISA KIMBALL
29855 | NoData | HighRise | LISA KIMBALL
29863 | NoData | HighRise | LISA KIMBALL
29953 | NoData | HighRise | LISA KIMBALL
29993 | NoData | HighRise | LISA KIMBALL
30059 | NoData | HighRise | LISA KIMBALL
30453 | NoData | HighRise | LISA KIMBALL
30528 | NoData | HighRise | LISA KIMBALL
30533 | NoData | HighRise | LISA KIMBALL
30538 | NoData | HighRise | LISA KIMBALL
31609 | NoData | HighRise | LISA KIMBALL
31640 | NoData | HighRise | LISA KIMBALL
31682 | NoData | HighRise | LISA KIMBALL
31689 | NoData | HighRise | LISA KIMBALL
31701 | NoData | HighRise | LISA KIMBALL
31708 | NoData | HighRise | LISA KIMBALL
31709 | NoData | HighRise | LISA KIMBALL
31716 | NoData | HighRise | LISA KIMBALL
31723 | NoData | HighRise | LISA KIMBALL
31727 | NoData | HighRise | LISA KIMBALL
31734 | NoData | HighRise | LISA KIMBALL
31743 | NoData | HighRise | LISA KIMBALL
32638 | A 911 KEY BOX IS NECESSARY AND SUGGESTED FOR EMERGENCY ACCESS WHERE SECURITY PERSONNEL MAY BE UNAVAILABLE OR INCAPABLE OF RESPONDING, ALLOWING ACCESS TO THE BUILDING, THE FIRE CONTROL ROOM, ETC. - ONLY ONE 24 HOUR SECURITY GUARD IS ON DUTY - IN AN EMERGENCY FORCED ENTRY MAY BE REQUIRED AND UNINTENTIONAL DAMAGE OR EXPENSE MAY RESULT THE FIRE ALARM ROOM/CONTROL ROOM HAS NO ACCESS UNLESS THE ALARM IS ACTIVATED - NO KEY AVAILABLE, NO 911 BOX | HighRise | LISA KIMBALL
32639 | PERTAINING TO FIRE EXTINGUISHERS IN THE PARKING GARAGE | HighRise | LISA KIMBALL
32640 | PROVIDE A COVER FOR OPEN JUNCTION BOX ON THE 6TH FLOOR | HighRise | LISA KIMBALL
32641 | EMERGENCY EXIT SIGNS ARE OUT ON THE 6TH FLOOR OF THE PARKING GARAGE - CALL SERVICE COMPANY IMMEDIATELY TO REPAIR OR REPLACE COMPONENTS EMERGENCY EGRESS LIGHTING MUST BE TESTED REGULARLY- CALL SERVICE COMPANY IMMEDIATELY TO REPAIR OR REPLACE ANY AND ALL NON- FUNCTIONING COMPONENTS PROVIDE EVIDENCE OF ANNUAL TESTING OF THE EMERGENCY ILLUMINATION AND ALL EMERGENCY EXIT LIGHTS OR MOST RECENT SERVICE OR REPAIR AND MAINTAIN ON SITE AT ALL TIMES | HighRise | LISA KIMBALL
32642 | PERTAINING TO SIGN NEEDED ON THE DOOR WHERE FLAMMABLES ARE STORED | HighRise | LISA KIMBALL
32643 | ENSURE THAT UL APPROVED RED CAN IN THE GENERATOR ROOM AND ELEVATOR ROOMS ARE EMPTIED DAILY - 16th FLOOR ELREVATOR ROOM | HighRise | LISA KIMBALL
32644 | FYI | HighRise | LISA KIMBALL
32645 | THE 'EMERGENCY STAIRWAY DOOR RELEASE' BUTTON COULD NOT BE LOCATED ON THE ALARM PANEL - LOCATE AND CLEARLY IDENTIFY THIS BUTTON AS TO BE OBVIOUS | HighRise | LISA KIMBALL
32646 | Facility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system must be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual REQUIRED FOR GARAGE " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED FOR GARAGE " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 5 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - N/A - REQIRED IF BOILERS ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
32647 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
32648 | SIGNS SAY "NO-RE-ENTRY" ON THE 15TH (STAIR C), 13TH AND 12TH FLOORS BUT BOTH ARE UNLOCKED - ENSURE ALL POSTED STAIRWELL SIGNS (ON THESE FLOORS AND NEAREST ABOVE AND BELOW) AGREE WITH DOOR FUNCTION | HighRise | LISA KIMBALL
32649 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN UTILITY ROOMS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR - ELECTRICAL/MECHANICAL ROOMS ON THE 15TH, 14TH, 13TH,12TH, 11TH, 10TH &10TH FLOOR STAIR C, 9TH, 8TH, 7TH, 6TH, 5TH, 4TH & 4TH FLOOR STAIR A, 3RD & 3RD FLOOR STAIR A | HighRise | LISA KIMBALL
32650 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
32651 | PERTAINING TO PLACEMENT AND DISTANCE OF FIRE EXTINGUISHERS ADDITIONAL FIRE EXTINGUISHERS ARE NEEDED THROUGHOUT THE GARAGE (SUGGESTED PLACEMENT IS NEAR THE STAIRS BUT VISIBLE FROM THE PARKED CARS) | HighRise | LISA KIMBALL
32652 | REPAIR ANY OPENINGS IN THE CIELING AND WALLS THROUGHOUT THE BUILDING - THE 6TH FLOOR HAS ALL CIELING TILES REMOVED - REPLACE TILES IMMEDIATELY OR CALL FIRE PROTECTION COMPANY TO ADJUST ALL HEADS TO OFFER PROTECTION TO THIS VACANT FLOOR | HighRise | LISA KIMBALL
32653 | THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH - MECHANICAL ROOMS MUST ALSO INDICATE "ELECTRICAL ROOM" ON THE 15TH, 14TH, 13TH,12TH, 11TH, 10TH, 9TH, 8TH, 7TH, 6TH, 5TH, 4TH, 3RD AND 2ND FLOORS ALL ELECTRICAL CIRCUIT BREAKERS IN ELECTRICAL PANELS MUST BE CLEARLY AND CORRECTLY LABELED ON THE 15TH, 14TH, 13TH FLOORS AND THROUGHOUT THE BUILDING | HighRise | LISA KIMBALL
32654 | PROVIDE SIGN TO INDICATE FLAMMABLES IN THE ROOM IN THE GARAGE ON THE 5TH FLOOR | HighRise | LISA KIMBALL
32655 | SUPPLY KEYS FOR THE EXTERIOR DOORS, MECHANICAL ROOMS, ELECTRICAL ROOMS, ELEVATOR ROOM, ROOF ACCESS, ELEVATOR CAR, ALARM ROOM, SPRINKLER RISER ROOM, PUMP ROOM, HVAC, ETC IN 911 KEY BOX THERE WAS NO ACCESS (OR KEY ON THE KEY RINGS SUPPLIED IN THE FIRE DEPOSITORY BOX) TO THE JANITOR'S CLOSETS ON FLOORS 6 THROUGH 14 | HighRise | LISA KIMBALL
32656 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
32657 | FYI | HighRise | LISA KIMBALL
32658 | THE LOCATION OF THE FIRE PUMP ROOM AND GENERATORS (IN GARAGE) MUST BE IDENTIFIED AND LABELED AS SUCH | HighRise | LISA KIMBALL
32659 | FYI | HighRise | LISA KIMBALL
32660 | FYI - PERTAINING TO TRAINING AND CERTIFICATION WITH INSPECTOR JUAN GARCIA | HighRise | LISA KIMBALL
32661 | FYI - PERTAINING TO TRAINING AND CERTIFICATION WITH INSPECTOR JUAN GARCIA | HighRise | LISA KIMBALL
32662 | STANDARDS AND CODES PERTAINING TO EMERGENCY ACCESS STATE THE NEED FOR A 911 KEY BOX OR KNOX BOX DUE TO THE LOCKED DOORS NOT ALLOWING ACCESS TO MECHANICAL ROOMS, ELECTRICAL ROOMS, ELEVATOR ROOMS, SPRINKLER RISER ROOMS AND/OR FIRE ALARM ROOMS THE PROPERTY HAS 24 HOUR SECURITY ON-SITE; IF SECURITY PERSONNEL RESPONSE IS HAMPERED, WITHOUT A 911 BOX TO ALLOW IMMEDIATE ENTRY TO THE BUILDING, EMERGENCY OPERATIONS CAN BE DELAYED | HighRise | LISA KIMBALL
32663 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
32664 | ONLY ONE ELEVATOR HOUSTWAY KEY WAS FOUND IN THE FDB - SUPPLY ONE ADDITIONAL KEY TO MAINTAIN THE MINUMUM STANDARD OF HAVING 2 PER THE FIRE CODE | HighRise | LISA KIMBALL
32665 | ALL ELECTRICAL ROOMS, HVAC ROOMS, MECHANICAL ROOMS, IT ROOMS, ELEVATOR ROOMS, FIRE SPRINKLER RISER ROOMS, FIRE ALARM ROOMS AND TRANSFORMER ROOMS MUST BE LABELED AS SUCH FOR READY IDENTIFICATION - IDENTIFY AND LABEL THE ELECTRICAL ROOM ON THE 2ND FLOOR | HighRise | LISA KIMBALL
32666 | FYI - PERTAINING TO TRAINING AND CERTIFICATION WITH INSPECTOR JUAN GARCIA | HighRise | LISA KIMBALL
32667 | ALL FIRE EXTINGUISHERS MUST BE HUNG - NOT STORED ON THE FLOOR - IN THE 2603 CLUB ROOM | HighRise | LISA KIMBALL
32668 | FYI - PERTAINING TO TRAINING AND CERTIFICATION WITH INSPECTOR JUAN GARCIA | HighRise | LISA KIMBALL
32669 | REMOVE AND DISCONTINUE STORAGE OF COMBUSTIBLES IN THE ELECTRICAL ROOMS, MECHANICAL ROOMS, ELEVATOR ROOMS, FIRE ALARM ROOM AND THE SPRINKLER RISER ROOM - RELOCATE THE FLAMMABLE STORAGE CABINET FROM THE 2ND FLOOR STORAGE WHICH IS AN ELECTRICAL ROOM | HighRise | LISA KIMBALL
32670 | AN EXIT ENCLOSURE SHALL NOT BE USED FOR ANY PURPOSE OTHER THAN MEANS OF EGRESS - REMOVE AND DISCONTINUE STORAGE ON THE 13TH FLOOR IN STAIR C | HighRise | LISA KIMBALL
32671 | FYI - PERTAINING TO TRAINING AND CERTIFICATION WITH INSPECTOR JUAN GARCIA | HighRise | LISA KIMBALL
32672 | DOOR CLOSURES FOUND ON THE 6TH FLOOR (STAIR C) IS NOT WORKING PROPERLY - ENSURE ALL STAIRWELL DOORS ARE LATCHING SHUT | HighRise | LISA KIMBALL
32673 | CABINETS CONTAINING FIRE FIGHTING EQUIPTMENT MUST INDICATE THE EQUIPTMENT CONTAINED THEREIN - "FIRE HOSE" AND/OR "FIRE EXTINGUISHER" - ID HOSE CABINET ON ROOF AND ALL FIRE CABINETS WHICH CONTAIN A FIRE EXTINGUISHER | HighRise | LISA KIMBALL
32674 | PERTAINING TO FIRE EXTINGUISHERS IN THE PARKING GARAGE | HighRise | LISA KIMBALL
32675 | FYI - PERTAINING TO TRAINING AND CERTIFICATION WITH INSPECTOR JUAN GARCIA | HighRise | LISA KIMBALL
32676 | FYI - PERTAINING TO TRAINING AND CERTIFICATION WITH INSPECTOR JUAN GARCIA | HighRise | LISA KIMBALL
32677 | PLEASE CONFER WITH INSPECTOR JUAN GARCIA BY EMAIL AT Juan.Garcia3@houstontx.gov IF YOU HAVE QUESTIIONS CONCERNING EVACUATION DRILLS, FIRE WARDEN TRAINING, ETC | HighRise | LISA KIMBALL
32678 | REMOVE ALL EVIDENCE OF INACTIVE/NON FUNCTIONING ELECTRICAL EQUIPTMENT IN THE DEAD ELECTRICAL ROOM ON THE 14TH FLOOR | HighRise | LISA KIMBALL
32679 | THE 16TH FLOOR SHOULD BE A RE-ENTRY FLOOR - READ CODE WORD '97 TOP RE-ENTRY THE RE-ENTRY PHONES ON THE 16TH FLOOR IN STAIRWELLS A AND C ARE NOT FUNCTIONING - ENSURE THESE PHONES ARE TESTED OFTEN | HighRise | LISA KIMBALL
32803 | A FIREFIGHTER INQUIRED AS TO HOW TO FILE A COMPLAINT ON A BUILDING HE KNEW WOULD BE DANGEROUS FOR FIRE COMPANIES TO RESPOND TO IN AN EMERGENCY. I INSTRUCTED HIM TO CALL 311 AND CONTACT THE RESPONSIBLE INSPECTOR OR SR. INSPECTOR - UPON RESEARCHING THE ADDRESS TO FIND WHICH TEAM WAS RESPONSIBLE FOR INSPECTING THIS LOCATION, I FOUND A CONFLICT IN THE DESCRIPTION AND USE OF THE LOCATION. I INFORMED SR. BAKER OF THE SITUATION AND ASKED HIM WHICH INSPECTOR WAS ASSIGNED TO THIS ZIP CODE - THE RESPONSIBLE INSPECTOR WAS OFF DUTY AND WAS GIVEN PERMISSION BY SR. BAKER TO MEET WITH THE FIREFIGHTER ON LOCATION TO ASSESS THE SITUATION. UPON ARRIVAL OF THE ADDRESS (LEGALLY ADDRESSED AS 600 WESTBURY SQUARE) I OBSERVED AND PHOTOGRAPHED WHAT APPEARED TO BE AN ABANDONED BUILDING WITH AN INCOMPLETE ADDRESS (MISSING THE 1ST 2 NUMBERS ON THE ENTRANCE SHOWS THE ADDRESS AS "25"),BOARDED UP ENTRANCES, EXITS AND WINDOWS, OPEN JUNCTION BOXES, A DETERIORATING EXTERIOR STAIRWELL. THERE WERE NO EXTINGUISHERS, FIRE DETECTION OR FIRE SUPPRESION ELEMENTS OBSERVED. THE FIREFIGHTER INFORMED ME THAT THERE WERE OCCUPANTS ON THE SECOND FLOOR - I OBSERVED SEVERAL ACTIVE MAILBOXES IN THE COURTYARD WHICH INDICATE THE VALIDITY OF HIS STATEMENT. A PROPERTY MANAGER ARRIVED CONFIRMING THE FACT THAT SEVERAL APARTMENTS WERE OCCUPIED ON THE 2ND FLOOR. HE APPEARED ANXIOUS AND ASKED THAT I LEAVE THE PROPERTY. FURTHER RESEARCH SHOWS HABITABILITY INVESTIGATED THIS AS A "DANGEROUS BUILDING" IN 2017, 2018, 2019. THIS BUILDING IS STILL LISTED AS A B OCCUPANCY (UNDER THE LEGAL ADDRESS) AND APPEARS UNFIT TO BE DESIGNATED AS AN R OCCUPANCY. I CONTACTED THE BUILDING DEPARTMENT (CASEY TOMLIN) AND AM FORWARDING THE COMPLAINT TO THE APARTMENT TEAM FOR INSPECTION AND RESOLUTION | HighRise | LISA KIMBALL
32804 | NoData | HighRise | LISA KIMBALL
32805 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED | HighRise | LISA KIMBALL
32806 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
32807 | NO CERTIFICATE OF OCCUPANCY WAS LOCATED FOR THIS BUILDING THIS BUILDING SHOULD NOT BE OCCUPIED AS A RESIDENTIAL OCCUPANCY UNTIL THE BUILDING DEPARTMENT HAS GRANTED APPROVAL FOR THIS PURPOSE THIS OCCUPANCY HAS BEEN PLACED ON A HARD HOLD | HighRise | LISA KIMBALL
32808 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
32809 | NoData | HighRise | LISA KIMBALL
32810 | NoData | HighRise | LISA KIMBALL
32811 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
32812 | NoData | HighRise | LISA KIMBALL
32813 | THE BUILDING IS LISTED AS A B OCCUPANCY (UNDER THE LEGAL ADDRESS OF 600 WETBURY SQUARE) BUT IS BEING USED AS AN R OCCUPANCY - VISIT THE HOUSTON PERMITTING CENTER AT 1002 WASHINGTON AVENUE TO REQUEST A CHANGE OF OCCUPANCY | HighRise | LISA KIMBALL
32814 | THE CORRECT ADDRESS MUST BE CLEARLY AND CONSPICUOUSLY POSTED TO AID IN EMERGENCY RESPONSE | HighRise | LISA KIMBALL
32848 | A CITATION WILL BE WRITTEN IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
32849 | THE CERTIFICATE OF OCCUPANCY AND ALL PERMITS SHOULD BE POSTED IN THE BUSINESS | HighRise | LISA KIMBALL
32850 | OBTAIN A CERTIFICATE OF OCCUPANCY AND ANY REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER | HighRise | LISA KIMBALL
32851 | ATTEND FIRE WARDEN TRAINING AND OBTAIN A CERTIFICATE OF COMPLETION VISIT http://houstontx.gov/fire/HFMO/highrisecert.html TO SIGN UP FOR THE OPEN CLASS (MUST LOG ON AND SIGN UP BEFORE THE DEADLINE) OBTAINING A CERTIFICATE OF OCCUPANCY AND ANY/ALL PERMITS IS THE RESPONSIBILITY OF THE OWNER/OCCUPANT | HighRise | LISA KIMBALL
32852 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
32853 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRE CODE OFFICIAL IS DEPENDENT UPON SUCCESSFUL COMPLETION OF THREE COMPONENTS; ONE OF WHICH IS FIRE WARDEN HIGH-RISE CERTIFICATION CLASS | HighRise | LISA KIMBALL
32854 | ATTENDANCE AT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH- RISE FIRE WARDENS | HighRise | LISA KIMBALL
32855 | CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
32856 | MEMBERS OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
32857 | NoData | HighRise | LISA KIMBALL
32858 | REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Rise or Mid-Rise Atruim Certification Training may send attendees to the following monthly seminars at no cost. Monthly seminars are available for management employees and tenant fire wardens of high-rise buildings who need to be certified. Certificates shall be valid for a period of five years from the date of training. There is no charge for attending these seminars. The only cost incurred may be parking fees, if applicable. Many buildings will have different fire safety features. The building management from each building represented is required to inform its employees and Fire Wardens of their specific fire safety features to complete the certification. Please note this training is not valid for Mid Rise Evacuation Training. For information on mid rise training please visit the HFD Mid Rise Fire Certification Webpage. Additional training availability information: The Houston Fire Department has set up and implemented a list of all high- rise buildings for Fire Safety Plan approvals. This list was set up to ensure that priority is given to buildings that have the greatest need while also providing each building an equal opportunity. The list of buildings is separated into two groups based on whether the building is an occupancy where people sleep, such as hotel, apartments, and condominiums or those buildings where people do not sleep, such as office buildings. Buildings are then sub- grouped by no sprinkler system, partial sprinkler system, or complete sprinkler systems before sorting by building height. The highest priority building is the residential building that is non-sprinklered, and the tallest in height. Our goal is to provide the needed services to approve each building within a two-year cycle. Buildings desiring to expedite the process also have three additional options. The monthly open high-rise certification seminar is for buildings that have requested to send a limited number of fire wardens and building management employees to a class that is open to all high-rise buildings. The class information is not specific to any particular building and requires building management to supplement the training with their building specifics. An inspector/instructor in the Life Safety Bureau, Public Education Section - High-rise Fire Safety Plan Approvals, may be obtained to provide training outside his regular work hours on an overtime basis. This may be done by contacting Diana Cardenas by e-mail at: diana.cardenas@houstontx.gov. This should be done prior to payment of a required permit fee so that an instructor can be assigned to made contact with the requesting party, to assist the requesting party with information on the application for over-time training and payment of the permit fees, and to schedule a mutually convenient training date. A City of Houston permit fee is required to schedule an inspector/instructor. The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019). Having a City of Houston Fire Marshal approved consultant perform the training. The process to receive an approved Fire Safety Plan consist of the three following essential training elements conducted by persons, institutions or companies approved by the Fire Marshal according to regulations established by the Fire Marshal: a consultation with building management, an approved certification training for Fire Wardens and building employees, and a fire drill supervised by persons, institutions or companies approved by the Fire Marshal. | HighRise | LISA KIMBALL
32859 | ALL OCCUPANTS OF THE BUILDING SHALL PARTICIPATE IN THE FIRE DRILLS AS REQUIRED BY THE CODE OFFICIAL AND THE FIRE CODE | HighRise | LISA KIMBALL
32860 | OCCUPANCY AND SUITE NUMBER ARE NOT LISTED IN ILMS COMPUTER SYSTEM - OBTAIN CERTIFICATE OF OCCUPANCY FROM THE HOUSTON PERMITTING CENTER WITH CURRENT INFORMATION | HighRise | LISA KIMBALL
32861 | APPROVAL OF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFUL COMPLETION OF SEVERAL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF A COMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS | HighRise | LISA KIMBALL
32862 | THE CERTIFICATE OF COMPLETION OF FIRE WARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
32937 | A FIREFIGHTER INQUIRED AS TO HOW TO FILE A COMPLAINT ON A BUILDING HE KNEW WOULD BE DANGEROUS FOR FIRE COMPANIES TO RESPOND TO IN AN EMERGENCY. I INSTRUCTED HIM TO CALL 311 AND CONTACT THE RESPONSIBLE INSPECTOR OR SR. INSPECTOR - UPON RESEARCHING THE ADDRESS TO FIND WHICH TEAM WAS RESPONSIBLE FOR INSPECTING THIS LOCATION, I FOUND A CONFLICT IN THE DESCRIPTION AND USE OF THE LOCATION. I INFORMED SR. BAKER OF THE SITUATION AND ASKED HIM WHICH INSPECTOR WAS ASSIGNED TO THIS ZIP CODE - THE RESPONSIBLE INSPECTOR WAS OFF DUTY AND WAS GIVEN PERMISSION BY SR. BAKER TO MEET WITH THE FIREFIGHTER ON LOCATION TO ASSESS THE SITUATION. UPON ARRIVAL OF THE ADDRESS (LEGALLY ADDRESSED AS 600 WESTBURY SQUARE) I OBSERVED AND PHOTOGRAPHED WHAT APPEARED TO BE AN ABANDONED BUILDING WITH AN INCOMPLETE ADDRESS (MISSING THE 1ST 2 NUMBERS ON THE ENTRANCE SHOWS THE ADDRESS AS "25"),BOARDED UP ENTRANCES, EXITS AND WINDOWS, OPEN JUNCTION BOXES, A DETERIORATING EXTERIOR STAIRWELL. THERE WERE NO EXTINGUISHERS, FIRE DETECTION OR FIRE SUPPRESION ELEMENTS OBSERVED. THE FIREFIGHTER INFORMED ME THAT THERE WERE OCCUPANTS ON THE SECOND FLOOR - I OBSERVED SEVERAL ACTIVE MAILBOXES IN THE COURTYARD WHICH INDICATE THE VALIDITY OF HIS STATEMENT. A PROPERTY MANAGER ARRIVED CONFIRMING THE FACT THAT SEVERAL APARTMENTS WERE OCCUPIED ON THE 2ND FLOOR. HE APPEARED ANXIOUS AND ASKED THAT I LEAVE THE PROPERTY. FURTHER RESEARCH SHOWS HABITABILITY INVESTIGATED THIS AS A "DANGEROUS BUILDING" IN 2017, 2018, 2019. THIS BUILDING IS STILL LISTED AS A B OCCUPANCY (UNDER THE LEGAL ADDRESS) AND APPEARS UNFIT TO BE DESIGNATED AS AN R OCCUPANCY. I CONTACTED THE BUILDING DEPARTMENT (CASEY TOMLIN) AND AM FORWARDING THE COMPLAINT TO THE APARTMENT TEAM FOR INSPECTION AND RESOLUTION | HighRise | LISA KIMBALL
32938 | NoData | HighRise | LISA KIMBALL
32939 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED | HighRise | LISA KIMBALL
32940 | NO PERMITS POSTED ON SITE - PERMITS ISSUED BY THE BUILDING DEPARTMENT MUST BE POSTED AND ENFORCED BY THE FIRE MARSHALS OFFICE | HighRise | LISA KIMBALL
32941 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
32942 | NO CERTIFICATE OF OCCUPANCY WAS LOCATED FOR THIS BUILDING THIS BUILDING SHOULD NOT BE OCCUPIED AS A RESIDENTIAL OCCUPANCY UNTIL THE BUILDING DEPARTMENT HAS GRANTED APPROVAL FOR THIS PURPOSE THIS OCCUPANCY HAS BEEN PLACED ON A HARD HOLD | HighRise | LISA KIMBALL
32943 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
32944 | NoData | HighRise | LISA KIMBALL
32945 | NoData | HighRise | LISA KIMBALL
32946 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
32947 | NoData | HighRise | LISA KIMBALL
32948 | THE BUILDING IS LISTED AS A B OCCUPANCY (UNDER THE LEGAL ADDRESS OF 600 WESTBURY SQUARE) BUT IS BEING USED AS AN R OCCUPANCY - VISIT THE HOUSTON PERMITTING CENTER AT 1002 WASHINGTON AVENUE TO REQUEST A CHANGE OF OCCUPANCY | HighRise | LISA KIMBALL
32949 | THE CORRECT ADDRESS MUST BE CLEARLY AND CONSPICUOUSLY POSTED TO AID IN EMERGENCY RESPONSE | HighRise | LISA KIMBALL
33806 | NoData | HighRise | LISA KIMBALL
33807 | NoData | HighRise | LISA KIMBALL
33808 | NoData | HighRise | LISA KIMBALL
33809 | NoData | HighRise | LISA KIMBALL
33810 | NoData | HighRise | LISA KIMBALL
33811 | NoData | HighRise | LISA KIMBALL
34051 | A TOWNHOME IN A GATED COMMUNITY WAS FOUND WELL PREPARED FOR FOSTER CARE.THE ADDRESS IS WELL MARKED.THE FIRE EXTINGUISHER IS NEW - PURCHASES W/IN YEAR; OWNER WAS INSTRUCTED TO INSPECT AND TAG IT ANNUALLYACTIVE SMOKE DETECTORS FOUND ABOVE ROOMS IN HALLWAYS.AN EVACUATION MAP IS POSTED.WE DISCUSSED FIRE DRILLS IN THE HOME.ALL ELECTRICAL OUTLETS WERE FOUND CAPPED. | HighRise | LISA KIMBALL
34105 | A PERMIT FOR BOTH THE KNOX BOX AND THE 911 BOX (IN THE OFFICE) MUST BE PAID FOR ANNUALLY | HighRise | LISA KIMBALL
34106 | NoData | HighRise | LISA KIMBALL
34107 | NoData | HighRise | LISA KIMBALL
34108 | NoData | HighRise | LISA KIMBALL
34109 | NoData | HighRise | LISA KIMBALL
34110 | NoData | HighRise | LISA KIMBALL
34111 | NoData | HighRise | LISA KIMBALL
34112 | PLEASE REVIEW LSB STANDARD 06 TO ENSURE ALL CONTENTS ARE CORRECTLY LABELED AND ORGANIZED WITHIN THE KEY BOX (IN THE OFFICE)ALL CONTENTS LISTED IN LSB 06 MUST BE CONTAINED IN THIS KEY BOX | HighRise | LISA KIMBALL
34113 | ENSURE THE KEY BOX IS SUPPLIED WITH ALL CONTENTS LISTED BELOW | HighRise | LISA KIMBALL
34114 | THE PERMIT FOR THE KNOX BOX AND THE KEY BOX MUST BE PAID ANNUALLY | HighRise | LISA KIMBALL
34115 | A KEY BOX IS SUPPLIED IN THE OFFICE; ENSURE THIS IS KNOWN AND LABELED AS SUCHVERIFY AND UPDATE ALL KEYS AND TAGS IN THE KEY BOX | HighRise | LISA KIMBALL
34116 | KEYS AND INSTRUCTIONS ARE REQUIRED IN THE KNOX BOX TO CONTROL ACCESS GATES | HighRise | LISA KIMBALL
34117 | PLACE UPDATED KEYS IN THE KNOX BOX;TEMPORARY KEYS (TAGGED WITH STICKY NOTES) AND INSTRUCTIONS HAVE BEEN SECURED UNTIL UPDATED KEYS WITH PERMANENT TAGS ARE READY.CALL THE INSPECTOR 832.216.7574 FOR ACCESS INTO THE KNOX BOX | HighRise | LISA KIMBALL
34212 | NoData | HighRise | LISA KIMBALL
34222 | POST CERTIFICATE OF OCCUPANCY CONSPICUOUSLY ON SITE | HighRise | LISA KIMBALL
34223 | NOTIFICATIONMUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OFSERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT OR SERVICE TO THEOWNER/OCCUPANT AND TO THE JURISDICTION – BY PHONE 713.884.3143 AND EMAIL AT HFD.DISPATCH3@houstontx.govTHE FIREDEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMALOPERATIONAL STATUS | HighRise | LISA KIMBALL
34224 | THE FIRE ALARM IS RED TAGGED DUE TO A SPRINKLER ACCIDENT ON THE 2ND FLOOR; ENSURE ALL FIRE DETECTION EQUIPMENT (WIRING, CONNECTIONS, DETECTORS, PANELS, ETC) WHICH WAS EXPOSED TO WATER IS NOT DAMAGED OR REPLACED IF DAMAGED. | HighRise | LISA KIMBALL
34225 | INSPECT ALL FIRE DETECTION AND FIRE SUPPRESSION EQUIPMENT TO ENSURE FUNCTIONALITY | HighRise | LISA KIMBALL
34226 | ALL FIRE DETECTION AND FIRE SUPPRESSION ELEMENTS MUST BE FULLY FUNCTIONAL AND BLUE TAGGED | HighRise | LISA KIMBALL
34228 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY AREPLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT ORSERVICE TO THE OWNER/OCCUPANT AND TO THE JURISDICTION – BY PHONE 713.884.3143 ANDEMAIL AT HFD.DISPATCH3@houstontx.govTHE FIREDEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMALOPERATIONAL STATUS | HighRise | LISA KIMBALL
34229 | THE FIRE ALARM SYSTEM IS RED TAGGED - TAG WAS ISSUED 07/22/20 AND SYSTEM MUST BESERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
34475 | NoData | HighRise | LISA KIMBALL
34495 | NoData | HighRise | LISA KIMBALL
34530 | NoData | HighRise | LISA KIMBALL
34541 | NoData | HighRise | LISA KIMBALL
34544 | NoData | HighRise | LISA KIMBALL
34555 | NoData | HighRise | LISA KIMBALL
34559 | NoData | HighRise | LISA KIMBALL
34731 | NoData | HighRise | LISA KIMBALL
34779 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY) ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENTOR SERVICE TO THE OWNER/OCCUPANT AND TO THE JURISDICTION – BY PHONE 713.884.3143 AND EMAIL AT HFD.DISPATCH3@houstontx.govTHE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
34780 | THE FIRE ALARM SYSTEM IS RED TAGGED - TAG WAS ISSUED 07/22/20 AND SYSTEM MUST BE SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
35278 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY) ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENTOR SERVICE TO THE OWNER/OCCUPANT AND TO THE JURISDICTION – BY PHONE 713.884.3143 AND EMAIL AT HFD.DISPATCH3@houstontx.govTHE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
35279 | THE FIRE ALARM SYSTEM IS RED TAGGED - TAG WAS ISSUED 07/22/20 AND SYSTEM MUST BE SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
35436 | NoData | HighRise | LISA KIMBALL
35437 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY) ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENTOR SERVICE TO THE OWNER/OCCUPANT AND TO THE JURISDICTION – BY PHONE 713.884.3143 AND EMAIL AT HFD.DISPATCH3@houstontx.govTHE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
35438 | THE FIRE ALARM SYSTEM IS RED TAGGED - TAG WAS ISSUED 07/22/20 AND SYSTEM MUST BE SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
35572 | THE ALARM SYSTEM IS RED TAGGED - TAG WAS ISSUED MARCH 2020 AND SYSTEM MUST BESERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
36004 | NoData | HighRise | LISA KIMBALL
36029 | NoData | HighRise | LISA KIMBALL
36046 | NoData | HighRise | LISA KIMBALL
36074 | NoData | HighRise | LISA KIMBALL
36341 | NoData | HighRise | LISA KIMBALL
36580 | REINSPECTION FEE FOR UNPAID F7; EMAILS SENT ON 6/23 AND 7/21 WITH INSTRUCTIONS FOR PAYMENT | HighRise | LISA KIMBALL
36581 | REINSPECTION FEE FOR UNPAID P2; EMAIL SENT ON 7/21 WITH INSTRUCTIONS FOR PAYMENT | HighRise | LISA KIMBALL
36584 | REINSPECTION FEE FOR UNPAID H1; EMAIL SENT ON 7/21 WITH INSTRUCTIONS FOR PAYMENT | HighRise | LISA KIMBALL
36585 | REINSPECTION FEE FOR UNPAID P2; EMAIL SENT 7/21 WITH INSTRUCTIONS FOR PAYMENT | HighRise | LISA KIMBALL
36586 | NoData | HighRise | LISA KIMBALL
36785 | THE ALARM SYSTEM ISYELLOW AND RED TAGGED - BOTH TAGS WERE ISSUED 8/4/20 AND SYSTEM MUST BESERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
36827 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIREPROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY ORNON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THESYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
36828 | THESUPPRESION SYSTEM IS YELLOW TAGGED - 2 YELLOW TAGS WERE ISSUED (FEBRUARY AND JUNE 2020) AND MUSTBE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
36829 | THE ALARM SYSTEM IS RED TAGGED - TAG WAS ISSUED MARCH 2020 AND SYSTEM MUST BESERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
37044 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIREPROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY ORNON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THESYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
37045 | THESUPPRESION SYSTEM IS YELLOW TAGGED - 2 YELLOW TAGS WERE ISSUED (FEBRUARY AND JUNE 2020) AND MUSTBE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
37046 | THE ALARM SYSTEM IS RED TAGGED - TAG WAS ISSUED MARCH 2020 AND SYSTEM MUST BESERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
37047 | A PERMIT FOR BOTH THE KNOX BOX AND THE 911 BOX (IN THE OFFICE) MUST BE PAID FOR ANNUALLY | HighRise | LISA KIMBALL
37048 | NoData | HighRise | LISA KIMBALL
37049 | NoData | HighRise | LISA KIMBALL
37050 | NoData | HighRise | LISA KIMBALL
37051 | NoData | HighRise | LISA KIMBALL
37052 | NoData | HighRise | LISA KIMBALL
37053 | NoData | HighRise | LISA KIMBALL
37054 | PLEASE REVIEW LSB STANDARD 06 TO ENSURE ALL CONTENTS ARE CORRECTLY LABELED AND ORGANIZED WITHIN THE KEY BOX (IN THE OFFICE)ALL CONTENTS LISTED IN LSB 06 MUST BE CONTAINED IN THIS KEY BOX | HighRise | LISA KIMBALL
37055 | ENSURE THE KEY BOX IS SUPPLIED WITH ALL CONTENTS LISTED BELOW | HighRise | LISA KIMBALL
37056 | THE PERMIT FOR THE KNOX BOX AND THE KEY BOX MUST BE PAID ANNUALLY | HighRise | LISA KIMBALL
37057 | A KEY BOX IS SUPPLIED IN THE OFFICE; ENSURE THIS IS KNOWN AND LABELED AS SUCHVERIFY AND UPDATE ALL KEYS AND TAGS IN THE KEY BOX | HighRise | LISA KIMBALL
37058 | KEYS AND INSTRUCTIONS ARE REQUIRED IN THE KNOX BOX TO CONTROL ACCESS GATES | HighRise | LISA KIMBALL
37059 | PLACE UPDATED KEYS IN THE KNOX BOX;TEMPORARY KEYS (TAGGED WITH STICKY NOTES) AND INSTRUCTIONS HAVE BEEN SECURED UNTIL UPDATED KEYS WITH PERMANENT TAGS ARE READY.CALL THE INSPECTOR 832.216.7574 FOR ACCESS INTO THE KNOX BOX | HighRise | LISA KIMBALL
37067 | DURING THE ENTIRE ALARM EVENT, ALL ELEVATORS WERE FULLY FUNCTIONAL AND DID NOT AUTOMATICALLY RECALL TO THE DESIGNATED LEVEL | HighRise | LISA KIMBALL
37068 | NoData | HighRise | LISA KIMBALL
37069 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
37070 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION DURING A FIRE ALARM ACTIVATION ON 11FEBRUARY2019, NO SIGNAL WAS SENT TO THE HOUSTON FIRE DEPARTMENT OF THE INCIDENT, NO NOTIFICATION WAS RECIEVED TO DISPATCH EMERGENCY APPARATUS TO THE LOCATION AND THE ELEVATORS IN THE HIGH-RISE DID NOT AUTOMATICALLY RECALL TO THE DESIGNATED LEVEL - AN INVESTIGATION BY BUILDING MANAGEMENT AND ENGINEERS IS REQUESTED TO ADDRESS THESE ISSUES AND ENSURE ANY DEVIATIONS FROM WHAT IS PRESCRIBED BY THE FIRE CODE IS CORRECTED | HighRise | LISA KIMBALL
37071 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
37072 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
37073 | A FIRE ALARM WAS ACTIVATED ON THE 4TH, 5TH AND 6TH FLOORS OF 5 GREENWAY PLAZA AT APPROXIMATELY 13:15 ON 11FEBRUARY2019 AS SOON AS THE ALARM SOUNDED, FIRE WARDENS MUSTERED PERSONNEL AND LISTENED TO INSTRUCTIONS OVER THE INTERCOM FOR THE DURATION OF APPROXIMATELY 15 TO 20 MINUTES THE SMELL AND SIGHT OF SMOKE WAS DETECTED ON THE 5TH FLOOR | HighRise | LISA KIMBALL
37074 | NoData | HighRise | LISA KIMBALL
37075 | NO HFD APPARATUS WERE DISPATCHED TO THE LOCATION; THE ALARM WAS NOT AUTOMATICALLY REPORTED TO HFD | HighRise | LISA KIMBALL
37454 | NoData | HighRise | LISA KIMBALL
37470 | NoData | HighRise | LISA KIMBALL
37491 | NoData | HighRise | LISA KIMBALL
37498 | NoData | HighRise | LISA KIMBALL
37507 | NoData | HighRise | LISA KIMBALL
37508 | NoData | HighRise | LISA KIMBALL
37518 | NoData | HighRise | LISA KIMBALL
37525 | NoData | HighRise | LISA KIMBALL
37526 | NoData | HighRise | LISA KIMBALL
38901 | NoData | HighRise | LISA KIMBALL
38935 | NoData | HighRise | LISA KIMBALL
38994 | NoData | HighRise | LISA KIMBALL
39433 | NoData | HighRise | LISA KIMBALL
39607 | NoData | HighRise | LISA KIMBALL
40896 | NoData | HighRise | LISA KIMBALL
40905 | NoData | HighRise | LISA KIMBALL
40917 | NoData | HighRise | LISA KIMBALL
40925 | NoData | HighRise | LISA KIMBALL
40954 | NoData | HighRise | LISA KIMBALL
40974 | NoData | HighRise | LISA KIMBALL
40984 | NoData | HighRise | LISA KIMBALL
41004 | NoData | HighRise | LISA KIMBALL
41013 | NoData | HighRise | LISA KIMBALL
41425 | NoData | HighRise | LISA KIMBALL
41450 | NoData | HighRise | LISA KIMBALL
41483 | NoData | HighRise | LISA KIMBALL
41496 | NoData | HighRise | LISA KIMBALL
41502 | NoData | HighRise | LISA KIMBALL
41508 | NoData | HighRise | LISA KIMBALL
41511 | NoData | HighRise | LISA KIMBALL
41514 | NoData | HighRise | LISA KIMBALL
41534 | NoData | HighRise | LISA KIMBALL
41538 | NoData | HighRise | LISA KIMBALL
42247 | NoData | HighRise | LISA KIMBALL
42258 | NoData | HighRise | LISA KIMBALL
42268 | NoData | HighRise | LISA KIMBALL
42277 | NoData | HighRise | LISA KIMBALL
42281 | NoData | HighRise | LISA KIMBALL
42377 | NoData | HighRise | LISA KIMBALL
43382 | A RE-INSPECTION FEE WILL BEISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
43383 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
43384 | THE EXIT DOORS IN ROOMS 5 AND 11 ARE STICKING - ENSURE ALL EXIT DOORS ARE CAPABLE OF OPENING WITHEASE THE EMERGENCY EGRESS PADDLE ON THE EXTERIOR EXIT IN ROOM 3 IS NOT FUNCTIONING PROPERLY (DOES NOT RELEASE EASILY) WHEN PRESSURE IS APPLIED - ENSURE IT RELEASES EASILY, EVERY TIME IT IS DEPRESSED | HighRise | LISA KIMBALL
43385 | ENSURE THAT THE SMOKE DETECTOR IN THE PARENT ROOM IS CHECKED FOR EXPIRATION DATE AND THE BATTERY IS REPLACED EVERY SIX MONTHS - IT IS CHIRPING EVERY FEW MINUTES | HighRise | LISA KIMBALL
43386 | KEY BOX (K1) PERMIT IS CURRENT AND POSTED ON SITE FIRE ALARM PERMIT IS CURRENT AND POSTED ONSITE FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - JULY 2020 EMERGENCY ESCAPE MAPS ARE ALL POSTED IN PLACE IN EACH CLASSROOM ALL FIRE DRILLS CONDUCTED MONTHLY IN 2019; SCHOOL JUST REOPENED AND WILL RESUME MONTHLY DRILLS THE FIRE ALARM SYSTEM WAS FOUND TO BE IN COMPLIANCE, INACCEPTABLE CONDITION AND CURRENT ANNUAL INSPECTIONS (05/12/20) CONDUCTED - NOFURTHER COMPLIANCE NEEDED | HighRise | LISA KIMBALL
43544 | HOUSEKEEPING IS NEEDED IN SUITE 700 - THIS BUILDING IS NOT FITTED WITH FIRE SPRINKLERS SUITABLE TO EXTINGUISH A HEAVY FIRE LOAD REMOVE ALL STORAGE FROM SUITE 700 IN THE CLASS B HIGH-RISE | HighRise | LISA KIMBALL
43545 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
43546 | REMOVE AND DISCONTINUE STORAGE IN EXIT ACCESSES, EXITS OR EXIT DISCHARGES - KEEP ALL OF THESE AREAS FREE FROM OBTRUCTIONS AT ALL TIMES THE BUILDING IS OCCUPIED | HighRise | LISA KIMBALL
43547 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
43548 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
43549 | REMOVE FURNITURE IN THE EXIT CORRIDORS IN SUITE 700 IMMEDIATELY | HighRise | LISA KIMBALL
43550 | THE REQUIRED WIDTH OF EXIT PASSAGEWAYS IN SUITE 700 SHALL NOT BE OBSTRUCTED | HighRise | LISA KIMBALL
44103 | RED TAGGED FIRE ALARM PANEL 9SEP20 - IMMEDIATELY CALL SERVICE COMPANY FOR REPAIR OR REPLACEMENT; TROUBLES INDICATED ON PANELRED TAGGED FIRE PUMP 4SEPT20 - IMMEDIATELY CALL SERVICE COMPANY FOR REPAIR OR REPLACEMENT | HighRise | LISA KIMBALL
44947 | NoData | HighRise | LISA KIMBALL
44968 | NoData | HighRise | LISA KIMBALL
44977 | NoData | HighRise | LISA KIMBALL
45125 | NoData | HighRise | LISA KIMBALL
45167 | NoData | HighRise | LISA KIMBALL
45329 | NoData | HighRise | LISA KIMBALL
45339 | NoData | HighRise | LISA KIMBALL
45341 | NoData | HighRise | LISA KIMBALL
45347 | NoData | HighRise | LISA KIMBALL
46414 | NoData | HighRise | LISA KIMBALL
46441 | NoData | HighRise | LISA KIMBALL
46463 | NoData | HighRise | LISA KIMBALL
46468 | NoData | HighRise | LISA KIMBALL
46475 | NoData | HighRise | LISA KIMBALL
46482 | NoData | HighRise | LISA KIMBALL
46497 | NoData | HighRise | LISA KIMBALL
46546 | NoData | HighRise | LISA KIMBALL
46547 | NoData | HighRise | LISA KIMBALL
46552 | NoData | HighRise | LISA KIMBALL
46574 | NoData | HighRise | LISA KIMBALL
46581 | NoData | HighRise | LISA KIMBALL
46585 | NoData | HighRise | LISA KIMBALL
46592 | NoData | HighRise | LISA KIMBALL
46602 | NoData | HighRise | LISA KIMBALL
46624 | NoData | HighRise | LISA KIMBALL
46628 | NoData | HighRise | LISA KIMBALL
46651 | NoData | HighRise | LISA KIMBALL
46656 | NoData | HighRise | LISA KIMBALL
46759 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTIONFEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90DAYS | HighRise | LISA KIMBALL
46760 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
46761 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
46762 | NoData | HighRise | LISA KIMBALL
46763 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED | HighRise | LISA KIMBALL
46764 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
46765 | EVIDENCE OF INCOMPLETE ORNON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONINGSYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRECODE | HighRise | LISA KIMBALL
46766 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS, PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
46767 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
46768 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS, PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
46769 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
46770 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
46771 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERALALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
46772 | Take the Fire Warden Certification class online through thefollowing link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottomto click on High-rise Fire Warden CertificationClass.Print out the certificate of completion and keep it in a safeplace where it can be accessed upon demand. | HighRise | LISA KIMBALL
46773 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS | HighRise | LISA KIMBALL
46774 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
46775 | Concerning fire drills during COVID-19, a link can befound by going to the "Resources" and then clicking on"Notices".https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/ | HighRise | LISA KIMBALL
46776 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
46777 | MEMBERS OF THE FIRESAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
46778 | NoData | HighRise | LISA KIMBALL
47987 | NoData | HighRise | LISA KIMBALL
48019 | NoData | HighRise | LISA KIMBALL
48076 | NoData | HighRise | LISA KIMBALL
48086 | NoData | HighRise | LISA KIMBALL
48107 | NoData | HighRise | LISA KIMBALL
48126 | NoData | HighRise | LISA KIMBALL
48132 | NoData | HighRise | LISA KIMBALL
48133 | NoData | HighRise | LISA KIMBALL
48134 | NoData | HighRise | LISA KIMBALL
48151 | NoData | HighRise | LISA KIMBALL
48164 | NoData | HighRise | LISA KIMBALL
48168 | THE BACK EXIT DOORS ON THE GROUND FLOOR (AND ANY DOORS LEADING TO A HALLWAY OF THE BACK EXIT DOOR) MUST BE IDENTIFIED AND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS | HighRise | LISA KIMBALL
48169 | NoData | HighRise | LISA KIMBALL
48170 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
48171 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIRE A LETTER - PROVIDE A PHOTOCOPY OF THESE PERMITS. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - N/A - REQUIRED IF BOILERS ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
48172 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
48173 | PERMITS THE INSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS: Key Box Permit - Flammable and Combustible Permit - Fire Alarm Permit - Elevator Operating Permit - Boiler Permit - Other - Assembly, Access Gates, Batteries, etc. - Certificate of Occupancies - Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
48174 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
48175 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
48176 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
48177 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENT APPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
48178 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
48179 | EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE | HighRise | LISA KIMBALL
48180 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
48181 | SUBMIT A COMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS | HighRise | LISA KIMBALL
48182 | ALL OCCUPANTS OF THE BUILDING SHALL PARTICIPATE IN THE FIRE DRILLS AS REQUIRED BY THE CODE OFFICIAL AND THE FIRE CODE | HighRise | LISA KIMBALL
48183 | CABINETS CONTAINING FIRE FIGHTING EQUIPMENT MUST INDICATE THE EQUIPTMENT CONTAINED THEREIN - "FIRE HOSE" AND/OR "FIRE EXTINGUISHER" - CABINETS MUST BE LABELED WITH "HOSE", TOO | HighRise | LISA KIMBALL
48184 | THE CERTIFICATE OF COMPLETION OF FIRE WARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Rise or Mid-Rise Atruim Certification Training may send attendees to the following monthly seminars at no cost. Monthly seminars are available for management employees and tenant fire wardens of high-rise buildings who need to be certified. Certificates shall be valid for a period of five years from the date of training. There is no charge for attending these seminars. The only cost incurred may be parking fees, if applicable. Many buildings will have different fire safety features. The building management from each building represented is required to inform its employees and Fire Wardens of their specific fire safety features to complete the certification. Please note this training is not valid for Mid Rise Evacuation Training. For information on mid rise training please visit the HFD Mid Rise Fire Certication Webpage. Additional training availability information: The Houston Fire Department has set up and implemented a list of all high- rise buildings for Fire Safety Plan approvals. This list was set up to ensure that priority is given to buildings that have the greatest need while also providing each building an equal opportunity. The list of buildings is separated into two groups based on whether the building is an occupancy where people sleep, such as hotel, apartments, and condominiums or those buildings where people do not sleep, such as office buildings. Buildings are then sub- grouped by no sprinkler system, partial sprinkler system, or complete sprinkler systems before sorting by building height. The highest priority building is the residential building that is non-sprinklered, and the tallest in height. Our goal is to provide the needed services to approve each building within a two-year cycle. Buildings desiring to expedite the process also have three additional options. 1. The monthly open high-rise certification seminar is for buildings that have requested to send a limited number of fire wardens and building management employees to a class that is open to all high-rise buildings. The class information is not specific to any particular building and requires building management to supplement the training with their building specifics. 2. An inspector/instructor in the Life Safety Bureau, Public Education Section - High-rise Fire Safety Plan Approvals, may be obtained to provide training outside his regular work hours on an overtime basis. This may be done by contacting Diana Cardenas by e-mail at: diana.cardenas@houstontx.gov. This should be done prior to payment of a required permit fee so that an instructor can be assigned to made contact with the requesting party, to assist the requesting party with information on the application for over-time training and payment of the permit fees, and to schedule a mutually convenient training date. A City of Houston permit fee is required to schedule an inspector/instructor. The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019). 3. Having a City of Houston Fire Marshal approved consultant perform the training. The process to receive an approved Fire Safety Plan consist of the three following essential training elements conducted by persons, institutions or companies approved by the Fire Marshal according to regulations established by the Fire Marshal: a consultation with building management, an approved certification training for Fire Wardens and building employees, and a fire drill supervised by persons, institutions or companies approved by the Fire Marshal. | HighRise | LISA KIMBALL
48185 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
48186 | NoData | HighRise | LISA KIMBALL
48187 | NoData | HighRise | LISA KIMBALL
48188 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
48189 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIRE A LETTER - PROVIDE A PHOTOCOPY OF THESE PERMITS. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - N/A " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
48190 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
48191 | 105.1.1 ++ PERMITS REQUIRED (HPC ADDRESS) PERMITS THE INSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS: Key Box Permit - Flammable and Combustible Permit - Fire Alarm Permit - Elevator Operating Permit - Boiler Permit - Other - Assembly, Access Gates, Batteries, etc. - Certificate of Occupancies - Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
48192 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
48193 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
48194 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
48195 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENT APPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
48196 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
48197 | EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE | HighRise | LISA KIMBALL
48198 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRE CODE OFFICIAL IS DEPENDENT UPON SUCCESSFUL COMPLETION OF THREE COMPONENTS - CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF A SUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
48199 | EACH MEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
48200 | ATTENDANCE AT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH- RISE FIRE WARDENS | HighRise | LISA KIMBALL
48201 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
48202 | SUBMIT A COMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS | HighRise | LISA KIMBALL
48203 | MEMBERS OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
48204 | REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Rise or Mid-Rise Atruim Certification Training may send attendees to the following monthly seminars at no cost. Monthly seminars are available for management employees and tenant fire wardens of high-rise buildings who need to be certified. Certificates shall be valid for a period of five years from the date of training. There is no charge for attending these seminars. The only cost incurred may be parking fees, if applicable. Many buildings will have different fire safety features. The building management from each building represented is required to inform its employees and Fire Wardens of their specific fire safety features to complete the certification. Please note this training is not valid for Mid Rise Evacuation Training. For information on mid rise training please visit the HFD Mid Rise Fire Certication Webpage. Additional training availability information: The Houston Fire Department has set up and implemented a list of all high- rise buildings for Fire Safety Plan approvals. This list was set up to ensure that priority is given to buildings that have the greatest need while also providing each building an equal opportunity. The list of buildings is separated into two groups based on whether the building is an occupancy where people sleep, such as hotel, apartments, and condominiums or those buildings where people do not sleep, such as office buildings. Buildings are then sub- grouped by no sprinkler system, partial sprinkler system, or complete sprinkler systems before sorting by building height. The highest priority building is the residential building that is non-sprinklered, and the tallest in height. Our goal is to provide the needed services to approve each building within a two-year cycle. Buildings desiring to expedite the process also have three additional options. 1. The monthly open high-rise certification seminar is for buildings that have requested to send a limited number of fire wardens and building management employees to a class that is open to all high-rise buildings. The class information is not specific to any particular building and requires building management to supplement the training with their building specifics. 2. An inspector/instructor in the Life Safety Bureau, Public Education Section - High-rise Fire Safety Plan Approvals, may be obtained to provide training outside his regular work hours on an overtime basis. This may be done by contacting Diana Cardenas by e-mail at: diana.cardenas@houstontx.gov. This should be done prior to payment of a required permit fee so that an instructor can be assigned to made contact with the requesting party, to assist the requesting party with information on the application for over-time training and payment of the permit fees, and to schedule a mutually convenient training date. A City of Houston permit fee is required to schedule an inspector/instructor. The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019). 3. Having a City of Houston Fire Marshal approved consultant perform the training. The process to receive an approved Fire Safety Plan consist of the three following essential training elements conducted by persons, institutions or companies approved by the Fire Marshal according to regulations established by the Fire Marshal: a consultation with building management, an approved certification training for Fire Wardens and building employees, and a fire drill supervised by persons, institutions or companies approved by the Fire Marshal. | HighRise | LISA KIMBALL
48205 | ALL OCCUPANTS OF THE BUILDING SHALL PARTICIPATE IN THE FIRE DRILLS AS REQUIRED BY THE CODE OFFICIAL AND THE FIRE CODE | HighRise | LISA KIMBALL
48206 | APPROVAL OF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFUL COMPLETION OF SEVERALALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF A COMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
48207 | THE CERTIFICATE OF COMPLETION OF FIRE WARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
48208 | ALL HOOD VENTS AND HOOD SUPPRESSION SYSTEMS MUST BE INSPECTED AND SERVICED - ENSURE THIS IS CONDUCTED FOR THE DELI VENT HOOD AS SOON AS POSSIBLE AND COMPLIES WITH THE FIRE CODE IN THE FUTURE | HighRise | LISA KIMBALL
48209 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
48211 | ALL REAR EXITS ON THE GROUND FLOOR AND THE BACK EXIT DOOR OF THE CAFE (AND ANY DOORS LEADING TO A HALLWAY OF THE BACK EXIT DOOR) MUST BE IDENTIFIED AND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS | HighRise | LISA KIMBALL
48212 | NoData | HighRise | LISA KIMBALL
48213 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
48214 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIRE A LETTER - PROVIDE A PHOTOCOPY OF THESE PERMITS. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - N/A - REQUIRED IF BOILERS ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
48215 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
48216 | PERMITS THE INSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS: Key Box Permit - Flammable and Combustible Permit - Fire Alarm Permit - Elevator Operating Permit - Boiler Permit - Other - Assembly, Access Gates, Batteries, etc. - Certificate of Occupancies - Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
48217 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
48218 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
48219 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
48220 | THE EXTERIOR DOOR OF SUITE 100 WHICH HAS BEEN PERMANENTLY OBSTRUCTED AND/OR NOT FUNCTIONAL MUST HAVE A SIGN ON THE EXTERIOR STATING "THIS DOOR BLOCKED" IN CONTRASTING COLOR FROM THE BACKGROUND | HighRise | LISA KIMBALL
48221 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENT APPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
48222 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
48223 | EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE | HighRise | LISA KIMBALL
48224 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
48225 | SUBMIT A COMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS | HighRise | LISA KIMBALL
48226 | ALL OCCUPANTS OF THE BUILDING SHALL PARTICIPATE IN THE FIRE DRILLS AS REQUIRED BY THE CODE OFFICIAL AND THE FIRE CODE | HighRise | LISA KIMBALL
48227 | THE CERTIFICATE OF COMPLETION OF FIRE WARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Rise or Mid-Rise Atruim Certification Training may send attendees to the following monthly seminars at no cost. Monthly seminars are available for management employees and tenant fire wardens of high-rise buildings who need to be certified. Certificates shall be valid for a period of five years from the date of training. There is no charge for attending these seminars. The only cost incurred may be parking fees, if applicable. Many buildings will have different fire safety features. The building management from each building represented is required to inform its employees and Fire Wardens of their specific fire safety features to complete the certification. Please note this training is not valid for Mid Rise Evacuation Training. For information on mid rise training please visit the HFD Mid Rise Fire Certication Webpage. Additional training availability information: The Houston Fire Department has set up and implemented a list of all high- rise buildings for Fire Safety Plan approvals. This list was set up to ensure that priority is given to buildings that have the greatest need while also providing each building an equal opportunity. The list of buildings is separated into two groups based on whether the building is an occupancy where people sleep, such as hotel, apartments, and condominiums or those buildings where people do not sleep, such as office buildings. Buildings are then sub- grouped by no sprinkler system, partial sprinkler system, or complete sprinkler systems before sorting by building height. The highest priority building is the residential building that is non-sprinklered, and the tallest in height. Our goal is to provide the needed services to approve each building within a two-year cycle. Buildings desiring to expedite the process also have three additional options. 1. The monthly open high-rise certification seminar is for buildings that have requested to send a limited number of fire wardens and building management employees to a class that is open to all high-rise buildings. The class information is not specific to any particular building and requires building management to supplement the training with their building specifics. 2. An inspector/instructor in the Life Safety Bureau, Public Education Section - High-rise Fire Safety Plan Approvals, may be obtained to provide training outside his regular work hours on an overtime basis. This may be done by contacting Diana Cardenas by e-mail at: diana.cardenas@houstontx.gov. This should be done prior to payment of a required permit fee so that an instructor can be assigned to made contact with the requesting party, to assist the requesting party with information on the application for over-time training and payment of the permit fees, and to schedule a mutually convenient training date. A City of Houston permit fee is required to schedule an inspector/instructor. The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019). 3. Having a City of Houston Fire Marshal approved consultant perform the training. The process to receive an approved Fire Safety Plan consist of the three following essential training elements conducted by persons, institutions or companies approved by the Fire Marshal according to regulations established by the Fire Marshal: a consultation with building management, an approved certification training for Fire Wardens and building employees, and a fire drill supervised by persons, institutions or companies approved by the Fire Marshal. | HighRise | LISA KIMBALL
48228 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
48229 | PERTAINING TO FIRE EXTINGUISHERS IN SUITE 100 ON THE 1ST FLOOR | HighRise | LISA KIMBALL
48230 | SECURE ALL COMPRESSED GAS CYLINDERS IN THE PENTHOUSE WITH A CHAIN | HighRise | LISA KIMBALL
48231 | NoData | HighRise | LISA KIMBALL
48232 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
48233 | NoData | HighRise | LISA KIMBALL
48234 | ENSURE THAT UL APPROVED RED CAN IN THE MECHANICAL ROOM ON PENTHOUSE LEVEL AND ELEVATOR ROOMS ARE EMPTIED DAILY | HighRise | LISA KIMBALL
48235 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIRE A LETTER - PROVIDE A PHOTOCOPY OF THESE PERMITS. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - K1 IS EXPIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - WILL EXPIRE 1/3/20 " Sprinkler Percentage Letter and Form (included in report) " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual " Fire Alarm System Test - Annual - REQUIRED; YELLOW TAGGED JAN 2019 " Fire Extinguishers - Annual " Fire Hoses - Annual " Fire Pumps Flow Test - Annual " Emergency Power & Lighting - Annual " Generator Test (ATS) - Annual - N/A " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year " Fire Dampers - 4 Year " Fire Alarm Sensitivity - 2 Year - EXPIRED " FDC Test (Bldg. & Garage) - 5 Year " PRV / PRD Test - 5 Year - N/A " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year " Water Supply Tank Inspection - 5 Year " Boiler Permit " Elevator Permit - Annual " Dry Partial or Full Trip Test - N/A " Gas Test - 5 Year - REQUIRED IF GAS ON SITE " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
48236 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
48237 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY THROUGHOUGHT THE PENTHOUSE,10TH FLOOR STAIR A, 9TH FLOOR STAIR B, 8TH FLOOR STAIRS, 7TH FLOOR STAIRS, 6TH FLOOR STAIRS, 5TH FLOOR STAIRS, 4TH FLOOR STAIRS, 3RD FLOOR STAIRS, 2ND FLOOR STAIRS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
48238 | OBTAIN A CERTIFICATE OF OCCUPANCY AND ANY REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER | HighRise | LISA KIMBALL
48239 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
48240 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
48241 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
48242 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENT APPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
48243 | RECEIVED; NO FURTHER ACTION NECESSARY | HighRise | LISA KIMBALL
48244 | ALL ELECTRICAL CIRCUIT BREAKERS IN ELECTRICAL PANELS ON THE 8TH FLOOR, 7TH FLOOR AND 5TH FLOOR MUST BE CLEARLY AND CORRECTLY LABELED THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH - THE MECHANICAL ROOM ON THE 6TH FLOOR SHOULD BE LABELED "ELECTRICAL' | HighRise | LISA KIMBALL
48245 | SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
48246 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
48247 | EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE | HighRise | LISA KIMBALL
48248 | REVIEW LSB #2 SECTION 2.5.4.3 TO REVISE THE FDC SIGN WITH NECESSARY CORRECTIONS AND ENSURE ALL PERTINENT INFORMATION IS INCLUDED Approved signs of weather-resistant materials, with not less than one inch high legible block lettering on a highly contrasting background, shall be placed on or immediately adjacent to all fire department connections and provide the following information: 1. Type of system - STANDPIPE, SPRINKLER, STANDPIPE / SPRINKLER, DRY PIPE SPRINKLER, etc. 2. Which building or structure, or what portion, zone, and floors of the building or structure the FDC serve. i. Ex: FLOORS B1 - 12; LEVELS 1 - 8; HIGH ZONE FLRS 21 - 40; etc. 3. On standpipe and combination standpipe/sprinkler systems - whether there are pressure regulating valves (PRV) or pressure reducing devices (PRD) on the system. System pressures shall also be indicated on all wet standpipe and combination standpipe/sprinkler systems. Examples: NO PRV/PRD (System Pres. 100 PSI) PRD Levels 1 - 7 (System Pres. 150 PSI) PRV Floors 1 - 10 (System Pres. 175 PSI) | HighRise | LISA KIMBALL
48249 | PERTAINING TO FIRE EXTINGUISHERS IN SUITE 100 ON THE 1ST FLOOR | HighRise | LISA KIMBALL
48250 | FIRE EXTINGUISHERS MUST BE HUNG IN SUITE 100 ON THE 1ST FLOOR | HighRise | LISA KIMBALL
48251 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRE CODE OFFICIAL IS DEPENDENT UPON SUCCESSFUL COMPLETION OF THREE COMPONENTS - CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF A SUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
48252 | EACH MEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
48253 | ATTENDANCE AT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH- RISE FIRE WARDENS | HighRise | LISA KIMBALL
48254 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
48255 | READ AND REVIEW LSB STANDARD 6; FULL COMPLIANCE OF PROVIDING A PROPERLY SUPPLIED FIRE DEPOSITORY BOX IS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
48256 | NO FIRE FIGHTER PHONES ARE PRESENT IN THE BUILDING DUE TO AGE OF FACILITY. BUILDING MANAGEMENT NEEDS TO SEEK ADVICE ON TESTING THE BUILDING FOR EMERGENCY RADIO COVERAGE BASED ON CHAPTER 10 OF THE FIRE CODE AND 2012 IFC HOUSTON AMENDMENTS OR INSTALLATION OF FIREFIGHTER TELEPHONES (IN FCR) AND JACKS (IN ALL ELEVATOR LOBBIES AND AT THE STAIRWELLS) (SEE PROVIDED DOCUMENTS: 2012 IFC HOUSTON RADIO AMENDMENTS and SECTION 510 RADIO COVERAGE 2012) COMPLIANCE WITHIN 60 CALENDAR DAYS. For Radio Survey assistance contact: Datavox Whitney Hamm WhitneyH@datavox.net Datavox is listed as a Company that can be consulted with only to help Management start the process of gathering information. It is recommended that other Companies be contacted before final decision is made. NO FIREFIGHTER PHONES OR JACKS FOUND IN THE BUILDING; ALL HIGH-RISES MUST HAVE A FIRE DEPARTMENT COMMUNICATION SYSTEM (PERMANENTLY INSTALLED PHONE JACKS IN ELEVATORS, ELEVATOR LOBBIES, EMERGENCY AND STANDBY POWER ROOMS, FIRE PUMP ROOMS, AREAS OF REFUGE AND AT ENCLOSED EXIT STAIRWAYS) OR EMERGENCY RESPONDER RADIO COVERAGE SECTION 510 EMERGENCY RESPONDER RADIO COVERAGE 510.1 Emergency responder radio coverage in new buildings. All new buildings shall have approved radio coverage for emergency responders within the building based upon the existing coverage levels of the public safety communication systems of the jurisdiction at the exterior of the building. This section shall not require improvement of the existing public safety communication systems. Exceptions: 1. Where approved by the building official and the fire code official, a wired communication system in accordance with Section 907.2.13.2 shall be permitted to be installed or maintained in lieu of an approved radio coverage system. 2. Where it is determined by the fire code official that the radio coverage system is not needed. 3. In facilities where emergency responder radio coverage is required and such systems, components or equipment required could have a negative impact on the normal operations of that facility, the fire code official shall have the authority to accept an automatically activated emergency responder radio coverage system. 510.2 Emergency responder radio coverage in existing buildings. Existing buildings shall be provided with approved radio coverage for emergency responders as required in Chapter 11. 510.3 Permit required. A construction permit for the installation of or modification to emergency responder radio coverage systems and related equipment is required as specified in Section 105.7.5. Maintenance performed in accordance with this code is not considered a modification and does not require a permit. 510.4 Technical requirements. Systems, components, and equipment required to provide emergency responder radio coverage system shall comply with Sections 511.4.1 through 511.4.2.5. 510.4.1 Radio signal strength. The building shall be considered to have acceptable emergency responder radio coverage when signal strength measurements in 95 percent of all areas on each floor of the building meet the signal strength requirements in Sections 510.4.1.1 and 510.4.1.2. 510.4.1.1 Minimum signal strength into the building. A minimum signal strength of -95 dBm shall be receivable within the building. 510.4.1.2 Minimum signal strength out of the building. A minimum signal strength of -95 dBm shall be 67 received by the agency's radio system when transmitted from within the building. 510.4.2 System design. The emergency responder radio coverage system shall be designed in accordance with Sections 510.4.2.1 through 510.4.2.5. 510.4.2.1 Amplification systems allowed. Buildings and structures which cannot support the required level of radio coverage shall be equipped with a radiating cable system, a distributed antenna system with Federal Communications Commission (FCC)-certified signal boosters, or other system approved by the fire code official in order to achieve the required adequate radio coverage. 510.4.2.2 Technical criteria. The fire code official shall maintain a document providing the specific technical information and requirements for the emergency responder radio coverage system. This document shall contain, but not be limited to, the various frequencies required, the location of radio sites, effective radiated power of radio sites, and other supporting technical information. 510.4.2.3 Secondary power. Emergency responder radio coverage systems shall be provided with an approved secondary source of power. The secondary power supply shall be capable of operating the emergency responder radio coverage system for a period of at least 24 hours. When primary power is lost, the power supply to the emergency responder radio coverage system shall automatically transfer to the secondary power supply. 510.4.2.4 Signal booster requirements. If used, signal boosters shall meet the following requirements: 1. All signal booster components shall be contained in a National Electrical Manufacturer's Association (NEMA) 4-type waterproof cabinet. 2. Battery systems used for the emergency power source shall be contained in a NEMA 4-type waterproof cabinet. 3. The signal booster system and battery system shall be electrically supervised and monitored by a supervisory service, or when approved by the fire code official, shall sound an audible signal at a constantly attended location. 4. Equipment shall have FCC certification prior to installation. 510.4.2.5 Additional frequencies and change of frequencies. The emergency responder radio coverage system shall be capable of modification or expansion in the event frequency changes are required by the FCC or additional frequencies are made available by the FCC. 510.5 Installation requirements. The installation of the public safety radio coverage system shall be in accordance with Sections 510.5.1 through 510.5.5.68 510.5.1 Approval prior to installation. Amplification systems capable of operating on frequencies licensed to any public safety agency by the FCC shall not be installed without prior coordination and approval of the fire code official. 510.5.2 Minimum qualifications of personnel. The minimum qualifications of the system designer and lead installation personnel shall include: 1. A valid FCC-issued general radio operators license; and 2. Certification of in-building system training issued by a nationally recognized organization, school or a certificate issued by the manufacturer of the equipment being installed. These qualifications shall not be required where demonstration of adequate skills and experience satisfactory to the fire code official is provided. 510.5.3 Acceptance test procedure. When an emergency responder radio coverage system is required, and upon completion of installation, the building owner shall have the radio system tested to ensure that two-way coverage on each floor of the building is a minimum of 90 percent. The test procedure shall be conducted as follows: 1. Each floor of the building shall be divided into a grid of 20 approximately equal test areas. 2. The test shall be conducted using a calibrated portable radio of the latest brand and model used by the agency talking through the agency's radio communications system. 3. Failure of a maximum of two nonadjacent test areas shall not result in failure of the test. 4. In the event that three of the test areas fail the test, in order to be more statistically accurate, the floor shall be permitted to be divided into 40 equal test areas. Failure of a maximum of four nonadjacent test areas shall not result in failure of the test. If the system fails the 40-area test, the system shall be altered to meet the 90 percent coverage requirement. 5. A test location approximately in the center of each test area shall be selected for the test, with the radio enabled to verify two-way communications to and from the outside of the building through the public agency's radio communications system. Once the test location has been selected, that location shall represent the entire test area. Failure in the selected test location shall be considered failure of that test area. Additional test locations shall not be permitted. 6. The gain values of all amplifiers shall be measured and the test measurement results shall be kept on file with the building owner so that the measurements can be verified during annual tests. In the event that the measurement results become lost, the building owner shall be required to rerun the acceptance test to reestablish the gain values. 7. As part of the installation a spectrum analyzer or other suitable test equipment shall be utilized to ensure spurious oscillations are not being generated by the subject signal booster. This test shall be conducted at time of installation and subsequent annual inspections. 510.5.4 FCC compliance. The emergency responder radio coverage system installation and components shall also comply with all applicable federal regulations including, but not limited to, FCC 47 CPR Part 90.219. 510.6 Maintenance. The emergency responder radio coverage system shall be maintained operational at all times in accordance with Sections 510.6.1 through 510.6.3. 510.6.1 Testing and proof of compliance. The emergency responder radio coverage system shall be inspected and tested annually or whenever structural changes occur including additions or remodels that could materially change the original field performance tests. Testing shall consist of the following: 1. In-building coverage test as described in Section 510.5.4. 2. Signal boosters shall be tested to ensure that the gain is the same as it was upon initial installation and acceptance. 3. Backup batteries and power supplies shall be tested under load of a period of one hour to verify that they will properly operate during an actual power outage. If within the 1-hour test period the battery exhibits symptoms of failure, the test shall be extended for additional 1-hour periods until the integrity of the battery can be determined. 4. All other active components shall be checked to verify operation within the manufacturer's specifications. 5. At the conclusion of the testing, a report, which shall verify compliance with Section 510.5.4, shall be submitted to the fire code official. 510.6.2 Additional frequencies. The building owner shall modify or expand the emergency responder radio coverage system at their expense in the event frequency changes are required by the FCC or additional frequencies are made available by the FCC. Prior approval of a public safety radio coverage system on previous frequencies does not exempt this section. 510.6.3 Field testing. Agency personnel shall have the right to enter onto the property at any reasonable time to conduct field testing to verify the required level of radio coverage | HighRise | LISA KIMBALL
48257 | SUBMIT A COMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS | HighRise | LISA KIMBALL
48258 | MEMBERS OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
48259 | THE DIRECTION (IF LOCATED AWAY FROM THE APPROACH OF THE BUILDING OR ABILITY TO READILY SEE IT IS OBSCURED) AND LOCATION OF THE FDC OR THE STEM VALVE MUST BE INDICATED - SIGN MUST ALSO INDICATE ADDRESS AND SUITES OR WHICH FLOORS/PORTION OF BUILDING ARE SERVED BY THE FIRE DEPARTMENT CONNECTION | HighRise | LISA KIMBALL
48260 | PERTAINING TO FIRE EXTINGUISHERS IN SUITE 100 ON THE 1ST FLOOR | HighRise | LISA KIMBALL
48261 | APPROVAL OF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFUL COMPLETION OF SEVERALALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF A COMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
48262 | THE CERTIFICATE OF COMPLETION OF FIRE WARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Rise or Mid-Rise Atruim Certification Training may send attendees to the following monthly seminars at no cost. Monthly seminars are available for management employees and tenant fire wardens of high-rise buildings who need to be certified. Certificates shall be valid for a period of five years from the date of training. There is no charge for attending these seminars. The only cost incurred may be parking fees, if applicable. Many buildings will have different fire safety features. The building management from each building represented is required to inform its employees and Fire Wardens of their specific fire safety features to complete the certification. Please note this training is not valid for Mid Rise Evacuation Training. For information on mid rise training please visit the HFD Mid Rise Fire Certication Webpage. Additional training availability information: The Houston Fire Department has set up and implemented a list of all high- rise buildings for Fire Safety Plan approvals. This list was set up to ensure that priority is given to buildings that have the greatest need while also providing each building an equal opportunity. The list of buildings is separated into two groups based on whether the building is an occupancy where people sleep, such as hotel, apartments, and condominiums or those buildings where people do not sleep, such as office buildings. Buildings are then sub- grouped by no sprinkler system, partial sprinkler system, or complete sprinkler systems before sorting by building height. The highest priority building is the residential building that is non-sprinklered, and the tallest in height. Our goal is to provide the needed services to approve each building within a two-year cycle. Buildings desiring to expedite the process also have three additional options. 1. The monthly open high-rise certification seminar is for buildings that have requested to send a limited number of fire wardens and building management employees to a class that is open to all high-rise buildings. The class information is not specific to any particular building and requires building management to supplement the training with their building specifics. 2. An inspector/instructor in the Life Safety Bureau, Public Education Section - High-rise Fire Safety Plan Approvals, may be obtained to provide training outside his regular work hours on an overtime basis. This may be done by contacting Diana Cardenas by e-mail at: diana.cardenas@houstontx.gov. This should be done prior to payment of a required permit fee so that an instructor can be assigned to made contact with the requesting party, to assist the requesting party with information on the application for over-time training and payment of the permit fees, and to schedule a mutually convenient training date. A City of Houston permit fee is required to schedule an inspector/instructor. The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019). 3. Having a City of Houston Fire Marshal approved consultant perform the training. The process to receive an approved Fire Safety Plan consist of the three following essential training elements conducted by persons, institutions or companies approved by the Fire Marshal according to regulations established by the Fire Marshal: a consultation with building management, an approved certification training for Fire Wardens and building employees, and a fire drill supervised by persons, institutions or companies approved by the Fire Marshal. | HighRise | LISA KIMBALL
48263 | PERTAINING TO THE FM 200 SYSTEM ON THE 1ST FLOOR | HighRise | LISA KIMBALL
48264 | FM 200 SYSTEM FOR SUITE 100 ON THE 1ST FLOOR MUST HAVE A "DISCHARGE" INDICATOR AT THE ENTRANCE FROM THE LOBBY DOCK | HighRise | LISA KIMBALL
48265 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
48271 | NoData | HighRise | LISA KIMBALL
48278 | NoData | HighRise | LISA KIMBALL
48283 | NoData | HighRise | LISA KIMBALL
48670 | NoData | HighRise | LISA KIMBALL
48745 | NoData | HighRise | LISA KIMBALL
48759 | NoData | HighRise | LISA KIMBALL
48761 | NoData | HighRise | LISA KIMBALL
48774 | NoData | HighRise | LISA KIMBALL
48794 | NoData | HighRise | LISA KIMBALL
48802 | NoData | HighRise | LISA KIMBALL
48809 | NoData | HighRise | LISA KIMBALL
48811 | NoData | HighRise | LISA KIMBALL
48818 | NoData | HighRise | LISA KIMBALL
48828 | NoData | HighRise | LISA KIMBALL
48832 | NoData | HighRise | LISA KIMBALL
48842 | NoData | HighRise | LISA KIMBALL
48844 | NoData | HighRise | LISA KIMBALL
48848 | NoData | HighRise | LISA KIMBALL
49517 | NoData | HighRise | LISA KIMBALL
49533 | NoData | HighRise | LISA KIMBALL
49549 | NoData | HighRise | LISA KIMBALL
49555 | NoData | HighRise | LISA KIMBALL
49563 | NoData | HighRise | LISA KIMBALL
49566 | NoData | HighRise | LISA KIMBALL
49576 | NoData | HighRise | LISA KIMBALL
49587 | NoData | HighRise | LISA KIMBALL
49603 | NoData | HighRise | LISA KIMBALL
49607 | NoData | HighRise | LISA KIMBALL
49608 | NoData | HighRise | LISA KIMBALL
49613 | NoData | HighRise | LISA KIMBALL
49620 | NoData | HighRise | LISA KIMBALL
49860 | NoData | HighRise | LISA KIMBALL
49910 | NoData | HighRise | LISA KIMBALL
49918 | NoData | HighRise | LISA KIMBALL
49926 | NoData | HighRise | LISA KIMBALL
49938 | NoData | HighRise | LISA KIMBALL
49947 | NoData | HighRise | LISA KIMBALL
49960 | NoData | HighRise | LISA KIMBALL
49979 | NoData | HighRise | LISA KIMBALL
49988 | NoData | HighRise | LISA KIMBALL
49992 | NoData | HighRise | LISA KIMBALL
49999 | NoData | HighRise | LISA KIMBALL
50006 | NoData | HighRise | LISA KIMBALL
51988 | NoData | HighRise | LISA KIMBALL
51989 | NoData | HighRise | LISA KIMBALL
51990 | NoData | HighRise | LISA KIMBALL
51991 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
51992 | CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET | HighRise | LISA KIMBALL
51993 | NO FIREFIGHTER PHONES OR JACKS FOUND IN THE BUILDING; ALL HIGH-RISES MUST HAVE A FIRE DEPARTMENT COMMUNICATION SYSTEM (PERMANENTLY INSTALLED PHONE JACKS IN ELEVATORS, ELEVATOR LOBBIES, EMERGENCY AND STANDBY POWER ROOMS, FIRE PUMP ROOMS, AREAS OF REFUGE AND AT ENCLOSED EXIT STAIRWAYS) OR EMERGENCY RESPONDER RADIO COVERAGE (DETAILS CONCERNING THE LATER BELOW) SECTION 510 EMERGENCY RESPONDER RADIO COVERAGE 510.1 Emergency responder radio coverage in new buildings. All new buildings shall have approved radio coverage for emergency responders within the building based upon the existing coverage levels of the public safety communication systems of the jurisdiction at the exterior of the building. This section shall not require improvement of the existing public safety communication systems. Exceptions: 1. Where approved by the building official and the fire code official, a wired communication system in accordance with Section 907.2.13.2 shall be permitted to be installed or maintained in lieu of an approved radio coverage system. 2. Where it is determined by the fire code official that the radio coverage system is not needed. 3. In facilities where emergency responder radio coverage is required and such systems, components or equipment required could have a negative impact on the normal operations of that facility, the fire code official shall have the authority to accept an automatically activated emergency responder radio coverage system. 510.2 Emergency responder radio coverage in existing buildings. Existing buildings shall be provided with approved radio coverage for emergency responders as required in Chapter 11. 510.3 Permit required. A construction permit for the installation of or modification to emergency responder radio coverage systems and related equipment is required as specified in Section 105.7.5. Maintenance performed in accordance with this code is not considered a modification and does not require a permit. 510.4 Technical requirements. Systems, components, and equipment required to provide emergency responder radio coverage system shall comply with Sections 511.4.1 through 511.4.2.5. 510.4.1 Radio signal strength. The building shall be considered to have acceptable emergency responder radio coverage when signal strength measurements in 95 percent of all areas on each floor of the building meet the signal strength requirements in Sections 510.4.1.1 and 510.4.1.2. 510.4.1.1 Minimum signal strength into the building. A minimum signal strength of -95 dBm shall be receivable within the building. 510.4.1.2 Minimum signal strength out of the building. A minimum signal strength of -95 dBm shall be 67 received by the agency's radio system when transmitted from within the building. 510.4.2 System design. The emergency responder radio coverage system shall be designed in accordance with Sections 510.4.2.1 through 510.4.2.5. 510.4.2.1 Amplification systems allowed. Buildings and structures which cannot support the required level of radio coverage shall be equipped with a radiating cable system, a distributed antenna system with Federal Communications Commission (FCC)-certified signal boosters, or other system approved by the fire code official in order to achieve the required adequate radio coverage. 510.4.2.2 Technical criteria. The fire code official shall maintain a document providing the specific technical information and requirements for the emergency responder radio coverage system. This document shall contain, but not be limited to, the various frequencies required, the location of radio sites, effective radiated power of radio sites, and other supporting technical information. 510.4.2.3 Secondary power. Emergency responder radio coverage systems shall be provided with an approved secondary source of power. The secondary power supply shall be capable of operating the emergency responder radio coverage system for a period of at least 24 hours. When primary power is lost, the power supply to the emergency responder radio coverage system shall automatically transfer to the secondary power supply. 510.4.2.4 Signal booster requirements. If used, signal boosters shall meet the following requirements: 1. All signal booster components shall be contained in a National Electrical Manufacturer's Association (NEMA) 4-type waterproof cabinet. 2. Battery systems used for the emergency power source shall be contained in a NEMA 4-type waterproof cabinet. 3. The signal booster system and battery system shall be electrically supervised and monitored by a supervisory service, or when approved by the fire code official, shall sound an audible signal at a constantly attended location. 4. Equipment shall have FCC certification prior to installation. 510.4.2.5 Additional frequencies and change of frequencies. The emergency responder radio coverage system shall be capable of modification or expansion in the event frequency changes are required by the FCC or additional frequencies are made available by the FCC. 510.5 Installation requirements. The installation of the public safety radio coverage system shall be in accordance with Sections 510.5.1 through 510.5.5.68 510.5.1 Approval prior to installation. Amplification systems capable of operating on frequencies licensed to any public safety agency by the FCC shall not be installed without prior coordination and approval of the fire code official. 510.5.2 Minimum qualifications of personnel. The minimum qualifications of the system designer and lead installation personnel shall include: 1. A valid FCC-issued general radio operators license; and 2. Certification of in-building system training issued by a nationally recognized organization, school or a certificate issued by the manufacturer of the equipment being installed. These qualifications shall not be required where demonstration of adequate skills and experience satisfactory to the fire code official is provided. 510.5.3 Acceptance test procedure. When an emergency responder radio coverage system is required, and upon completion of installation, the building owner shall have the radio system tested to ensure that two-way coverage on each floor of the building is a minimum of 90 percent. The test procedure shall be conducted as follows: 1. Each floor of the building shall be divided into a grid of 20 approximately equal test areas. 2. The test shall be conducted using a calibrated portable radio of the latest brand and model used by the agency talking through the agency's radio communications system. 3. Failure of a maximum of two nonadjacent test areas shall not result in failure of the test. 4. In the event that three of the test areas fail the test, in order to be more statistically accurate, the floor shall be permitted to be divided into 40 equal test areas. Failure of a maximum of four nonadjacent test areas shall not result in failure of the test. If the system fails the 40-area test, the system shall be altered to meet the 90 percent coverage requirement. 5. A test location approximately in the center of each test area shall be selected for the test, with the radio enabled to verify two-way communications to and from the outside of the building through the public agency's radio communications system. Once the test location has been selected, that location shall represent the entire test area. Failure in the selected test location shall be considered failure of that test area. Additional test locations shall not be permitted. 6. The gain values of all amplifiers shall be measured and the test measurement results shall be kept on file with the building owner so that the measurements can be verified during annual tests. In the event that the measurement results become lost, the building owner shall be required to rerun the acceptance test to reestablish the gain values. 7. As part of the installation a spectrum analyzer or other suitable test equipment shall be utilized to ensure spurious oscillations are not being generated by the subject signal booster. This test shall be conducted at time of installation and subsequent annual inspections. 510.5.4 FCC compliance. The emergency responder radio coverage system installation and components shall also comply with all applicable federal regulations including, but not limited to, FCC 47 CPR Part 90.219. 510.6 Maintenance. The emergency responder radio coverage system shall be maintained operational at all times in accordance with Sections 510.6.1 through 510.6.3. 510.6.1 Testing and proof of compliance. The emergency responder radio coverage system shall be inspected and tested annually or whenever structural changes occur including additions or remodels that could materially change the original field performance tests. Testing shall consist of the following: 1. In-building coverage test as described in Section 510.5.4. 2. Signal boosters shall be tested to ensure that the gain is the same as it was upon initial installation and acceptance. 3. Backup batteries and power supplies shall be tested under load of a period of one hour to verify that they will properly operate during an actual power outage. If within the 1-hour test period the battery exhibits symptoms of failure, the test shall be extended for additional 1-hour periods until the integrity of the battery can be determined. 4. All other active components shall be checked to verify operation within the manufacturer's specifications. 5. At the conclusion of the testing, a report, which shall verify compliance with Section 510.5.4, shall be submitted to the fire code official. 510.6.2 Additional frequencies. The building owner shall modify or expand the emergency responder radio coverage system at their expense in the event frequency changes are required by the FCC or additional frequencies are made available by the FCC. Prior approval of a public safety radio coverage system on previous frequencies does not exempt this section. 510.6.3 Field testing. Agency personnel shall have the right to enter onto the property at any reasonable time to conduct field testing to verify the required level of radio coverage. | HighRise | LISA KIMBALL
52583 | NoData | HighRise | LISA KIMBALL
52595 | NoData | HighRise | LISA KIMBALL
52630 | NoData | HighRise | LISA KIMBALL
52652 | NoData | HighRise | LISA KIMBALL
52676 | NoData | HighRise | LISA KIMBALL
52685 | NoData | HighRise | LISA KIMBALL
52693 | NoData | HighRise | LISA KIMBALL
52699 | NoData | HighRise | LISA KIMBALL
52716 | NoData | HighRise | LISA KIMBALL
53025 | NoData | HighRise | LISA KIMBALL
53188 | NoData | HighRise | LISA KIMBALL
53197 | NoData | HighRise | LISA KIMBALL
53386 | NoData | HighRise | LISA KIMBALL
53470 | NoData | HighRise | LISA KIMBALL
53478 | NoData | HighRise | LISA KIMBALL
53488 | NoData | HighRise | LISA KIMBALL
53491 | NoData | HighRise | LISA KIMBALL
53494 | NoData | HighRise | LISA KIMBALL
53495 | NoData | HighRise | LISA KIMBALL
53541 | NoData | HighRise | LISA KIMBALL
53548 | NoData | HighRise | LISA KIMBALL
53549 | NoData | HighRise | LISA KIMBALL
53551 | NoData | HighRise | LISA KIMBALL
53563 | NoData | HighRise | LISA KIMBALL
53565 | NoData | HighRise | LISA KIMBALL
53566 | NoData | HighRise | LISA KIMBALL
53567 | NoData | HighRise | LISA KIMBALL
53569 | NoData | HighRise | LISA KIMBALL
53695 | THE FIRE ALARM SYSTEM IS YELLOW TAGGED - A TAG WAS ISSUED 06/18/19 AND SYSTEM MUST BE SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
53696 | NoData | HighRise | LISA KIMBALL
53697 | NoData | HighRise | LISA KIMBALL
53698 | NoData | HighRise | LISA KIMBALL
53699 | CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
53786 | THE SPRINKLER SYSTEM IS YELLOW TAGGED - A YELLOW TAG WAS ISSUED IN 12/17 AND MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY THE WATER TANK IS YELLOW TAGGED - A YELLOW TAG WAS ISSUED IN 12/09 AND MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
53787 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
53788 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
53789 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
53790 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
53791 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT OR SERVICE THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
53800 | NoData | HighRise | LISA KIMBALL
53809 | THE SPRINKLER SYSTEM HAS YELLOW TAGS - YELLOW TAG WAS ISSUED IN 01/2019 ON THE PUMP AND 2/2016 ON THE TANK - THESE MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
53810 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED | HighRise | LISA KIMBALL
53811 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
53812 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
53813 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
53814 | NoData | HighRise | LISA KIMBALL
53823 | PROVIDE EVIDENCE OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP THIS INFORMATION ON SITE PROVIDE DOCUMENTATION OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP POSTED ON SITE WITH ALL OTHER PERMITS, WITHIN THE ELEVATOR CAR OR WITHIN 10 FEET OF THE CALL BUTTONS | HighRise | LISA KIMBALL
53824 | HOUSEKEEPING IS REQUIRED IN THE 1ST FLOOR ELEVATOR/MECHANICAL ROOM | HighRise | LISA KIMBALL
53825 | SUPPLY THE CODE FOR ENTRY IN THE 911 BOX SPPLY A SIGN STATING "911 BOX 9@CORNER OF MAIN AND POLK) HAS CODE FOR ACCESS | HighRise | LISA KIMBALL
53826 | FIRE EXTINGUISHERS ARE REQUIRED IN ALL ELEVATOR ROOMS, ELECTRICAL ROOMS, IT ROOMS, GENERATOR ROOMS, MECHANICAL ROOMS AND WHERE FLAMMABLES ARE STORED PROVIDE FIRE EXTINGUISHERS IN THE EQUIPMENT ROOM (AT EACH DOOR) AND IN THE BREAK ROOM ON THE SECOND FLOOR | HighRise | LISA KIMBALL
53827 | PROVIDE COVERS MECHANICAL/ELECTRICAL ROOMS ON THE 1ST AND 2ND FLOORS FOR OPEN JUNCTION BOXES | HighRise | LISA KIMBALL
53828 | THE BACK EXIT DOORS WHICH ARE LOCATED IN THE LOADING DOCK MUST BE IDENTIFIED AND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS | HighRise | LISA KIMBALL
53829 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOST RECENT TEST EXIT SIGNS WERE FOUND OUT/NOT ILLUMINATED ON THE 2ND FLOOR NEAR THE MECHANICAL/ELECTRICAL ROOM - REPAIR OR REPLACE THEM IMMEDIATELY | HighRise | LISA KIMBALL
53830 | PROVIDE ADDITIONAL EXIT SIGNS ON THE WALL IN THE STAIRWELL ON THE GROUND FLOOR (LEAVING THE CLASS AREA) TO DETER OCCUPANTS FROM CONTINUING BACK TO THE STAIRS AND AWAY FROM THE ACTUAL EXIT | HighRise | LISA KIMBALL
53831 | NoData | HighRise | LISA KIMBALL
53832 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
53833 | NoData | HighRise | LISA KIMBALL
53834 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
53835 | PROVIDE A UL APPROVED RED CAN IN THE ELEVATOR ROOM AND ENSURE IT IS EMPTIED DAILY | HighRise | LISA KIMBALL
53836 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIRE A LETTER - PROVIDE A PHOTOCOPY OF THESE PERMITS. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - REQUIRED IF BOILER ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
53837 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED | HighRise | LISA KIMBALL
53838 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE MECHANICAL/ELECTRICAL ROOMS ON THE 1ST AND 2ND FLOORS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
53839 | NO 'PIGGYBACKING' OF MULTIPLE EXTENSION CORDS ALLOWED - USE ONLY ONE UL APPROVED, SURGE-PROTECTED EXTENSION CORD FROM THE WALL TO THE APPLIANCE OR APPLIANCES IN THE MASS CHALLENGE ROOM UNDER THE TABLE AND IN OFFICES NEARBY - | HighRise | LISA KIMBALL
53840 | PERMITS THE INSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS: Key Box Permit - Flammable and Combustible Permit - Fire Alarm Permit - Elevator Operating Permit - Boiler Permit - Other - Assembly, Access Gates, Batteries, etc. - Certificate of Occupancies - Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
53841 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
53842 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
53843 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
53844 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENT APPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
53845 | SUPPLY A LETTER INDICATING 1313 MAIN IS IN COMPLIANCE WITH APPENDIX J | HighRise | LISA KIMBALL
53846 | THE ELECTRICAL ROOM ON THE CLAY SIDE MUST BE IDENTIFIED AND LABELED AS SUCH | HighRise | LISA KIMBALL
53847 | PROVIDE SIGN ON THE DOOR OF THE EQUIPMENT ROOM (FROM THE GARAGE AND FROM THE TENANT SIDE) TO INDICATE THE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
53848 | SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
53849 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
53850 | NO CITY MAG LOCK STICKER WAS FOUND ON THE LOADING DOCK DOOR - ENSURE IT IS TESTED AND STICKERED EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE | HighRise | LISA KIMBALL
53851 | THE LOCATION OF THE ELEVATOR ROOM MUST BE IDENTIFIED AND LABELED AS SUCH ON THE DOOR AND ALL DOORS LEADING TO IT THE AIR HANDLER ROOM DOOR MUST ALSO STATE "MECHANICAL ROOM" AND "ELECTRICAL ROOM" | HighRise | LISA KIMBALL
53852 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRE CODE OFFICIAL IS DEPENDENT UPON SUCCESSFUL COMPLETION OF THREE COMPONENTS - CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF A SUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
53853 | EACH MEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
53854 | ATTENDANCE AT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH- RISE FIRE WARDENS | HighRise | LISA KIMBALL
53855 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
53856 | PROVIDE A KEY TO THE FIRE ALARM PANEL OF 1313 MAIN IN THE FIRE DEPOSITORY BOX AND BEHIND THE FRONT DESK; SUPPLY A LABEL INDICATING THE LOCATION OF THE KEYS ON THE FIRE ALARM PANEL | HighRise | LISA KIMBALL
53857 | SUBMIT A COMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS | HighRise | LISA KIMBALL
53858 | NoData | HighRise | LISA KIMBALL
53859 | MANICURE THE LANDSCAPING TO REVEAL THE HIDDEN HYDRANT ON MAIN STREET ENSURE LANDSCAPING DOES NOT OBSCURE FIRE DEPARTMENT ELEMENTS AND/OR FIRE HYDRANTS | HighRise | LISA KIMBALL
53860 | REMOVE AND DISCONTINUE USE OF UNAPPROVED EXTENSION CORD IN THE MASS CHALLENGE ROOM UNDER THE TABLE AND IN OFFICES NEARBY - ONLY UL APPROVED, SURGE PROTECTED CORDS ARE SAFE FOR TEMPORARY USE | HighRise | LISA KIMBALL
53861 | FDC SIGN MUST BE UPDATED - REVIEW LSB #2 SECTION 2.5.4.3 TO REVISE THE FDC SIGN WITH NECESSARY CORRECTIONS AND ENSURE ALL PERTINENT INFORMATION IS INCLUDED Approved signs of weather-resistant materials, with not less than one inch high legible block lettering on a highly contrasting background, shall be placed on or immediately adjacent to all fire department connections and provide the following information: 1. Type of system - STANDPIPE, SPRINKLER, STANDPIPE / SPRINKLER, DRY PIPE SPRINKLER, etc. 2. Which building or structure, or what portion, zone, and floors of the building or structure the FDC serve. i. Ex: FLOORS B1 - 12; LEVELS 1 - 8; HIGH ZONE FLRS 21 - 40; etc. 3. On standpipe and combination standpipe/sprinkler systems - whether there are pressure regulating valves (PRV) or pressure reducing devices (PRD) on the system. System pressures shall also be indicated on all wet standpipe and combination standpipe/sprinkler systems. Examples: NO PRV/PRD (System Pres. 100 PSI) PRD Levels 1 - 7 (System Pres. 150 PSI) PRV Floors 1 - 10 (System Pres. 175 PSI) | HighRise | LISA KIMBALL
53862 | THE LOCK-OUT/TAG-OUT EQUIPMENT AND SETS (SET = 1 LOCK + 1 TAG) MUST BE READILY ACCESSIBLE IN THE ELEVATOR ROOM AND PROPERLY LABELED: PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS | HighRise | LISA KIMBALL
53863 | NoData | HighRise | LISA KIMBALL
53864 | ALL OCCUPANTS OF THE BUILDING SHALL PARTICIPATE IN THE FIRE DRILLS AS REQUIRED BY THE CODE OFFICIAL AND THE FIRE CODE | HighRise | LISA KIMBALL
53865 | APPROVAL OF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFUL COMPLETION OF SEVERALALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF A COMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
53866 | REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Rise or Mid-Rise Atruim Certification Training may send attendees to the following monthly seminars at no cost. Monthly seminars are available for management employees and tenant fire wardens of high-rise buildings who need to be certified. Certificates shall be valid for a period of five years from the date of training. There is no charge for attending these seminars. The only cost incurred may be parking fees, if applicable. Many buildings will have different fire safety features. The building management from each building represented is required to inform its employees and Fire Wardens of their specific fire safety features to complete the certification. Please note this training is not valid for Mid Rise Evacuation Training. For information on mid-rise training please visit the HFD Mid Rise Fire Certification Webpage. Additional training availability information: The Houston Fire Department has set up and implemented a list of all high- rise buildings for Fire Safety Plan approvals. This list was set up to ensure that priority is given to buildings that have the greatest need while also providing each building an equal opportunity. The list of buildings is separated into two groups based on whether the building is an occupancy where people sleep, such as hotel, apartments, and condominiums or those buildings where people do not sleep, such as office buildings. Buildings are then sub- grouped by no sprinkler system, partial sprinkler system, or complete sprinkler systems before sorting by building height. The highest priority building is the residential building that is non-sprinklered, and the tallest in height. Our goal is to provide the needed services to approve each building within a two-year cycle. Buildings desiring to expedite the process also have three additional options. The monthly open high-rise certification seminar is for buildings that have requested to send a limited number of fire wardens and building management employees to a class that is open to all high-rise buildings. The class information is not specific to any particular building and requires building management to supplement the training with their building specifics. An inspector/instructor in the Life Safety Bureau, Public Education Section - High-rise Fire Safety Plan Approvals, may be obtained to provide training outside his regular work hours on an overtime basis. This may be done by contacting Diana Cardenas by e-mail at: diana.cardenas@houstontx.gov. This should be done prior to payment of a required permit fee so that an instructor can be assigned to made contact with the requesting party, to assist the requesting party with information on the application for over-time training and payment of the permit fees, and to schedule a mutually convenient training date. A City of Houston permit fee is required to schedule an inspector/instructor. The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019). Having a City of Houston Fire Marshal approved consultant perform the training. The process to receive an approved Fire Safety Plan consist of the three following essential training elements conducted by persons, institutions or companies approved by the Fire Marshal according to regulations established by the Fire Marshal: a consultation with building management, an approved certification training for Fire Wardens and building employees, and a fire drill supervised by persons, institutions or companies approved by the Fire Marshal. THE CERTIFICATE OF COMPLETION OF FIRE WARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
53867 | REMOVE ALL EVIDENCE OF INACTIVE/NON FUNCTIONING (TELEPHONE AND TELEPHONE BOX AT THE LOADING DOCK DOOR) OR REPAIR IT TO ENABLE A FULLY FUNCTIONAL SYSTEM | HighRise | LISA KIMBALL
53868 | NoData | HighRise | LISA KIMBALL
53869 | PROVIDE 2 ELEVATOR INDEPENDENT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX WHERE 24 HOUR SECURITY IS PROVIDED, INDEPENDANT SERVICE KEYS MAY BE KEPT SECURED AT THE SECURITY CONSOL AND MADE READILY AVAILABLE TO THE FIRE DEPARTMENT UPON REQUEST - A NOTE OR SIGN IN THE FCR REGUARDING THE ALTERNATE PLACEMENT IS SUGGESTED | HighRise | LISA KIMBALL
53870 | THE FIRE ALARM MUST BE TESTED, INSPECTED, TAGGED, MAINTAINED AND FULLY/PROPERLY FUNCTIONING - THE FIRE ALARM WAS YELLOW-TAGGED ON 06/18/19 CALL CERTIFIED TESTING COMPANY TO CONDUCT ANNUAL INSPECTION OF THE SYSTEM PROVIDE A KEY IN A CONVENIENT LOCATION FOR THE FIRE ALARM PANEL AND LABEL THE PANEL INDICATION THE LOCATION OF THE KEY | HighRise | LISA KIMBALL
53871 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
54469 | THE FIRE ALARM SYSTEM IS BLUE TAGGED AND INSPECTED SEPTEMBER 2020 THE SPRINKLER SYSTEM IS BLUE TAGGED AND INSPECTED SEPTEMBER 2020 ALL FIRE EXTINGUISHERS ARE TAGGED (SEPTEMBER 2020), ACCEPTABLE AND ACCESSIBLE IN UNLOCKED CABINETS ALL EXITS ARE UNLOCKED, READILY OPEN AND SECURED WITH PANIC HARDWARE ALL EMERGENCY EXIT LIGHTS ARE ILLUMINATED AND RECENTLY TESTED NEXT 5 YEAR LAST GAS TEST DUE - 07/2021 DATE OF ALARM PERMIT - 09/14/2020 COMPRESSED GAS PERMIT (504 CUBIC FEET) - N/A; QUANTITIES ARE WELL BELOW | HighRise | LISA KIMBALL
55917 | SERVICE AND PASSENGER ELEVATOR EXPIRES 1ST QUARTER 2021FIRE EXTINGUISHERS INSPECTED/TAGGED MARCH 2020DOWNSTAIRS AND UPSTAIRS RISER QUARTERLY INSPECTED SEPT 2020 AND 5 YEAR CONDUCTED JULY 2019GAS TEST CONDUCTEDQUARTERLY ALARM INSPECTION 9/15/20SENSITIVITY FIRE ALARM 2YR TEST 2/25/19FIRE ALARM PERMIT EXPIRES 23JULY21C of O POSTED911 BOX SUPPLIED | HighRise | LISA KIMBALL
56690 | A RE-INSPECTION FEE WILL BEISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
56691 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
56692 | THE EXIT DOORS IN ROOMS 5 AND 11 ARE STICKING - ENSURE ALL EXIT DOORS ARE CAPABLE OF OPENING WITHEASE THE EMERGENCY EGRESS PADDLE ON THE EXTERIOR EXIT IN ROOM 3 IS NOT FUNCTIONING PROPERLY (DOES NOT RELEASE EASILY) WHEN PRESSURE IS APPLIED - ENSURE IT RELEASES EASILY, EVERY TIME IT IS DEPRESSED | HighRise | LISA KIMBALL
56693 | ENSURE THAT THE SMOKE DETECTOR IN THE PARENT ROOM IS CHECKED FOR EXPIRATION DATE AND THE BATTERY IS REPLACED EVERY SIX MONTHS - IT IS CHIRPING EVERY FEW MINUTES | HighRise | LISA KIMBALL
56694 | KEY BOX (K1) PERMIT IS CURRENT AND POSTED ON SITE FIRE ALARM PERMIT IS CURRENT AND POSTED ONSITE FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - JULY 2020 EMERGENCY ESCAPE MAPS ARE ALL POSTED IN PLACE IN EACH CLASSROOM ALL FIRE DRILLS CONDUCTED MONTHLY IN 2019; SCHOOL JUST REOPENED AND WILL RESUME MONTHLY DRILLS THE FIRE ALARM SYSTEM WAS FOUND TO BE IN COMPLIANCE, INACCEPTABLE CONDITION AND CURRENT ANNUAL INSPECTIONS (05/12/20) CONDUCTED - NOFURTHER COMPLIANCE NEEDED | HighRise | LISA KIMBALL
56695 | REMOVE DEADBOLT (PLAYGROUND EXIT) AND LOCKING DOOR HANDLE (FRONT ENTRY/EXIT) WHICH ARE BEING USED IN CONJUNCTION WITH PANIC HARDWARE | HighRise | LISA KIMBALL
56696 | NoData | HighRise | LISA KIMBALL
56697 | OBTAIN A CERTIFICATE OF OCCUPANCY AND ANY OTHER PERMITS REQUIRED PER THE CODE | HighRise | LISA KIMBALL
56698 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
56699 | INFORMATION TO BE INCLUDED IN FIRE SAFETYPLANS | HighRise | LISA KIMBALL
56700 | MISSING ILLUMINATED EMERGENCY EXIT SIGNS MUST BE INSTALLED AND TESTED | HighRise | LISA KIMBALL
56701 | THE CERTIFICATE OF OCCUPANCY AND ALLREQUIRED PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES | HighRise | LISA KIMBALL
56702 | POST ADDRESS CONSPICUOUSLY - THE LOCATION MUST HAVE A NUMERICAL ADDRESS WHICH IS CLEARLY VISIBLE FROM THE STREET | HighRise | LISA KIMBALL
56703 | INFORMATION TO BE INCLUDED IN FIRE EVACUATIONPLANS | HighRise | LISA KIMBALL
56704 | NoData | HighRise | LISA KIMBALL
56705 | WHERE LOCAL FIRE MARSHAL APPROVALS AREREQUIRED BY REGULATORY AGENCIES, APPROVED FIRE SAFETY AND EVACUATION PLANSSHALL BE PREPARED, MAINTAINED AND POSTED IN GROUP E OCCUPANCIES | HighRise | LISA KIMBALL
56706 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRESUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALSAND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ONSITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
56709 | THE SPRINKLER SYSTEM HAS YELLOW TAGS - YELLOW TAG WAS ISSUED IN 01/2019 ON THE PUMP AND 2/2016 ON THE TANK - THESE MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
56710 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED | HighRise | LISA KIMBALL
56711 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
56712 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
56713 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
57333 | NoData | HighRise | LISA KIMBALL
57359 | NoData | HighRise | LISA KIMBALL
57448 | NoData | HighRise | LISA KIMBALL
57461 | NoData | HighRise | LISA KIMBALL
57462 | NoData | HighRise | LISA KIMBALL
57463 | NoData | HighRise | LISA KIMBALL
57464 | NoData | HighRise | LISA KIMBALL
57465 | NoData | HighRise | LISA KIMBALL
57466 | NoData | HighRise | LISA KIMBALL
57467 | NoData | HighRise | LISA KIMBALL
57468 | NoData | HighRise | LISA KIMBALL
57469 | NoData | HighRise | LISA KIMBALL
57470 | NoData | HighRise | LISA KIMBALL
57471 | NoData | HighRise | LISA KIMBALL
57472 | NoData | HighRise | LISA KIMBALL
57473 | NoData | HighRise | LISA KIMBALL
57474 | NoData | HighRise | LISA KIMBALL
57475 | NoData | HighRise | LISA KIMBALL
57476 | NoData | HighRise | LISA KIMBALL
57477 | NoData | HighRise | LISA KIMBALL
57478 | NoData | HighRise | LISA KIMBALL
57479 | NoData | HighRise | LISA KIMBALL
57480 | NoData | HighRise | LISA KIMBALL
57482 | NoData | HighRise | LISA KIMBALL
57483 | NoData | HighRise | LISA KIMBALL
57484 | NoData | HighRise | LISA KIMBALL
57485 | NoData | HighRise | LISA KIMBALL
57486 | NoData | HighRise | LISA KIMBALL
57487 | NoData | HighRise | LISA KIMBALL
57488 | NoData | HighRise | LISA KIMBALL
57489 | NoData | HighRise | LISA KIMBALL
57490 | NoData | HighRise | LISA KIMBALL
57491 | NoData | HighRise | LISA KIMBALL
57492 | NoData | HighRise | LISA KIMBALL
57493 | NoData | HighRise | LISA KIMBALL
57494 | NoData | HighRise | LISA KIMBALL
57495 | NoData | HighRise | LISA KIMBALL
57496 | NoData | HighRise | LISA KIMBALL
57497 | NoData | HighRise | LISA KIMBALL
57498 | NoData | HighRise | LISA KIMBALL
57499 | NoData | HighRise | LISA KIMBALL
57500 | NoData | HighRise | LISA KIMBALL
57501 | NoData | HighRise | LISA KIMBALL
57516 | NoData | HighRise | LISA KIMBALL
57527 | NoData | HighRise | LISA KIMBALL
57528 | NoData | HighRise | LISA KIMBALL
57533 | NoData | HighRise | LISA KIMBALL
57659 | NoData | HighRise | LISA KIMBALL
57685 | NoData | HighRise | LISA KIMBALL
57733 | NoData | HighRise | LISA KIMBALL
57759 | NoData | HighRise | LISA KIMBALL
57775 | NoData | HighRise | LISA KIMBALL
57778 | NoData | HighRise | LISA KIMBALL
57781 | NoData | HighRise | LISA KIMBALL
57786 | NoData | HighRise | LISA KIMBALL
57811 | NoData | HighRise | LISA KIMBALL
58006 | NoData | HighRise | LISA KIMBALL
58036 | NoData | HighRise | LISA KIMBALL
58042 | NoData | HighRise | LISA KIMBALL
58065 | NoData | HighRise | LISA KIMBALL
58077 | NoData | HighRise | LISA KIMBALL
58082 | NoData | HighRise | LISA KIMBALL
58091 | NoData | HighRise | LISA KIMBALL
58095 | NoData | HighRise | LISA KIMBALL
58117 | NoData | HighRise | LISA KIMBALL
58147 | NoData | HighRise | LISA KIMBALL
58151 | NoData | HighRise | LISA KIMBALL
58158 | NoData | HighRise | LISA KIMBALL
58159 | NoData | HighRise | LISA KIMBALL
58876 | NoData | HighRise | LISA KIMBALL
58975 | NoData | HighRise | LISA KIMBALL
58984 | NoData | HighRise | LISA KIMBALL
59001 | NoData | HighRise | LISA KIMBALL
59021 | NoData | HighRise | LISA KIMBALL
59024 | NoData | HighRise | LISA KIMBALL
59025 | NoData | HighRise | LISA KIMBALL
59034 | NoData | HighRise | LISA KIMBALL
59045 | NoData | HighRise | LISA KIMBALL
59306 | NoData | HighRise | LISA KIMBALL
59312 | NoData | HighRise | LISA KIMBALL
59326 | NoData | HighRise | LISA KIMBALL
59331 | NoData | HighRise | LISA KIMBALL
59345 | NoData | HighRise | LISA KIMBALL
59754 | NoData | HighRise | LISA KIMBALL
59778 | NoData | HighRise | LISA KIMBALL
59819 | NoData | HighRise | LISA KIMBALL
59837 | CITATIONS WILL BE WRITTEN AFTER 2REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT METWITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
59838 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30 CALENDARDAYS | HighRise | LISA KIMBALL
59839 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
59840 | NoData | HighRise | LISA KIMBALL
59841 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIREDIF THE HIGH-RISE DOES NOT HAVE ANY OF THESESYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED)DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30 CALENDAR DAYS | HighRise | LISA KIMBALL
59842 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
59843 | EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE | HighRise | LISA KIMBALL
59844 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
59845 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
59846 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIREPROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY ORNON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEMIS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
59847 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
59848 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
59849 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERAL ALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
59850 | Take the Fire Warden Certification class online through the following link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottom to click onHigh-rise Fire Warden Certification Class.Print out the certificate of completion and keep it in a safe place where it can be accessed upon demand. REGISTER FOR FIRE WARDEN TRAINING AThttps://houstontx.gov/fire/HFMO/highrisecert.htmlAny Building Manager in need of High-Riseor Mid-Rise Atruim Certification Training may send attendees to the followingmonthly seminars at no cost. Monthly seminars are available for managementemployees and tenant fire wardens of high-rise buildings who need to becertified. Certificates shall be valid for a period of five years from the dateof training.There is no charge for attending theseseminars. The only cost incurred may be parking fees, if applicable. Manybuildings will have different fire safety features. The building managementfrom each building represented is required to inform its employees and FireWardens of their specific fire safety features to complete the certification. Please note this training is not valid forMid Rise Evacuation Training. For information on mid rise training please visitthe HFD Mid Rise Fire Certication Webpage.Additional training availability information:The Houston Fire Department has set up and implemented a list of all high-risebuildings for Fire Safety Plan approvals. This list was set up to ensure thatpriority is given to buildings that have the greatest need while also providingeach building an equal opportunity. The list of buildings is separated into twogroups based on whether the building is an occupancy where people sleep, suchas hotel, apartments, and condominiums or those buildings where people do notsleep, such as office buildings. Buildings are then sub-grouped by no sprinklersystem, partial sprinkler system, or complete sprinkler systems before sortingby building height. The highest priority building is the residential buildingthat is non-sprinklered, and the tallest in height. Our goal is to provide theneeded services to approve each building within a two-year cycle. Buildingsdesiring to expedite the process also have three additional options. 1. The monthly openhigh-rise certification seminar is for buildings that have requested to send alimited number of fire wardens and building management employees to a classthat is open to all high-rise buildings. The class information is not specificto any particular building and requires building management to supplement thetraining with their building specifics.2. An inspector/instructorin the Life Safety Bureau, Public Education Section - High-rise Fire SafetyPlan Approvals, may be obtained to provide training outside his regular workhours on an overtime basis. This may be done by contacting Diana Cardenas bye-mail at:diana.cardenas@houstontx.gov. This should be done prior to payment of arequired permit fee so that an instructor can be assigned to made contact withthe requesting party, to assist the requesting party with information on theapplication for over-time training and payment of the permit fees, and toschedule a mutually convenient training date.A City of Houston permit fee is required to schedule an inspector/instructor.The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019).3. Having a City of HoustonFire Marshal approved consultant perform the training. The process to receivean approved Fire Safety Plan consist of the three following essential trainingelements conducted by persons, institutions or companies approved by the FireMarshal according to regulations established by the Fire Marshal: aconsultation with building management, an approved certification training forFire Wardens and building employees, and a fire drill supervised by persons,institutions or companies approved by the Fire Marshal. | HighRise | LISA KIMBALL
59851 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS | HighRise | LISA KIMBALL
59852 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
59853 | Concerningfire drills during COVID-19, a link can be found by going to the "Resources" andthen clicking on "Notices"https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/ | HighRise | LISA KIMBALL
59854 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
59855 | MEMBERS OF THE FIRESAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
59856 | NoData | HighRise | LISA KIMBALL
59860 | NoData | HighRise | LISA KIMBALL
59882 | NoData | HighRise | LISA KIMBALL
59886 | NO RE-ENTRY FROM THE TOP FLOOR STAIRWELL AFTER 2 CALLS, NO ACCESS ON 9TH FLOOR STAIR A AND THE CALL BOX ON THE 9TH FLOOR STAIR B IS NOT WORKING | HighRise | LISA KIMBALL
59887 | CITATIONS WILL BE WRITTEN AFTER 2REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT METWITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
59888 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30 CALENDARDAYS | HighRise | LISA KIMBALL
59889 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
59890 | FACILITYNEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMSHAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TESTFAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIREINSPECTOR SIGNING OFF ON THE INSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTIONEQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHATTESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUETAGGED, RED TAGGED,YELLOW TAGGED OR FAILED.DO NOT PROVIDE TEST REPORTS, BILLING INVOICES ORCHECKS PAID. Long term deficiencieswill require a letter of intent with a time line arrived at after consultationwith the fire inspector. (Managementshall obtain an acceptability letter for 3-5 year tests that do not have a lettercurrently on file)." Certificate of Occupancy: Core of BuildingC of O only - REQUIRED" Active Fire Permits: Up to date and Paid -REQUIRED" Fire Depository Box Keys Letter: A letterstating all Fire Depository Box keys work properly and have been checked foroperation - REQUIRED" Fire Marshal Training &amp; EvacuationLetter: A letter stating all fire wardens, property management employees, staffand/or contract personnel have attended the proper training and building hasconducted fire drills as per HFD Standards - REQUIRED" Fire Alarm Permit - Annual - REQUIRED" Sprinkler Percentage Letter and Form(included in report) - REQUIRED" Electronic Locks -Semi Annual - REQUIRED" Sprinkler System - Annual - REQUIRED" Fire Alarm System Test - Annual - REQUIRED" Fire Extinguishers - Annual - REQUIRED" Fire Hoses – Annual - REQUIRED " Fire Pumps Flow Test - Annual - REQUIRED" Emergency Power &amp; Lighting - Annual -REQUIRED" Generator Test (ATS) - Annual - REQUIRED" Fire Alarm Audibility Test - 3 Year -REQUIRED" Fire Hose Pressure Test - 3 year - REQUIRED" Fire Dampers - 4 Year - REQUIRED" Fire Alarm Sensitivity - 2 Year - REQUIRED" FDC Test (Bldg. &amp; Garage) - 5 Year -REQUIRED" PRV / PRD Test - 5 Year - REQUIRED" Stair pressurization Test - 5 Year -REQUIRED" Standpipe System - 5 Year - REQUIRED" Water Supply Tank Inspection - 5 Year -REQUIRED" Boiler Permit - N/A – REQUIRED IF BOILERSON SITE" Elevator Permit - Annual - REQUIRED" Dry Partial or Full Trip Test - REQUIRED" Gas Test - 5 Year - REQUIRED IF GAS ON SITE" FireFighter Phones or Emergency ResponderRadio Coverage - REQUIREDIF THE HIGH-RISE DOES NOTHAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD(SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30CALENDAR DAYS | HighRise | LISA KIMBALL
59891 | LOCK ON 911 BOX ON THE GARAGE GATE IS RUSTED SHUT - REPLACE LOCK WITH NEW FALCON LOCK - CALL THE INSPECTOR FOR ASSISTANCE WITH SECURING NEW LOCK NO 911 BOX TO GAIN ENTRY TO THE MAIN BUILDING - 24HR SECURITY | HighRise | LISA KIMBALL
59892 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
59893 | LOCATEAND IDENTIFY FIRE DEPARTMENT TEST CONNECTIONS | HighRise | LISA KIMBALL
59894 | ENSURE ALL FIRE PHONESARE PROVIDED IN THEIR CRADLES (ONLY 3 PRESENT) AND ARE TESTED ANNUALLY | HighRise | LISA KIMBALL
59895 | IDENTIFY THE1230 SYSTEM ON THE 7TH FLOOR WITH A SIGN/LABEL AND A WARNING SYSTEM ON BOTH DOORS LEADING INTO THE ROOM THIS SYSTEM (GAS AND ALARM) WAS LAST INSPECTED IN 2015 - IT MUST BE INSPECTED ANNUALLY | HighRise | LISA KIMBALL
59896 | EVIDENCE OF INCOMPLETEOR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALLFUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TOTHE FIRE CODE | HighRise | LISA KIMBALL
59897 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
59898 | PERTAINING TO SPACEHEATER USE, PLEASE REFER TO THE FOLLOWING CODES(605.10.1 -605.10.4) TO ENSURE SAFE USE | HighRise | LISA KIMBALL
59899 | PERTAINING TO SPACEHEATER USE, PLEASE REFER TO THE FOLLOWING CODES(605.10.1 -605.10.4) TO ENSURE SAFE USE | HighRise | LISA KIMBALL
59900 | PERTAINING TO SPACEHEATER USE, PLEASE REFER TO THE FOLLOWING CODES(605.10.1 -605.10.4) TO ENSURE SAFE USE | HighRise | LISA KIMBALL
59901 | PERTAINING TO SPACEHEATER USE, PLEASE REFER TO THE FOLLOWING CODES(605.10.1 -605.10.4) TO ENSURE SAFE USE | HighRise | LISA KIMBALL
59902 | PERTAINING TO SPACEHEATER USE, PLEASE REFER TO THE FOLLOWING CODES(605.10.1 -605.10.4) TO ENSURE SAFE USE | HighRise | LISA KIMBALL
59903 | PROVIDE 2ELEVATOR INDEPENDENT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TOBE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX WHERE 24HOUR SECURITY IS PROVIDED, INDEPENDANT SERVICE KEYS MAY BE KEPT SECURED AT THESECURITY CONSOL AND MADE READILY AVAILABLE TO THE FIRE DEPARTMENT UPON REQUEST- A NOTE OR SIGN IN THE FCR REGUARDING THE ALTERNATE PLACEMENT IS SUGGESTED | HighRise | LISA KIMBALL
59904 | PROVIDE 5 COPIES OF THE HIGH SURVEY (ONLY 1 COPY WAS FOUND IN THE BINDER) | HighRise | LISA KIMBALL
59905 | NEED 5 ELEVATOR ROOM KEYS ON THE 5 SETS OF KEYS IN THE FIRE DEPOSITORY BOX - ENSURE ALL 5SETS OF KEYS REMAIN IN THE FDB AT ALL TIMES | HighRise | LISA KIMBALL
59906 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
59907 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT OR SERVICE TO THE OWNER/OCCUPANT AND TO THE JURISDICTION – BY PHONE 713.884.3143 AND EMAIL AT HFD.DISPATCH3@houstontx.gov THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEMIS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
59908 | THE ALARM SYSTEM IS RED TAGGED - SYSTEM MUST BE SERVICED OR REPAIRED IMMEDIATELY THE WATER TANK IS YELLOW TAGGED AND MUSTBE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
59909 | NoData | HighRise | LISA KIMBALL
59910 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
59911 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
59912 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERAL ALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
59913 | Take the Fire Warden Certification class online through thefollowing link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottomto click on High-rise Fire Warden CertificationClass.Print out the certificate of completion and keep it in a safeplace where it can be accessed upon demand. REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Riseor Mid-Rise Atruim Certification Training may send attendees to the followingmonthly seminars at no cost. Monthly seminars are available for managementemployees and tenant fire wardens of high-rise buildings who need to becertified. Certificates shall be valid for a period of five years from the dateof training.There is no charge for attending theseseminars. The only cost incurred may be parking fees, if applicable. Manybuildings will have different fire safety features. The building managementfrom each building represented is required to inform its employees and FireWardens of their specific fire safety features to complete the certification. Please note this training is not valid forMid Rise Evacuation Training. For information on mid rise training please visitthe HFD Mid Rise Fire Certication Webpage.Additional training availability information:The Houston Fire Department has set up and implemented a list of all high-risebuildings for Fire Safety Plan approvals. This list was set up to ensure thatpriority is given to buildings that have the greatest need while also providingeach building an equal opportunity. The list of buildings is separated into twogroups based on whether the building is an occupancy where people sleep, suchas hotel, apartments, and condominiums or those buildings where people do notsleep, such as office buildings. Buildings are then sub-grouped by no sprinklersystem, partial sprinkler system, or complete sprinkler systems before sortingby building height. The highest priority building is the residential buildingthat is non-sprinklered, and the tallest in height. Our goal is to provide theneeded services to approve each building within a two-year cycle. Buildingsdesiring to expedite the process also have three additional options. 1. The monthly openhigh-rise certification seminar is for buildings that have requested to send alimited number of fire wardens and building management employees to a classthat is open to all high-rise buildings. The class information is not specificto any particular building and requires building management to supplement thetraining with their building specifics.2. An inspector/instructorin the Life Safety Bureau, Public Education Section - High-rise Fire SafetyPlan Approvals, may be obtained to provide training outside his regular workhours on an overtime basis. This may be done by contacting Diana Cardenas bye-mail at:diana.cardenas@houstontx.gov. This should be done prior to payment of arequired permit fee so that an instructor can be assigned to made contact withthe requesting party, to assist the requesting party with information on theapplication for over-time training and payment of the permit fees, and toschedule a mutually convenient training date.A City of Houston permit fee is required to schedule an inspector/instructor.The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019).3. Having a City of HoustonFire Marshal approved consultant perform the training. The process to receivean approved Fire Safety Plan consist of the three following essential trainingelements conducted by persons, institutions or companies approved by the FireMarshal according to regulations established by the Fire Marshal: aconsultation with building management, an approved certification training forFire Wardens and building employees, and a fire drill supervised by persons,institutions or companies approved by the Fire Marshal. | HighRise | LISA KIMBALL
59914 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS | HighRise | LISA KIMBALL
59915 | SUBMIT ACOMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINEDFIRE WARDENS HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
59916 | Concerningfire drills during COVID-19, a link can be found by going to the "Resources" andthen clicking on "Notices"https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/ | HighRise | LISA KIMBALL
59917 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
59918 | MEMBERS OF THE FIRESAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
59919 | NoData | HighRise | LISA KIMBALL
59922 | NoData | HighRise | LISA KIMBALL
59929 | NoData | HighRise | LISA KIMBALL
59936 | NoData | HighRise | LISA KIMBALL
60100 | CITATIONS WILL BEWRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT METWITHIN 30 DAYS | HighRise | LISA KIMBALL
60101 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30CALENDAR DAYS | HighRise | LISA KIMBALL
60102 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
60103 | NoData | HighRise | LISA KIMBALL
60104 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIREDIF THE HIGH-RISE DOES NOT HAVE ANY OF THESESYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED)DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30 CALENDAR DAYS | HighRise | LISA KIMBALL
60105 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
60106 | EVIDENCE OF INCOMPLETE ORNON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONINGSYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRECODE | HighRise | LISA KIMBALL
60107 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
60108 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
60109 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY AREPLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT ORSERVICE TO THE OWNER/OCCUPANT AND TO THE JURISDICTION – BY PHONE 713.884.3143AND EMAIL AT HFD.DISPATCH3@houstontx.gov THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THESYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
60110 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
60111 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
60112 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERAL ALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
60113 | Take the Fire Warden Certification class online through thefollowing link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottomto click on High-rise Fire Warden CertificationClass.Print out the certificate of completion and keep it in a safeplace where it can be accessed upon demand. REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Riseor Mid-Rise Atruim Certification Training may send attendees to the followingmonthly seminars at no cost. Monthly seminars are available for managementemployees and tenant fire wardens of high-rise buildings who need to becertified. Certificates shall be valid for a period of five years from the dateof training.There is no charge for attending theseseminars. The only cost incurred may be parking fees, if applicable. Manybuildings will have different fire safety features. The building managementfrom each building represented is required to inform its employees and FireWardens of their specific fire safety features to complete the certification. Please note this training is not valid forMid Rise Evacuation Training. For information on mid rise training please visitthe HFD Mid Rise Fire Certication Webpage.Additional training availability information:The Houston Fire Department has set up and implemented a list of all high-risebuildings for Fire Safety Plan approvals. This list was set up to ensure thatpriority is given to buildings that have the greatest need while also providingeach building an equal opportunity. The list of buildings is separated into twogroups based on whether the building is an occupancy where people sleep, suchas hotel, apartments, and condominiums or those buildings where people do notsleep, such as office buildings. Buildings are then sub-grouped by no sprinklersystem, partial sprinkler system, or complete sprinkler systems before sortingby building height. The highest priority building is the residential buildingthat is non-sprinklered, and the tallest in height. Our goal is to provide theneeded services to approve each building within a two-year cycle. Buildingsdesiring to expedite the process also have three additional options. 1. The monthly openhigh-rise certification seminar is for buildings that have requested to send alimited number of fire wardens and building management employees to a classthat is open to all high-rise buildings. The class information is not specificto any particular building and requires building management to supplement thetraining with their building specifics.2. An inspector/instructorin the Life Safety Bureau, Public Education Section - High-rise Fire SafetyPlan Approvals, may be obtained to provide training outside his regular workhours on an overtime basis. This may be done by contacting Diana Cardenas bye-mail at:diana.cardenas@houstontx.gov. This should be done prior to payment of arequired permit fee so that an instructor can be assigned to made contact withthe requesting party, to assist the requesting party with information on theapplication for over-time training and payment of the permit fees, and toschedule a mutually convenient training date.A City of Houston permit fee is required to schedule an inspector/instructor.The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019).3. Having a City of HoustonFire Marshal approved consultant perform the training. The process to receivean approved Fire Safety Plan consist of the three following essential trainingelements conducted by persons, institutions or companies approved by the FireMarshal according to regulations established by the Fire Marshal: aconsultation with building management, an approved certification training forFire Wardens and building employees, and a fire drill supervised by persons,institutions or companies approved by the Fire Marshal. | HighRise | LISA KIMBALL
60114 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS | HighRise | LISA KIMBALL
60115 | SUBMIT ACOMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINEDFIRE WARDENS HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
60116 | Concerningfire drills during COVID-19, a link can be found by going to the "Resources" andthen clicking on "Notices"https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/ | HighRise | LISA KIMBALL
60117 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
60118 | MEMBERS OF THEFIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
60119 | NoData | HighRise | LISA KIMBALL
60288 | NoData | HighRise | LISA KIMBALL
60311 | NoData | HighRise | LISA KIMBALL
60338 | NoData | HighRise | LISA KIMBALL
60353 | NoData | HighRise | LISA KIMBALL
60368 | NoData | HighRise | LISA KIMBALL
60386 | NoData | HighRise | LISA KIMBALL
60399 | NoData | HighRise | LISA KIMBALL
60422 | NoData | HighRise | LISA KIMBALL
60437 | NoData | HighRise | LISA KIMBALL
60446 | NoData | HighRise | LISA KIMBALL
60452 | NoData | HighRise | LISA KIMBALL
60453 | NoData | HighRise | LISA KIMBALL
60456 | NoData | HighRise | LISA KIMBALL
60460 | NoData | HighRise | LISA KIMBALL
60463 | NoData | HighRise | LISA KIMBALL
60476 | NoData | HighRise | LISA KIMBALL
60568 | PERTAINING TO MOBILE FOOD UNITS (FOOD TRUCKS) | HighRise | LISA KIMBALL
60569 | PERTAINING TO MOBILE FOOD UNITS (FOOD TRUCKS) A PERMIT FOR STANDBY PERSONNEL WILL BE REQUIRED BY THE FIRE MARSHAL FOR USE OF ANY LP-GAS APPLIANCES INSIDE DOL NO.1 OR NO. 2 | HighRise | LISA KIMBALL
60570 | NoData | HighRise | LISA KIMBALL
60571 | A REINSPECTION FEE WILL ONLY ACCRUE IFTOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOPRIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTIONFEES ARE CHARGED | HighRise | LISA KIMBALL
60572 | PERTAINING TO MOBILE FOOD UNITS (FOOD TRUCKS) IT IS SUGGESTED THAT ALL MFUs PRACTICE THE USE OF WHEEL CHOCKS TO AVOID ACCIDENTAL 'ROLLING' - THE DRIVE WHERE THE MFUs ARE STAGED IS ON A SLOPE | HighRise | LISA KIMBALL
60573 | NoData | HighRise | LISA KIMBALL
60574 | PERTAINING TO MOBILE FOOD UNITS (FOOD TRUCKS) A STANDBY MUST BE OBTAINED IF MFUs (FOOD TRUCKS) ARE PLACED WITHIN 60 FEET OF ANOTHER MFU PER HOUSTON FIRE DEPARTMENT LIFE SAFETY BUREAU STANDARD 10 p.14 CITATIONS WILL BE ISSUED TO GREENWAY IF A 60 FOOT DISTANCE IS NOT MAINTAINED OR PERMIT NOT OBTAINED TO GRANT THIS EXCEPTION | HighRise | LISA KIMBALL
60575 | PERTAINING TO MOBILE FOOD UNITS (FOOD TRUCKS) | HighRise | LISA KIMBALL
60576 | PERTAINING TO MOBILE FOOD UNITS (FOOD TRUCKS) ENSURE THE APPROPRIATE EXTINGUISHERS ARE IN PLACE AND READILY ACCESSIBLE ON ALL FOOD TRUCKS ENSURE ALL FOOD TRUCKS ARE PLACARDED WITH A MEDALLION FROM THE HEALTH DEPARTMENT AND HAVE A CURRENT PERMIT (POSTED) FROM THE FIRE DEPARTMENT | HighRise | LISA KIMBALL
60577 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRESUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALSAND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ONSITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
60578 | PERTAINING TO MOBILE FOOD UNITS (FOOD TRUCKS) | HighRise | LISA KIMBALL
60579 | NoData | HighRise | LISA KIMBALL
60580 | NoData | HighRise | LISA KIMBALL
60581 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
60582 | NoData | HighRise | LISA KIMBALL
60583 | PERTAINING TO MOBILE FOOD UNITS (FOOD TRUCKS) | HighRise | LISA KIMBALL
60584 | PERTAINING TO MOBILE FOOD UNITS (FOOD TRUCKS) MAINTAIN A DISTANCE OF AT LEAST 10 FEET BETWEEN ANY HEAT SOURCE AND COMBUSTIBLE OR FLAMMIBLE MATERIALS DISCONTINUE THE PRACTICE OF PARKING FOOD TRUCKS UNDER ANY UNPROTECTED AREAS OF THE BUILDING (ABSENCE OF FIRE PROTECTION/FIRE SPRINLERS) INCLUDING THE CATWALKS | HighRise | LISA KIMBALL
60585 | NoData | HighRise | LISA KIMBALL
60586 | PERTAINING TO MOBILE FOOD UNITS (FOOD TRUCKS) MOBILE FOOD UNITS SHALL NOT EXCEED LP GAS QUANTITY EXCEEDS LIMITS; IF LIMITS ARE EXCEEDED, A PERMIT AND STANDBY MUST BE OBTAINED | HighRise | LISA KIMBALL
60587 | ???????????????? PERTAINING TO MOBILE FOOD UNITS (FOOD TRUCKS) MOBILE FOOD UNITS SHALL NOT EXCEED LP GAS QUANTITY EXCEEDS LIMITS; IF LIMITS ARE EXCEEDED, A PERMIT AND STANDBY MUST BE OBTAINED | HighRise | LISA KIMBALL
60588 | NoData | HighRise | LISA KIMBALL
60589 | NoData | HighRise | LISA KIMBALL
60590 | NoData | HighRise | LISA KIMBALL
60591 | PERTAINING TO MOBILE FOOD UNITS (FOOD TRUCKS) | HighRise | LISA KIMBALL
63649 | NoData | HighRise | LISA KIMBALL
63668 | NoData | HighRise | LISA KIMBALL
63678 | NoData | HighRise | LISA KIMBALL
63683 | NoData | HighRise | LISA KIMBALL
63709 | NoData | HighRise | LISA KIMBALL
63715 | NoData | HighRise | LISA KIMBALL
63728 | NoData | HighRise | LISA KIMBALL
63734 | NoData | HighRise | LISA KIMBALL
63744 | NoData | HighRise | LISA KIMBALL
63746 | NoData | HighRise | LISA KIMBALL
63749 | NoData | HighRise | LISA KIMBALL
63754 | NoData | HighRise | LISA KIMBALL
63777 | NoData | HighRise | LISA KIMBALL
63784 | NoData | HighRise | LISA KIMBALL
63787 | NoData | HighRise | LISA KIMBALL
63790 | NoData | HighRise | LISA KIMBALL
63837 | NoData | HighRise | LISA KIMBALL
63857 | NoData | HighRise | LISA KIMBALL
63863 | NoData | HighRise | LISA KIMBALL
63866 | NoData | HighRise | LISA KIMBALL
63875 | NoData | HighRise | LISA KIMBALL
63902 | NoData | HighRise | LISA KIMBALL
63907 | NoData | HighRise | LISA KIMBALL
63916 | NoData | HighRise | LISA KIMBALL
63917 | NoData | HighRise | LISA KIMBALL
63918 | NoData | HighRise | LISA KIMBALL
63919 | NoData | HighRise | LISA KIMBALL
63920 | NoData | HighRise | LISA KIMBALL
63921 | NoData | HighRise | LISA KIMBALL
63922 | NoData | HighRise | LISA KIMBALL
63923 | NoData | HighRise | LISA KIMBALL
63924 | NoData | HighRise | LISA KIMBALL
63925 | NoData | HighRise | LISA KIMBALL
63926 | NoData | HighRise | LISA KIMBALL
63927 | NoData | HighRise | LISA KIMBALL
63928 | NoData | HighRise | LISA KIMBALL
63929 | NoData | HighRise | LISA KIMBALL
63930 | NoData | HighRise | LISA KIMBALL
63931 | NoData | HighRise | LISA KIMBALL
63932 | NoData | HighRise | LISA KIMBALL
63933 | NoData | HighRise | LISA KIMBALL
63934 | NoData | HighRise | LISA KIMBALL
63935 | NoData | HighRise | LISA KIMBALL
63937 | NoData | HighRise | LISA KIMBALL
63980 | NoData | HighRise | LISA KIMBALL
64022 | NoData | HighRise | LISA KIMBALL
64028 | NoData | HighRise | LISA KIMBALL
64032 | NoData | HighRise | LISA KIMBALL
64035 | NoData | HighRise | LISA KIMBALL
64053 | NoData | HighRise | LISA KIMBALL
64062 | NoData | HighRise | LISA KIMBALL
64066 | NoData | HighRise | LISA KIMBALL
64072 | NoData | HighRise | LISA KIMBALL
64081 | NoData | HighRise | LISA KIMBALL
64097 | NoData | HighRise | LISA KIMBALL
64109 | NoData | HighRise | LISA KIMBALL
64110 | NoData | HighRise | LISA KIMBALL
64114 | NoData | HighRise | LISA KIMBALL
64120 | NoData | HighRise | LISA KIMBALL
64125 | NoData | HighRise | LISA KIMBALL
64131 | NoData | HighRise | LISA KIMBALL
64134 | NoData | HighRise | LISA KIMBALL
64144 | NoData | HighRise | LISA KIMBALL
64428 | PROVIDE EVIDENCE OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP THIS INFORMATION ON SITE PROVIDE DOCUMENTATION OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP POSTED ON SITE WITH ALL OTHER PERMITS, WITHIN THE ELEVATOR CAR OR WITHIN 10 FEET OF THE CALL BUTTONS | HighRise | LISA KIMBALL
64429 | HOUSEKEEPING IS REQUIRED IN THE 1ST FLOOR ELEVATOR/MECHANICAL ROOM | HighRise | LISA KIMBALL
64430 | SUPPLY THE CODE FOR ENTRY IN THE 911 BOX SPPLY A SIGN STATING "911 BOX 9@CORNER OF MAIN AND POLK) HAS CODE FOR ACCESS | HighRise | LISA KIMBALL
64431 | FIRE EXTINGUISHERS ARE REQUIRED IN ALL ELEVATOR ROOMS, ELECTRICAL ROOMS, IT ROOMS, GENERATOR ROOMS, MECHANICAL ROOMS AND WHERE FLAMMABLES ARE STORED PROVIDE FIRE EXTINGUISHERS IN THE EQUIPMENT ROOM (AT EACH DOOR) AND IN THE BREAK ROOM ON THE SECOND FLOOR | HighRise | LISA KIMBALL
64432 | PROVIDE COVERS MECHANICAL/ELECTRICAL ROOMS ON THE 1ST AND 2ND FLOORS FOR OPEN JUNCTION BOXES | HighRise | LISA KIMBALL
64433 | THE BACK EXIT DOORS WHICH ARE LOCATED IN THE LOADING DOCK MUST BE IDENTIFIED AND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS | HighRise | LISA KIMBALL
64434 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOST RECENT TEST EXIT SIGNS WERE FOUND OUT/NOT ILLUMINATED ON THE 2ND FLOOR NEAR THE MECHANICAL/ELECTRICAL ROOM - REPAIR OR REPLACE THEM IMMEDIATELY | HighRise | LISA KIMBALL
64435 | PROVIDE ADDITIONAL EXIT SIGNS ON THE WALL IN THE STAIRWELL ON THE GROUND FLOOR (LEAVING THE CLASS AREA) TO DETER OCCUPANTS FROM CONTINUING BACK TO THE STAIRS AND AWAY FROM THE ACTUAL EXIT | HighRise | LISA KIMBALL
64436 | NoData | HighRise | LISA KIMBALL
64437 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
64438 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
64439 | NoData | HighRise | LISA KIMBALL
64440 | PROVIDE A UL APPROVED RED CAN IN THE ELEVATOR ROOM AND ENSURE IT IS EMPTIED DAILY | HighRise | LISA KIMBALL
64441 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIRE A LETTER - PROVIDE A PHOTOCOPY OF THESE PERMITS. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - REQUIRED IF BOILER ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
64442 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED | HighRise | LISA KIMBALL
64443 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE MECHANICAL/ELECTRICAL ROOMS ON THE 1ST AND 2ND FLOORS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
64444 | NO 'PIGGYBACKING' OF MULTIPLE EXTENSION CORDS ALLOWED - USE ONLY ONE UL APPROVED, SURGE-PROTECTED EXTENSION CORD FROM THE WALL TO THE APPLIANCE OR APPLIANCES IN THE MASS CHALLENGE ROOM UNDER THE TABLE AND IN OFFICES NEARBY - | HighRise | LISA KIMBALL
64445 | PERMITS THE INSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS: Key Box Permit - Flammable and Combustible Permit - Fire Alarm Permit - Elevator Operating Permit - Boiler Permit - Other - Assembly, Access Gates, Batteries, etc. - Certificate of Occupancies - Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
64446 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
64447 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
64448 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
64449 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENT APPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
64450 | SUPPLY A LETTER INDICATING 1313 MAIN IS IN COMPLIANCE WITH APPENDIX J | HighRise | LISA KIMBALL
64451 | THE ELECTRICAL ROOM ON THE CLAY SIDE MUST BE IDENTIFIED AND LABELED AS SUCH | HighRise | LISA KIMBALL
64452 | PROVIDE SIGN ON THE DOOR OF THE EQUIPMENT ROOM (FROM THE GARAGE AND FROM THE TENANT SIDE) TO INDICATE THE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
64453 | SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
64454 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
64455 | NO CITY MAG LOCK STICKER WAS FOUND ON THE LOADING DOCK DOOR - ENSURE IT IS TESTED AND STICKERED EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE | HighRise | LISA KIMBALL
64456 | THE LOCATION OF THE ELEVATOR ROOM MUST BE IDENTIFIED AND LABELED AS SUCH ON THE DOOR AND ALL DOORS LEADING TO IT THE AIR HANDLER ROOM DOOR MUST ALSO STATE "MECHANICAL ROOM" AND "ELECTRICAL ROOM" | HighRise | LISA KIMBALL
64457 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRE CODE OFFICIAL IS DEPENDENT UPON SUCCESSFUL COMPLETION OF THREE COMPONENTS - CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF A SUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
64458 | EACH MEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
64459 | ATTENDANCE AT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH- RISE FIRE WARDENS | HighRise | LISA KIMBALL
64460 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
64461 | PROVIDE A KEY TO THE FIRE ALARM PANEL OF 1313 MAIN IN THE FIRE DEPOSITORY BOX AND BEHIND THE FRONT DESK; SUPPLY A LABEL INDICATING THE LOCATION OF THE KEYS ON THE FIRE ALARM PANEL | HighRise | LISA KIMBALL
64462 | SUBMIT A COMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS | HighRise | LISA KIMBALL
64463 | NoData | HighRise | LISA KIMBALL
64464 | MANICURE THE LANDSCAPING TO REVEAL THE HIDDEN HYDRANT ON MAIN STREET ENSURE LANDSCAPING DOES NOT OBSCURE FIRE DEPARTMENT ELEMENTS AND/OR FIRE HYDRANTS | HighRise | LISA KIMBALL
64465 | REMOVE AND DISCONTINUE USE OF UNAPPROVED EXTENSION CORD IN THE MASS CHALLENGE ROOM UNDER THE TABLE AND IN OFFICES NEARBY - ONLY UL APPROVED, SURGE PROTECTED CORDS ARE SAFE FOR TEMPORARY USE | HighRise | LISA KIMBALL
64466 | FDC SIGN MUST BE UPDATED - REVIEW LSB #2 SECTION 2.5.4.3 TO REVISE THE FDC SIGN WITH NECESSARY CORRECTIONS AND ENSURE ALL PERTINENT INFORMATION IS INCLUDED Approved signs of weather-resistant materials, with not less than one inch high legible block lettering on a highly contrasting background, shall be placed on or immediately adjacent to all fire department connections and provide the following information: 1. Type of system - STANDPIPE, SPRINKLER, STANDPIPE / SPRINKLER, DRY PIPE SPRINKLER, etc. 2. Which building or structure, or what portion, zone, and floors of the building or structure the FDC serve. i. Ex: FLOORS B1 - 12; LEVELS 1 - 8; HIGH ZONE FLRS 21 - 40; etc. 3. On standpipe and combination standpipe/sprinkler systems - whether there are pressure regulating valves (PRV) or pressure reducing devices (PRD) on the system. System pressures shall also be indicated on all wet standpipe and combination standpipe/sprinkler systems. Examples: NO PRV/PRD (System Pres. 100 PSI) PRD Levels 1 - 7 (System Pres. 150 PSI) PRV Floors 1 - 10 (System Pres. 175 PSI) | HighRise | LISA KIMBALL
64467 | THE LOCK-OUT/TAG-OUT EQUIPMENT AND SETS (SET = 1 LOCK + 1 TAG) MUST BE READILY ACCESSIBLE IN THE ELEVATOR ROOM AND PROPERLY LABELED: PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS | HighRise | LISA KIMBALL
64468 | NoData | HighRise | LISA KIMBALL
64469 | ALL OCCUPANTS OF THE BUILDING SHALL PARTICIPATE IN THE FIRE DRILLS AS REQUIRED BY THE CODE OFFICIAL AND THE FIRE CODE | HighRise | LISA KIMBALL
64470 | APPROVAL OF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFUL COMPLETION OF SEVERALALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF A COMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
64471 | REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Rise or Mid-Rise Atruim Certification Training may send attendees to the following monthly seminars at no cost. Monthly seminars are available for management employees and tenant fire wardens of high-rise buildings who need to be certified. Certificates shall be valid for a period of five years from the date of training. There is no charge for attending these seminars. The only cost incurred may be parking fees, if applicable. Many buildings will have different fire safety features. The building management from each building represented is required to inform its employees and Fire Wardens of their specific fire safety features to complete the certification. Please note this training is not valid for Mid Rise Evacuation Training. For information on mid-rise training please visit the HFD Mid Rise Fire Certification Webpage. Additional training availability information: The Houston Fire Department has set up and implemented a list of all high- rise buildings for Fire Safety Plan approvals. This list was set up to ensure that priority is given to buildings that have the greatest need while also providing each building an equal opportunity. The list of buildings is separated into two groups based on whether the building is an occupancy where people sleep, such as hotel, apartments, and condominiums or those buildings where people do not sleep, such as office buildings. Buildings are then sub- grouped by no sprinkler system, partial sprinkler system, or complete sprinkler systems before sorting by building height. The highest priority building is the residential building that is non-sprinklered, and the tallest in height. Our goal is to provide the needed services to approve each building within a two-year cycle. Buildings desiring to expedite the process also have three additional options. The monthly open high-rise certification seminar is for buildings that have requested to send a limited number of fire wardens and building management employees to a class that is open to all high-rise buildings. The class information is not specific to any particular building and requires building management to supplement the training with their building specifics. An inspector/instructor in the Life Safety Bureau, Public Education Section - High-rise Fire Safety Plan Approvals, may be obtained to provide training outside his regular work hours on an overtime basis. This may be done by contacting Diana Cardenas by e-mail at: diana.cardenas@houstontx.gov. This should be done prior to payment of a required permit fee so that an instructor can be assigned to made contact with the requesting party, to assist the requesting party with information on the application for over-time training and payment of the permit fees, and to schedule a mutually convenient training date. A City of Houston permit fee is required to schedule an inspector/instructor. The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019). Having a City of Houston Fire Marshal approved consultant perform the training. The process to receive an approved Fire Safety Plan consist of the three following essential training elements conducted by persons, institutions or companies approved by the Fire Marshal according to regulations established by the Fire Marshal: a consultation with building management, an approved certification training for Fire Wardens and building employees, and a fire drill supervised by persons, institutions or companies approved by the Fire Marshal. THE CERTIFICATE OF COMPLETION OF FIRE WARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
64472 | REMOVE ALL EVIDENCE OF INACTIVE/NON FUNCTIONING (TELEPHONE AND TELEPHONE BOX AT THE LOADING DOCK DOOR) OR REPAIR IT TO ENABLE A FULLY FUNCTIONAL SYSTEM | HighRise | LISA KIMBALL
64473 | NoData | HighRise | LISA KIMBALL
64474 | PROVIDE 2 ELEVATOR INDEPENDENT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX WHERE 24 HOUR SECURITY IS PROVIDED, INDEPENDANT SERVICE KEYS MAY BE KEPT SECURED AT THE SECURITY CONSOL AND MADE READILY AVAILABLE TO THE FIRE DEPARTMENT UPON REQUEST - A NOTE OR SIGN IN THE FCR REGUARDING THE ALTERNATE PLACEMENT IS SUGGESTED | HighRise | LISA KIMBALL
64475 | THE FIRE ALARM MUST BE TESTED, INSPECTED, TAGGED, MAINTAINED AND FULLY/PROPERLY FUNCTIONING - THE FIRE ALARM WAS YELLOW-TAGGED ON 06/18/19 CALL CERTIFIED TESTING COMPANY TO CONDUCT ANNUAL INSPECTION OF THE SYSTEM PROVIDE A KEY IN A CONVENIENT LOCATION FOR THE FIRE ALARM PANEL AND LABEL THE PANEL INDICATION THE LOCATION OF THE KEY | HighRise | LISA KIMBALL
64476 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
64477 | CITATIONS WILL BEWRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT METWITHIN 30 DAYS | HighRise | LISA KIMBALL
64478 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30CALENDAR DAYS | HighRise | LISA KIMBALL
64479 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
64480 | NoData | HighRise | LISA KIMBALL
64481 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIREDIF THE HIGH-RISE DOES NOT HAVE ANY OF THESESYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED)DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30 CALENDAR DAYS | HighRise | LISA KIMBALL
64482 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
64483 | EVIDENCE OF INCOMPLETE ORNON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONINGSYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRECODE | HighRise | LISA KIMBALL
64484 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
64485 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
64486 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY AREPLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT ORSERVICE TO THE OWNER/OCCUPANT AND TO THE JURISDICTION – BY PHONE 713.884.3143AND EMAIL AT HFD.DISPATCH3@houstontx.gov THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THESYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
64487 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
64488 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
64489 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERAL ALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
64490 | Take the Fire Warden Certification class online through thefollowing link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottomto click on High-rise Fire Warden CertificationClass.Print out the certificate of completion and keep it in a safeplace where it can be accessed upon demand. REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Riseor Mid-Rise Atruim Certification Training may send attendees to the followingmonthly seminars at no cost. Monthly seminars are available for managementemployees and tenant fire wardens of high-rise buildings who need to becertified. Certificates shall be valid for a period of five years from the dateof training.There is no charge for attending theseseminars. The only cost incurred may be parking fees, if applicable. Manybuildings will have different fire safety features. The building managementfrom each building represented is required to inform its employees and FireWardens of their specific fire safety features to complete the certification. Please note this training is not valid forMid Rise Evacuation Training. For information on mid rise training please visitthe HFD Mid Rise Fire Certication Webpage.Additional training availability information:The Houston Fire Department has set up and implemented a list of all high-risebuildings for Fire Safety Plan approvals. This list was set up to ensure thatpriority is given to buildings that have the greatest need while also providingeach building an equal opportunity. The list of buildings is separated into twogroups based on whether the building is an occupancy where people sleep, suchas hotel, apartments, and condominiums or those buildings where people do notsleep, such as office buildings. Buildings are then sub-grouped by no sprinklersystem, partial sprinkler system, or complete sprinkler systems before sortingby building height. The highest priority building is the residential buildingthat is non-sprinklered, and the tallest in height. Our goal is to provide theneeded services to approve each building within a two-year cycle. Buildingsdesiring to expedite the process also have three additional options. 1. The monthly openhigh-rise certification seminar is for buildings that have requested to send alimited number of fire wardens and building management employees to a classthat is open to all high-rise buildings. The class information is not specificto any particular building and requires building management to supplement thetraining with their building specifics.2. An inspector/instructorin the Life Safety Bureau, Public Education Section - High-rise Fire SafetyPlan Approvals, may be obtained to provide training outside his regular workhours on an overtime basis. This may be done by contacting Diana Cardenas bye-mail at:diana.cardenas@houstontx.gov. This should be done prior to payment of arequired permit fee so that an instructor can be assigned to made contact withthe requesting party, to assist the requesting party with information on theapplication for over-time training and payment of the permit fees, and toschedule a mutually convenient training date.A City of Houston permit fee is required to schedule an inspector/instructor.The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019).3. Having a City of HoustonFire Marshal approved consultant perform the training. The process to receivean approved Fire Safety Plan consist of the three following essential trainingelements conducted by persons, institutions or companies approved by the FireMarshal according to regulations established by the Fire Marshal: aconsultation with building management, an approved certification training forFire Wardens and building employees, and a fire drill supervised by persons,institutions or companies approved by the Fire Marshal. | HighRise | LISA KIMBALL
64491 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS | HighRise | LISA KIMBALL
64492 | SUBMIT ACOMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINEDFIRE WARDENS HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
64493 | Concerningfire drills during COVID-19, a link can be found by going to the "Resources" andthen clicking on "Notices"https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/ | HighRise | LISA KIMBALL
64494 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
64495 | MEMBERS OF THEFIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
64496 | NoData | HighRise | LISA KIMBALL
64497 | PROVIDE EVIDENCE OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP THIS INFORMATION ON SITE PROVIDE DOCUMENTATION OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP POSTED ON SITE WITH ALL OTHER PERMITS, WITHIN THE ELEVATOR CAR OR WITHIN 10 FEET OF THE CALL BUTTONS | HighRise | LISA KIMBALL
64498 | HOUSEKEEPING IS REQUIRED IN THE 1ST FLOOR ELEVATOR/MECHANICAL ROOM | HighRise | LISA KIMBALL
64499 | SUPPLY THE CODE FOR ENTRY IN THE 911 BOX SPPLY A SIGN STATING "911 BOX 9@CORNER OF MAIN AND POLK) HAS CODE FOR ACCESS | HighRise | LISA KIMBALL
64500 | FIRE EXTINGUISHERS ARE REQUIRED IN ALL ELEVATOR ROOMS, ELECTRICAL ROOMS, IT ROOMS, GENERATOR ROOMS, MECHANICAL ROOMS AND WHERE FLAMMABLES ARE STORED PROVIDE FIRE EXTINGUISHERS IN THE EQUIPMENT ROOM (AT EACH DOOR) AND IN THE BREAK ROOM ON THE SECOND FLOOR | HighRise | LISA KIMBALL
64501 | PROVIDE COVERS MECHANICAL/ELECTRICAL ROOMS ON THE 1ST AND 2ND FLOORS FOR OPEN JUNCTION BOXES | HighRise | LISA KIMBALL
64502 | THE BACK EXIT DOORS WHICH ARE LOCATED IN THE LOADING DOCK MUST BE IDENTIFIED AND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS | HighRise | LISA KIMBALL
64503 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOST RECENT TEST EXIT SIGNS WERE FOUND OUT/NOT ILLUMINATED ON THE 2ND FLOOR NEAR THE MECHANICAL/ELECTRICAL ROOM - REPAIR OR REPLACE THEM IMMEDIATELY | HighRise | LISA KIMBALL
64504 | PROVIDE ADDITIONAL EXIT SIGNS ON THE WALL IN THE STAIRWELL ON THE GROUND FLOOR (LEAVING THE CLASS AREA) TO DETER OCCUPANTS FROM CONTINUING BACK TO THE STAIRS AND AWAY FROM THE ACTUAL EXIT | HighRise | LISA KIMBALL
64505 | NoData | HighRise | LISA KIMBALL
64506 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
64507 | NoData | HighRise | LISA KIMBALL
64508 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
64509 | PROVIDE A UL APPROVED RED CAN IN THE ELEVATOR ROOM AND ENSURE IT IS EMPTIED DAILY | HighRise | LISA KIMBALL
64510 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIRE A LETTER - PROVIDE A PHOTOCOPY OF THESE PERMITS. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - REQUIRED IF BOILER ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
64511 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED | HighRise | LISA KIMBALL
64512 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE MECHANICAL/ELECTRICAL ROOMS ON THE 1ST AND 2ND FLOORS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
64513 | NO 'PIGGYBACKING' OF MULTIPLE EXTENSION CORDS ALLOWED - USE ONLY ONE UL APPROVED, SURGE-PROTECTED EXTENSION CORD FROM THE WALL TO THE APPLIANCE OR APPLIANCES IN THE MASS CHALLENGE ROOM UNDER THE TABLE AND IN OFFICES NEARBY - | HighRise | LISA KIMBALL
64514 | PERMITS THE INSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS: Key Box Permit - Flammable and Combustible Permit - Fire Alarm Permit - Elevator Operating Permit - Boiler Permit - Other - Assembly, Access Gates, Batteries, etc. - Certificate of Occupancies - Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
64515 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
64516 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
64517 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
64518 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENT APPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
64519 | SUPPLY A LETTER INDICATING 1313 MAIN IS IN COMPLIANCE WITH APPENDIX J | HighRise | LISA KIMBALL
64520 | THE ELECTRICAL ROOM ON THE CLAY SIDE MUST BE IDENTIFIED AND LABELED AS SUCH | HighRise | LISA KIMBALL
64521 | PROVIDE SIGN ON THE DOOR OF THE EQUIPMENT ROOM (FROM THE GARAGE AND FROM THE TENANT SIDE) TO INDICATE THE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
64522 | SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
64523 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
64524 | NO CITY MAG LOCK STICKER WAS FOUND ON THE LOADING DOCK DOOR - ENSURE IT IS TESTED AND STICKERED EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE | HighRise | LISA KIMBALL
64525 | THE LOCATION OF THE ELEVATOR ROOM MUST BE IDENTIFIED AND LABELED AS SUCH ON THE DOOR AND ALL DOORS LEADING TO IT THE AIR HANDLER ROOM DOOR MUST ALSO STATE "MECHANICAL ROOM" AND "ELECTRICAL ROOM" | HighRise | LISA KIMBALL
64526 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRE CODE OFFICIAL IS DEPENDENT UPON SUCCESSFUL COMPLETION OF THREE COMPONENTS - CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF A SUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
64527 | EACH MEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
64528 | ATTENDANCE AT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH- RISE FIRE WARDENS | HighRise | LISA KIMBALL
64529 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
64530 | PROVIDE A KEY TO THE FIRE ALARM PANEL OF 1313 MAIN IN THE FIRE DEPOSITORY BOX AND BEHIND THE FRONT DESK; SUPPLY A LABEL INDICATING THE LOCATION OF THE KEYS ON THE FIRE ALARM PANEL | HighRise | LISA KIMBALL
64531 | SUBMIT A COMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS | HighRise | LISA KIMBALL
64532 | NoData | HighRise | LISA KIMBALL
64533 | MANICURE THE LANDSCAPING TO REVEAL THE HIDDEN HYDRANT ON MAIN STREET ENSURE LANDSCAPING DOES NOT OBSCURE FIRE DEPARTMENT ELEMENTS AND/OR FIRE HYDRANTS | HighRise | LISA KIMBALL
64534 | REMOVE AND DISCONTINUE USE OF UNAPPROVED EXTENSION CORD IN THE MASS CHALLENGE ROOM UNDER THE TABLE AND IN OFFICES NEARBY - ONLY UL APPROVED, SURGE PROTECTED CORDS ARE SAFE FOR TEMPORARY USE | HighRise | LISA KIMBALL
64535 | FDC SIGN MUST BE UPDATED - REVIEW LSB #2 SECTION 2.5.4.3 TO REVISE THE FDC SIGN WITH NECESSARY CORRECTIONS AND ENSURE ALL PERTINENT INFORMATION IS INCLUDED Approved signs of weather-resistant materials, with not less than one inch high legible block lettering on a highly contrasting background, shall be placed on or immediately adjacent to all fire department connections and provide the following information: 1. Type of system - STANDPIPE, SPRINKLER, STANDPIPE / SPRINKLER, DRY PIPE SPRINKLER, etc. 2. Which building or structure, or what portion, zone, and floors of the building or structure the FDC serve. i. Ex: FLOORS B1 - 12; LEVELS 1 - 8; HIGH ZONE FLRS 21 - 40; etc. 3. On standpipe and combination standpipe/sprinkler systems - whether there are pressure regulating valves (PRV) or pressure reducing devices (PRD) on the system. System pressures shall also be indicated on all wet standpipe and combination standpipe/sprinkler systems. Examples: NO PRV/PRD (System Pres. 100 PSI) PRD Levels 1 - 7 (System Pres. 150 PSI) PRV Floors 1 - 10 (System Pres. 175 PSI) | HighRise | LISA KIMBALL
64536 | THE LOCK-OUT/TAG-OUT EQUIPMENT AND SETS (SET = 1 LOCK + 1 TAG) MUST BE READILY ACCESSIBLE IN THE ELEVATOR ROOM AND PROPERLY LABELED: PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS | HighRise | LISA KIMBALL
64537 | NoData | HighRise | LISA KIMBALL
64538 | ALL OCCUPANTS OF THE BUILDING SHALL PARTICIPATE IN THE FIRE DRILLS AS REQUIRED BY THE CODE OFFICIAL AND THE FIRE CODE | HighRise | LISA KIMBALL
64539 | APPROVAL OF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFUL COMPLETION OF SEVERALALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF A COMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
64540 | REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Rise or Mid-Rise Atruim Certification Training may send attendees to the following monthly seminars at no cost. Monthly seminars are available for management employees and tenant fire wardens of high-rise buildings who need to be certified. Certificates shall be valid for a period of five years from the date of training. There is no charge for attending these seminars. The only cost incurred may be parking fees, if applicable. Many buildings will have different fire safety features. The building management from each building represented is required to inform its employees and Fire Wardens of their specific fire safety features to complete the certification. Please note this training is not valid for Mid Rise Evacuation Training. For information on mid-rise training please visit the HFD Mid Rise Fire Certification Webpage. Additional training availability information: The Houston Fire Department has set up and implemented a list of all high- rise buildings for Fire Safety Plan approvals. This list was set up to ensure that priority is given to buildings that have the greatest need while also providing each building an equal opportunity. The list of buildings is separated into two groups based on whether the building is an occupancy where people sleep, such as hotel, apartments, and condominiums or those buildings where people do not sleep, such as office buildings. Buildings are then sub- grouped by no sprinkler system, partial sprinkler system, or complete sprinkler systems before sorting by building height. The highest priority building is the residential building that is non-sprinklered, and the tallest in height. Our goal is to provide the needed services to approve each building within a two-year cycle. Buildings desiring to expedite the process also have three additional options. The monthly open high-rise certification seminar is for buildings that have requested to send a limited number of fire wardens and building management employees to a class that is open to all high-rise buildings. The class information is not specific to any particular building and requires building management to supplement the training with their building specifics. An inspector/instructor in the Life Safety Bureau, Public Education Section - High-rise Fire Safety Plan Approvals, may be obtained to provide training outside his regular work hours on an overtime basis. This may be done by contacting Diana Cardenas by e-mail at: diana.cardenas@houstontx.gov. This should be done prior to payment of a required permit fee so that an instructor can be assigned to made contact with the requesting party, to assist the requesting party with information on the application for over-time training and payment of the permit fees, and to schedule a mutually convenient training date. A City of Houston permit fee is required to schedule an inspector/instructor. The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019). Having a City of Houston Fire Marshal approved consultant perform the training. The process to receive an approved Fire Safety Plan consist of the three following essential training elements conducted by persons, institutions or companies approved by the Fire Marshal according to regulations established by the Fire Marshal: a consultation with building management, an approved certification training for Fire Wardens and building employees, and a fire drill supervised by persons, institutions or companies approved by the Fire Marshal. THE CERTIFICATE OF COMPLETION OF FIRE WARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
64541 | REMOVE ALL EVIDENCE OF INACTIVE/NON FUNCTIONING (TELEPHONE AND TELEPHONE BOX AT THE LOADING DOCK DOOR) OR REPAIR IT TO ENABLE A FULLY FUNCTIONAL SYSTEM | HighRise | LISA KIMBALL
64542 | NoData | HighRise | LISA KIMBALL
64543 | PROVIDE 2 ELEVATOR INDEPENDENT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX WHERE 24 HOUR SECURITY IS PROVIDED, INDEPENDANT SERVICE KEYS MAY BE KEPT SECURED AT THE SECURITY CONSOL AND MADE READILY AVAILABLE TO THE FIRE DEPARTMENT UPON REQUEST - A NOTE OR SIGN IN THE FCR REGUARDING THE ALTERNATE PLACEMENT IS SUGGESTED | HighRise | LISA KIMBALL
64544 | THE FIRE ALARM MUST BE TESTED, INSPECTED, TAGGED, MAINTAINED AND FULLY/PROPERLY FUNCTIONING - THE FIRE ALARM WAS YELLOW-TAGGED ON 06/18/19 CALL CERTIFIED TESTING COMPANY TO CONDUCT ANNUAL INSPECTION OF THE SYSTEM PROVIDE A KEY IN A CONVENIENT LOCATION FOR THE FIRE ALARM PANEL AND LABEL THE PANEL INDICATION THE LOCATION OF THE KEY | HighRise | LISA KIMBALL
64545 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
64546 | CITATIONS WILL BE WRITTEN AFTER 2REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT METWITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
64547 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30 CALENDARDAYS | HighRise | LISA KIMBALL
64548 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
64549 | NoData | HighRise | LISA KIMBALL
64550 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIREDIF THE HIGH-RISE DOES NOT HAVE ANY OF THESESYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED)DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30 CALENDAR DAYS | HighRise | LISA KIMBALL
64551 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
64552 | EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE | HighRise | LISA KIMBALL
64553 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
64554 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
64555 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIREPROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY ORNON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEMIS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
64556 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
64557 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
64558 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERAL ALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
64559 | Take the Fire Warden Certification class online through the following link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottom to click onHigh-rise Fire Warden Certification Class.Print out the certificate of completion and keep it in a safe place where it can be accessed upon demand. REGISTER FOR FIRE WARDEN TRAINING AThttps://houstontx.gov/fire/HFMO/highrisecert.htmlAny Building Manager in need of High-Riseor Mid-Rise Atruim Certification Training may send attendees to the followingmonthly seminars at no cost. Monthly seminars are available for managementemployees and tenant fire wardens of high-rise buildings who need to becertified. Certificates shall be valid for a period of five years from the dateof training.There is no charge for attending theseseminars. The only cost incurred may be parking fees, if applicable. Manybuildings will have different fire safety features. The building managementfrom each building represented is required to inform its employees and FireWardens of their specific fire safety features to complete the certification. Please note this training is not valid forMid Rise Evacuation Training. For information on mid rise training please visitthe HFD Mid Rise Fire Certication Webpage.Additional training availability information:The Houston Fire Department has set up and implemented a list of all high-risebuildings for Fire Safety Plan approvals. This list was set up to ensure thatpriority is given to buildings that have the greatest need while also providingeach building an equal opportunity. The list of buildings is separated into twogroups based on whether the building is an occupancy where people sleep, suchas hotel, apartments, and condominiums or those buildings where people do notsleep, such as office buildings. Buildings are then sub-grouped by no sprinklersystem, partial sprinkler system, or complete sprinkler systems before sortingby building height. The highest priority building is the residential buildingthat is non-sprinklered, and the tallest in height. Our goal is to provide theneeded services to approve each building within a two-year cycle. Buildingsdesiring to expedite the process also have three additional options. 1. The monthly openhigh-rise certification seminar is for buildings that have requested to send alimited number of fire wardens and building management employees to a classthat is open to all high-rise buildings. The class information is not specificto any particular building and requires building management to supplement thetraining with their building specifics.2. An inspector/instructorin the Life Safety Bureau, Public Education Section - High-rise Fire SafetyPlan Approvals, may be obtained to provide training outside his regular workhours on an overtime basis. This may be done by contacting Diana Cardenas bye-mail at:diana.cardenas@houstontx.gov. This should be done prior to payment of arequired permit fee so that an instructor can be assigned to made contact withthe requesting party, to assist the requesting party with information on theapplication for over-time training and payment of the permit fees, and toschedule a mutually convenient training date.A City of Houston permit fee is required to schedule an inspector/instructor.The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019).3. Having a City of HoustonFire Marshal approved consultant perform the training. The process to receivean approved Fire Safety Plan consist of the three following essential trainingelements conducted by persons, institutions or companies approved by the FireMarshal according to regulations established by the Fire Marshal: aconsultation with building management, an approved certification training forFire Wardens and building employees, and a fire drill supervised by persons,institutions or companies approved by the Fire Marshal. | HighRise | LISA KIMBALL
64560 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS | HighRise | LISA KIMBALL
64561 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
64562 | Concerningfire drills during COVID-19, a link can be found by going to the "Resources" andthen clicking on "Notices"https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/ | HighRise | LISA KIMBALL
64563 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
64564 | MEMBERS OF THE FIRESAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
64565 | NoData | HighRise | LISA KIMBALL
64568 | CITATIONS WILL BE WRITTEN AFTER 2REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT METWITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
64569 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30 CALENDARDAYS | HighRise | LISA KIMBALL
64570 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
64571 | NoData | HighRise | LISA KIMBALL
64572 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIREDIF THE HIGH-RISE DOES NOT HAVE ANY OF THESESYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED)DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30 CALENDAR DAYS | HighRise | LISA KIMBALL
64573 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
64574 | EVIDENCE OF INCOMPLETE ORNON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONINGSYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRECODE | HighRise | LISA KIMBALL
64575 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
64576 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
64577 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIREPROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY ORNON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEMIS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
64578 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
64579 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
64580 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERAL ALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
64581 | Take the Fire Warden Certification class online through thefollowing link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottomto click on High-rise Fire Warden CertificationClass.Print out the certificate of completion and keep it in a safeplace where it can be accessed upon demand. REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Riseor Mid-Rise Atruim Certification Training may send attendees to the followingmonthly seminars at no cost. Monthly seminars are available for managementemployees and tenant fire wardens of high-rise buildings who need to becertified. Certificates shall be valid for a period of five years from the dateof training.There is no charge for attending theseseminars. The only cost incurred may be parking fees, if applicable. Manybuildings will have different fire safety features. The building managementfrom each building represented is required to inform its employees and FireWardens of their specific fire safety features to complete the certification. Please note this training is not valid forMid Rise Evacuation Training. For information on mid rise training please visitthe HFD Mid Rise Fire Certication Webpage.Additional training availability information:The Houston Fire Department has set up and implemented a list of all high-risebuildings for Fire Safety Plan approvals. This list was set up to ensure thatpriority is given to buildings that have the greatest need while also providingeach building an equal opportunity. The list of buildings is separated into twogroups based on whether the building is an occupancy where people sleep, suchas hotel, apartments, and condominiums or those buildings where people do notsleep, such as office buildings. Buildings are then sub-grouped by no sprinklersystem, partial sprinkler system, or complete sprinkler systems before sortingby building height. The highest priority building is the residential buildingthat is non-sprinklered, and the tallest in height. Our goal is to provide theneeded services to approve each building within a two-year cycle. Buildingsdesiring to expedite the process also have three additional options. 1. The monthly openhigh-rise certification seminar is for buildings that have requested to send alimited number of fire wardens and building management employees to a classthat is open to all high-rise buildings. The class information is not specificto any particular building and requires building management to supplement thetraining with their building specifics.2. An inspector/instructorin the Life Safety Bureau, Public Education Section - High-rise Fire SafetyPlan Approvals, may be obtained to provide training outside his regular workhours on an overtime basis. This may be done by contacting Diana Cardenas bye-mail at:diana.cardenas@houstontx.gov. This should be done prior to payment of arequired permit fee so that an instructor can be assigned to made contact withthe requesting party, to assist the requesting party with information on theapplication for over-time training and payment of the permit fees, and toschedule a mutually convenient training date.A City of Houston permit fee is required to schedule an inspector/instructor.The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019).3. Having a City of HoustonFire Marshal approved consultant perform the training. The process to receivean approved Fire Safety Plan consist of the three following essential trainingelements conducted by persons, institutions or companies approved by the FireMarshal according to regulations established by the Fire Marshal: aconsultation with building management, an approved certification training forFire Wardens and building employees, and a fire drill supervised by persons,institutions or companies approved by the Fire Marshal. | HighRise | LISA KIMBALL
64582 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS | HighRise | LISA KIMBALL
64583 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRE CODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS - CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF A SUPERVISED FIRE DRILL SUBMIT A COMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINEDFIRE WARDENS | HighRise | LISA KIMBALL
64584 | Concerningfire drills during COVID-19, a link can be found by going to the "Resources" andthen clicking on "Notices"https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/ | HighRise | LISA KIMBALL
64585 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
64586 | MEMBERS OF THE FIRESAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
64587 | NoData | HighRise | LISA KIMBALL
64588 | HOUSEKEEPING IS REQUIRED IN THE GROUND FLOOR MECHANICAL ROOM (BY KRUP) | HighRise | LISA KIMBALL
64589 | FIRE EXTINGUISHERS ARE REQUIRED IN ALL ELEVATOR ROOMS, ELECTRICAL ROOMS, IT ROOMS, GENERATOR ROOMS AND MECHANICAL ROOMS PROVIDE A FIRE EXTINGUISHER IN THE FIRE CONTROL ROOM AND THE MECHANICAL ROOM IN THE GARAGE | HighRise | LISA KIMBALL
64590 | PROVIDE BLANKS OR COVERS FOR MISSING TEETH, CIRCUITS OR VOIDS IN THE ELECTRICAL PANEL IN THE MECHANICAL ROOMS ON THE ROOF AND THE 11TH FLOORS | HighRise | LISA KIMBALL
64591 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOST RECENT TEST EXIT SIGNS WERE FOUND OUT/NOT ILLUMINATED ON THE 8TH FLOOR ABOVE 803 - REPAIR OR REPLACE THEM IMMEDIATELY | HighRise | LISA KIMBALL
64592 | THE FIRE ALARM SYSTEM IS YELLOW TAGGED - A YELLOW TAG WAS ISSUED IN 14AUG19 AND MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
64593 | PROVIDE EXIT SIGNS ON THE EXTERIOR SIDE AT THE GROUND LEVEL TO IDENTIFY STAIR C | HighRise | LISA KIMBALL
64594 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64595 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
64596 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
64597 | NoData | HighRise | LISA KIMBALL
64598 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - N/A - REQUIRED IF BOILERS ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
64599 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
64600 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN UTILITY ROOMS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR - PROVIDE PROTECTION ON BULBS IN THE 11TH FLOOR ELEVATOR ROOM, THE ELECTRICAL ROOMS ON THE 11TH, 7TH AND 6TH FLOORS, STAIR B ON THE 8TH FLOOR, THE MECHANICAL ROOMS ON THE ROOF, 10TH, 9TH AND GROUND FLOOR AND IN THE DELI | HighRise | LISA KIMBALL
64601 | THE CERTIFICATE OF OCCUPANCY AND ALL PERMITS SHOULD BE POSTED IN THE RESPECTIVE BUSINESS (DELI) | HighRise | LISA KIMBALL
64602 | OBTAIN ALL REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER - THE DELI REQUIRES A CERTIFICATE OF OCCUPANCY | HighRise | LISA KIMBALL
64603 | DOORS TO/FROM THE GARAGE REQUIRE MAG LOCK APPROVAL FROM THE BUILDING DEPARTMENT ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
64604 | ENSURE THE OPENING FORCE FOR THE DOOR LATCH ON THE 11TH FLOOR (STAIR A) AND THE 10TH FLOOR (STAIR B) RELEASE WHEN SUBJECTED TO A FORCE OF NO MORE THAN 15LBS | HighRise | LISA KIMBALL
64605 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
64606 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
64607 | THE MOBILITY IMPAIRED LIST MUST BE UPDATED EVERY 6 MONTHS - LAST UPDATED MARCH 2017 | HighRise | LISA KIMBALL
64608 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64609 | RECEIVED; NO FURTHER ACTION NECESSARY | HighRise | LISA KIMBALL
64610 | THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH (WHICH IS INSIDE THE "MECHANICAL ROOM") ON THE 11TH, 10TH, 9TH, 8TH, 7TH AND 6TH FLOORS | HighRise | LISA KIMBALL
64611 | PROVIDE SIGN ON THE DOOR OF THE GROUND FLOOR ENGINE SHOP TO INDICATE THE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
64612 | SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
64613 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
64614 | EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE REPLACE CIELING TILES OR TURN THE SPRINKLER HEADS UP IN THE ELECTRICAL ROOMS ON THE 9TH, 8TH, 7TH, 6TH, 5TH, 4TH, 3RD AND 2ND FLOORS | HighRise | LISA KIMBALL
64615 | DOOR CLOSERS FOUND ON THE 8TH FLOOR (STAIR B) IS NOT WORKING PROPERLY - ENSURE DOORS ARE LATCHING SHUT ON ALL EXIT STAIRWELL DOORS | HighRise | LISA KIMBALL
64616 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64617 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64618 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64619 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
64620 | REMOVE AND DISCONTINUE STORAGE OF GASOLINE FUELED EQUIPTMENT IN THE FIRE PUMP ROOM | HighRise | LISA KIMBALL
64621 | READ AND REVIEW LSB STANDARD 6; FULL COMPLIANCE OF PROVIDING A PROPERLY SUPPLIED FIRE DEPOSITORY BOX IS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
64622 | PROVIDE DOCUMENTATION OR LETTER TO ENSURE ALL FIREPHONES AND JACKS (IN THE BUILDING ON ALL FLOORS) HAVE BEEN TESTED BY AN APPROVED, CERTIFIED FIRE PROTECTION COMPANY AND FUNCTIONING PROPERLY ENSURE 2 FIRE PHONES ARE PROVIDED | HighRise | LISA KIMBALL
64623 | INDICATE DIRECTION AND LOCATION OF FIRE COMMAND ROOM FROM THE ENTRANCE OF THE BUILDING | HighRise | LISA KIMBALL
64624 | THE ANSUL SYSTEM IN THE DELI WAS LAST INSPECTED AND TAGGED OCTOBER 2016 - ENSURE THE SYSTEM IS INSPECTED AND BLUE TAGGED EVERY 6 MONTHS | HighRise | LISA KIMBALL
64625 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64626 | REMOVE AND DISCONTINUE USE OF UNAPPROVED EXTENSION CORD (BROWN EXTENSION CORD IN THE DELI) - ONLY UL APPROVED, SURGE PROTECTED CORDS ARE SAFE FOR TEMPORARY USE | HighRise | LISA KIMBALL
64627 | ENSURE A SIGN POSTED NEXT TO THE CALL BUTTONS IN THE ELEVATOR LOBBY ON THE 3RD FLOOR WHICH INCLUDES A PICTORIAL OR DIAGRAM OF A MAP SHOWING THE FLOOR LAYOUT AND EXACT LOCATION OF THE EXITS IN RELATION TO THE ELEVATORS | HighRise | LISA KIMBALL
64628 | THE EXIT DOOR IN STAIR A DOES NOT LATCH CLOSED DOOR CLOSERS FOUND ON THE 10TH FLOOR (STAIR A), 9TH FLOOR (STAIR A), 6TH FLOOR (STAIR B), THE 2ND FLOOR (STAIR B) AND THE GROUND FLOOR (STAIR C) ARE NOT WORKING PROPERLY - ENSURE DOORS ARE LATCHING SHUT ON ALL EXIT STAIRWELL DOORS | HighRise | LISA KIMBALL
64629 | CABINETS CONTAINING FIRE FIGHTING EQUIPMENT MUST INDICATE THE EQUIPTMENT CONTAINED THEREIN - "FIRE HOSE" AND/OR "FIRE EXTINGUISHER" - CABINETS MUST BE CORRECTLY MARKED ON THE 8TH FLOOR, 7TH FLOOR, 6TH FLOOR, 4TH FLOOR, GROUND FLOOR AND THROUGHOUT THE GARAGE | HighRise | LISA KIMBALL
64630 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64631 | THE CLASS K FIRE EXTINGUISHER IN THE DELI MUST BE INSPECTED ANNUALLY - LAST INSPECTION WAS OCTOBER 2016 | HighRise | LISA KIMBALL
64632 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64633 | ALL FIRE EXTINGUISHERS MUST HAVE A CURRENT TAG INDICATING DATE OF LAST ANNUAL INSPECTION OR SERVICE/MAINTENANCE - EXTINGUISHER IN THE DELI LAST INSPECTED AND TAGGED IN OCTOBER 2016 AND THE EXTIGUISHER IN THE ELEVATOR ROOM ON THE ROOF WAS LAST INSPECTED IN MAY 2017 | HighRise | LISA KIMBALL
64634 | PROVIDE 2 ELEVATOR INDEPENDANT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX | HighRise | LISA KIMBALL
64635 | PROVIDE 2 ELEVATOR HOISTWAY KEYS/TOOLS (OF EACH TYPE) IN THE FIRE DEPOSITORY BOX - ONLY ONE IS PROVIDED | HighRise | LISA KIMBALL
64636 | THE HOOD VENTS AND HOOD SUPPRESSION SYSTEM IN THE DELI MUST BE INSPECTED AND SERVICED - ENSURE THIS IS CONDUCTED AS SOON AS POSSIBLE AND COMPLIES WITH THE FIRE CODE IN THE FUTURE ALL VENT HOOD SUPPRESSION SYSTEMS MUST BE INSPECTED AND SERVICED AT LEAST EVERY 6 MONTHS - MAINTAIN EVIDENCE ON SITE OR STICKER THE EQUIPMENT INDICATING SERVICE DATE | HighRise | LISA KIMBALL
64637 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
64645 | PROVIDE A COVER PLATE FOR EXPOSED ELECTRICAL OUTLET BEHIND THE UPS BOX ON THE GROUND FLOOR | HighRise | LISA KIMBALL
64646 | THE BACK EXIT DOOR AND ABOVE ACCESS GATE CONTROL TO SUITE 700 SHOULD BE LABELED "SUITE 700 ACCESS GATE CONTROL" | HighRise | LISA KIMBALL
64647 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64648 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
64649 | NoData | HighRise | LISA KIMBALL
64650 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
64651 | ENSURE THE EMERGENCY "RE-ENTRY" BUTTON ON THE FIRE ALARM PANEL IS HIGHLIGHTED OR CONSPICUOUSLY LABELED | HighRise | LISA KIMBALL
64652 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - RECIEVED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - RECIEVED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - RECIEVED " Electronic Locks -Semi Annual - RECIEVED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - RECIEVED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - RECIEVED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - RECIEVED " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - RECIEVED " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
64653 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
64654 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE ELEVATOR ROOM ON THE GROUND FLOOR IN JOE'S OFFICE & THE ELCTRICAL ROOM, ON THE 6TH FLOOR, MECHANICAL ROOMS ON THE 12TH & 13TH FLOORS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
64655 | THE EXIT DOOR ON THE 14TH FLOOR STAIR B IS STICKING - ENSURE ALL EXIT DOORS ARE CAPABLE OF OPENING WITH EASE | HighRise | LISA KIMBALL
64656 | OBTAIN ALL REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER - F7 (FLAMMABLE LIQUIDS PERMIT) AND K1 (KEY BOX PERMIT) ARE DUE THE ALARM PERMIT COULD NOT BE LOCATED IN OUR SYSTEM VIA MY SEARCH - PLEASE VISIT THE HOUSTON PERMITTING CENTER AND OBTAIN THE FIRE ALARM PERMIT | HighRise | LISA KIMBALL
64657 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
64658 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
64659 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
64660 | THE MOBILITY IMPAIRED LIST MUST BE UPDATED EVERY 6 MONTHS | HighRise | LISA KIMBALL
64661 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64662 | RECEIVED; NO FURTHER ACTION NECESSARY | HighRise | LISA KIMBALL
64663 | THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH - IDENTIFY ACCESS TO THE ELECTRICAL ROOM THROUGH SUITE 350 | HighRise | LISA KIMBALL
64664 | PROVIDE SIGN ON THE DOOR OF THE PRESSURE WASHING CAGE IN THE GARAGE TO INDICATE THE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
64665 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
64666 | DOOR CLOSER FOUND ON THE 14TH FLOOR (STAIR B) IS NOT WORKING PROPERLY - ENSURE DOORS ARE LATCHING SHUT ON ALL EXIT STAIRWELL DOORS | HighRise | LISA KIMBALL
64667 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64668 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64669 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64670 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
64671 | PERTAINING TO PLACEMENT AND DISTANCE OF FIRE EXTINGUISHERS NEEDED THROUGHOUT THE PARKING GARAGE ENSURE THAT ENOUGH FIRE EXTINGUISHERS ARE SUPPLIED, OBVIOUS AND ACCESSIBLE IN THE PARKING GARAGE (AN S-2) NO FIRE EXTINGUISHERS WERE FOUND IN THE PARKING GARAGE - SUPPLY FIRE EXTINGUISHERS ON ALL LEVELS IN DISTANCES PRESCRIBED BY THE FIRE CODE | HighRise | LISA KIMBALL
64672 | ADD FOBS FOR ENTRY TO ALL 5 SETS OF KEYS IN THE FDB WRITE CODE FOR ENTRY TO PUMP ROOM ON KEY TAG TO PUMP ROOM (ON ALL 5 SETS) READ AND REVIEW LSB STANDARD 6; FULL COMPLIANCE OF PROVIDING A PROPERLY SUPPLIED FIRE DEPOSITORY BOX IS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
64673 | PROVIDE DOCUMENTATION OR LETTER TO ENSURE ALL FIREPHONES AND JACKS (IN THE BUILDING ON ALL FLOORS) HAVE BEEN TESTED BY AN APPROVED, CERTIFIED FIRE PROTECTION COMPANY AND FUNCTIONING PROPERLY FIREFIGHTER PHONES AND ALL JACKS IN THE BUILDING MUST BE TESTED ANNUALLY | HighRise | LISA KIMBALL
64674 | ALL ELECTRICAL ROOMS, HVAC ROOMS, MECHANICAL ROOMS, IT ROOMS, ELEVATOR ROOMS, FIRE SPRINKLER RISER ROOMS, FIRE ALARM ROOMS AND TRANSFORMER ROOMS MUST BE LABELED AS SUCH FOR READY IDENTIFICATION - ID THE "PIT" AND ELEVATOR ROOM ON THE 10TH FLOOR, ID THE MECHANICAL ROOM ON THE 3RD FLOOR, ID THE MECHANICAL ROOM ALSO AS "DRY PIPE" ON THE 3RD FLOOR AND ACCESS TO THE GARAGE ELEVATORS THROUGH SUITE 620 | HighRise | LISA KIMBALL
64675 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64676 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64677 | THE EXIT DOOR ON THE 14TH FLOOR STAIR B DOES NOT LATCH CLOSED | HighRise | LISA KIMBALL
64678 | CABINETS CONTAINING FIRE FIGHTING EQUIPMENT MUST INDICATE THE EQUIPMENT CONTAINED THEREIN - "FIRE HOSE" AND/OR "FIRE EXTINGUISHER" - CORRECTLY IDENTIFY CONTENTS OF CABINET ON THE 3RD FLOOR | HighRise | LISA KIMBALL
64679 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64680 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
64681 | PROVIDE 2 ELEVATOR INDEPENDANT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX | HighRise | LISA KIMBALL
64682 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
64686 | NoData | HighRise | LISA KIMBALL
64691 | NoData | HighRise | LISA KIMBALL
64692 | NoData | HighRise | LISA KIMBALL
64693 | NoData | HighRise | LISA KIMBALL
64694 | NoData | HighRise | LISA KIMBALL
64695 | NoData | HighRise | LISA KIMBALL
64696 | NoData | HighRise | LISA KIMBALL
64697 | NoData | HighRise | LISA KIMBALL
64698 | NoData | HighRise | LISA KIMBALL
64699 | NoData | HighRise | LISA KIMBALL
64700 | NoData | HighRise | LISA KIMBALL
64701 | NoData | HighRise | LISA KIMBALL
64702 | NoData | HighRise | LISA KIMBALL
64703 | NoData | HighRise | LISA KIMBALL
64704 | NoData | HighRise | LISA KIMBALL
64705 | NoData | HighRise | LISA KIMBALL
64706 | NoData | HighRise | LISA KIMBALL
64707 | NoData | HighRise | LISA KIMBALL
64708 | NoData | HighRise | LISA KIMBALL
64709 | NoData | HighRise | LISA KIMBALL
64710 | NoData | HighRise | LISA KIMBALL
64711 | NoData | HighRise | LISA KIMBALL
64712 | NoData | HighRise | LISA KIMBALL
64713 | NoData | HighRise | LISA KIMBALL
64714 | NoData | HighRise | LISA KIMBALL
64715 | NoData | HighRise | LISA KIMBALL
64716 | NoData | HighRise | LISA KIMBALL
64717 | NoData | HighRise | LISA KIMBALL
64718 | NoData | HighRise | LISA KIMBALL
64719 | NoData | HighRise | LISA KIMBALL
64720 | NoData | HighRise | LISA KIMBALL
64721 | NoData | HighRise | LISA KIMBALL
64722 | NoData | HighRise | LISA KIMBALL
64725 | NoData | HighRise | LISA KIMBALL
64730 | NoData | HighRise | LISA KIMBALL
64731 | NoData | HighRise | LISA KIMBALL
64732 | WIRES FOUND HANGING FROM THE CIELING IN THE MAINTENANCE ROOM ON THE GROUND FLOOR MUST BE CAPPED AND SECURED IN THE JUNCTION BOX | HighRise | LISA KIMBALL
64733 | THE LIGHTS ARE NOT OPERATING IN THE STAIRWELL BETWEEN THE 3RD AND 2ND FLOOR AND MUST BE REPAIRED OR REPLACED | HighRise | LISA KIMBALL
64734 | A YELLOW TAGGED WAS DISCOVERED IN ON THE STANDPIPE IN THE STAIRWELL - SYSTEM MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
64735 | IDENTIFY AND LABEL THE FIRE DEPARTMENT TEST CONNECTION ON THE ROOF | HighRise | LISA KIMBALL
64736 | A FIRE DRILL MUST BE SUPERVISED BY JUAN GARCIA - CONTACT HIM PRIOR TO PLANNING AND SCHEDULING | HighRise | LISA KIMBALL
64737 | PERTAINING TO SIGN INDICATING FLAMMABLES OR DIESEL FOR THE MAINTENANCE SHOP AND CENTRAL PLANT | HighRise | LISA KIMBALL
64738 | NoData | HighRise | LISA KIMBALL
64739 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
64740 | PROVIDE UL APPROVED RED CAN IN ELEVATOR ROOMS AND ENSURE THEY ARE EMPTIED DAILY | HighRise | LISA KIMBALL
64741 | SUPPLY STAIRWELL SIGN FOR THE PARKING GARAGE (C AND D) | HighRise | LISA KIMBALL
64742 | Facility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system must be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED FOR GARAGE " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED FOR GARAGE " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - N/A - REQUIRED IF BOILERS ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
64743 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
64744 | PEDESTRIAN DOORS AND/OR MAG LOCKS AND EMERGENCY RELEASE BUTTONS ARE NEEDED IN THE PARKING GARAGE TO ENABLE PEDESTRIANS TO ESCAPE IN CASE OF EMERGENCY | HighRise | LISA KIMBALL
64745 | REMOVE AND DISCONTINUE STORAGE IN EXIT ACCESSES, EXITS OR EXIT DISCHARGES - KEEP THE BACK EXIT OF THE DELI FREE FROM OBTRUCTIONS AT ALL TIMES THE BUILDING IS OCCUPIED | HighRise | LISA KIMBALL
64746 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE MAINTENANCE ROOM ON THE GROUND FLOOR ROOM AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
64747 | A COPIES OF PERMITS (IF NEEDED) AND A CERTIFICATE OF OCCUPANCY FOR THE DELI MUST BE POSTED IN THE BUSINESS | HighRise | LISA KIMBALL
64748 | IF THE DELI HAS AN OCCUPANCY LOAD OF MORE THAN 50 - THE OCCUPANCY LOAD MUST BE POSTED CONSPICUOUSLY NEAR THE ENTRANCE | HighRise | LISA KIMBALL
64749 | OBTAIN ALL REQUIRED PERMITS AND CERTIFICATES OF OCCUPANCY FROM THE HOUSTON PERMITTING CENTER THE DELI WILL REQUIRE AN ASSEMBLY PERMIT (P2) IF THE OCCUPANCY LOAD IS MORE THAN 50 PERSONS | HighRise | LISA KIMBALL
64750 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
64751 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
64752 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
64753 | THE MOBILITY IMPAIRED LIST WAS LAST UPDATED IN 2016 - THIS LIST MUST BE UPDATED EVERY 6 MONTHS | HighRise | LISA KIMBALL
64754 | NoData | HighRise | LISA KIMBALL
64755 | LETTER RECIEVED; NO FURTHER ACTION NECESSARY | HighRise | LISA KIMBALL
64756 | A SIGN OR ADHESIVE STATING "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED" MUST BE POSTED ON OR NEAR THE FRONT ENTRANCE DOOR OF THE DELI | HighRise | LISA KIMBALL
64757 | PROVIDE A FLAMMABLE STORAGE CABINET FOR THE MAINTENANCE SHOP IF NEEDED | HighRise | LISA KIMBALL
64758 | ALL ELECTRICAL CIRCUIT BREAKERS IN ELECTRICAL PANELS MUST BE CLEARLY AND CORRECTLY LABELED - CABINETS #2, 3 AND 4 IN 2L ON THE 2ND FLOOR THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH (ADD "ELECTRICAL ROOM" TO THE MECHANICAL ROOMS) ON THE 8TH, 7TH, 6TH, 5TH, 4TH AND 3RD FLOORS | HighRise | LISA KIMBALL
64759 | PROVIDE SIGN TO INDICATE FLAMMABLES OR DIESEL IN THE MAINTENANCE SHOP AND CENTRAL PLANT | HighRise | LISA KIMBALL
64760 | SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
64761 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
64762 | EVIDENCE OF INCOMPLETE AND NON FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED - ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE | HighRise | LISA KIMBALL
64763 | THE "MECHANICAL ROOM" MUST ALSO BE MARKED "ELEVATOR ROOM" FOR IDENTIFICATION | HighRise | LISA KIMBALL
64764 | SEVERAL DOORS IN THE STAIRWELL DO NOT LATCH CLOSED | HighRise | LISA KIMBALL
64765 | NoData | HighRise | LISA KIMBALL
64766 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION | HighRise | LISA KIMBALL
64767 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION | HighRise | LISA KIMBALL
64768 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
64769 | PERTAINING TO PLACEMENT AND DISTANCE OF FIRE EXTINGUISHERS NEEDED THROUGHOUT THE PARKING GARAGE ENSURE THAT FIRE EXTINGUISHERS ARE SUPPLIED, OBVIOUS AND ACCESSIBLE IN THE PARKING GARAGE (AN S-2) | HighRise | LISA KIMBALL
64770 | NoData | HighRise | LISA KIMBALL
64771 | THE SUPPLEMENTAL INFO SHEET MUST BE UPDATED PROVIDE THE 8X 11 LAMINATED LEGEND CARD IN COLOR THE FDB MUST BE DOUBLE LOCKED SO IT CAN BE ACCESSED BY HFD AND BUILDING MANAGEMENT PROVIDE THE COMBINATION OF THE ROOF LOCK ON ALL 5 KEY RINGS AND IN THE BINDER READ AND REVIEW LSB STANDARD 6; FULL COMPLIANCE OF PROVIDING A PROPERLY SUPPLIED FIRE DEPOSITORY BOX IS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
64772 | FIRE PHONES AND ALL JACKS MUST BE TESTED BY A CERTIFIED COMPANY | HighRise | LISA KIMBALL
64773 | THE ANSUL SYSTEM IN THE DELI WAS LAST INSPECTED IN SEPTEMBER 2014 - THIS SYSTEM MUST BE INSPECTED AND TAGGED AT LEAST EVERY 6 MONTHS | HighRise | LISA KIMBALL
64774 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION | HighRise | LISA KIMBALL
64775 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION | HighRise | LISA KIMBALL
64776 | THE LOCK-OUT/TAG-OUT EQUIPMENT AND SETS MUST BE READILY ACCESSIBLE AND PROPERLY LABELED - SUPPLY EQUIPMENT FOR THE ELEVATOR ROOM ON THE GROUND FLOOR: - PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS - A MINIMUM TWO (2) LOCK-OUT/TAG-OUT SETS FOR 4 TO 6 ELEVATORS - A MINIMUM THREE (3) LOCK-OUT/TAG-OUT SETS FOR 7 OR MORE ELEVATORS | HighRise | LISA KIMBALL
64777 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION | HighRise | LISA KIMBALL
64778 | DOOR CLOSERS FOUND ON THE 3RD FLOOR (STAIR B), THE 2ND FLOOR AND THE GROUND FLOOR (STAIR A) ARE NOT WORKING PROPERLY - ENSURE DOORS ARE LATCHING SHUT ON ALL EXIT STAIRWELL DOORS | HighRise | LISA KIMBALL
64779 | FIRE EXTINGUISHERS IN THE STAIRWELLS ARE NOT A SUBSTITUTE FOR EXTINGUISHERS REQUIRED ON EACH FLOOR IN THE HALLS/CORRIDORS - FIRE EXTINGUISHERS MUST BE CONSPICUOUSLY LOCATED, READILY AVAILABLE AND ALONG "NORMAL PATHS OF TRAVEL" - REMOVE AND RELOCATE FIRE EXTIGUISHERS FROM THE STAIRWELLS ON THE 8TH, 4TH, 3RD AND 2ND FLOORS | HighRise | LISA KIMBALL
64780 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION | HighRise | LISA KIMBALL
64781 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION | HighRise | LISA KIMBALL
64782 | PLEASE CONTACT INSPECTOR JUAN GARCIA BY EMAIL AT Juan.Garcia3@houstontx.gov OR 281.896.7084 WITH QUESTIONS CONCERNING EVACUATION DRILLS, FIRE WARDEN TRAINING, ETC | HighRise | LISA KIMBALL
64783 | THE VENT HOOD SYSTEM IN THE DELI MUST BE INSPECTED AND SERVICED AT LEAST EVERY 6 MONTHS THE VENT HOOD REQUIRES CLEANING | HighRise | LISA KIMBALL
64784 | PROVIDE CAP (MISSING) FOR 3" CONNECTION IN GARAGE | HighRise | LISA KIMBALL
64785 | THE FIRE ALARM MUST DISPLAYS "TROUBLES" AND MUST BE INVESTIGATED AND RECTIFIED | HighRise | LISA KIMBALL
64786 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT OR SERVICE THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
64787 | ENSURE A SET OF INDEPENDENT SERVICE KEYS ARE ACCESSIBLE AND PROVIDED OUTSIDE OF THE FIRE DEPOSITORY BOX FOR EMERGENCIES | HighRise | LISA KIMBALL
64788 | NoData | HighRise | LISA KIMBALL
64789 | NoData | HighRise | LISA KIMBALL
64790 | WIRES FOUND HANGING FROM THE CIELING IN THE MAINTENANCE ROOM ON THE GROUND FLOOR MUST BE CAPPED AND SECURED IN THE JUNCTION BOX | HighRise | LISA KIMBALL
64791 | THE LIGHTS ARE NOT OPERATING IN THE STAIRWELL BETWEEN THE 3RD AND 2ND FLOOR AND MUST BE REPAIRED OR REPLACED | HighRise | LISA KIMBALL
64792 | A YELLOW TAGGED WAS DISCOVERED IN ON THE STANDPIPE IN THE STAIRWELL - SYSTEM MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
64793 | IDENTIFY AND LABEL THE FIRE DEPARTMENT TEST CONNECTION ON THE ROOF | HighRise | LISA KIMBALL
64794 | A FIRE DRILL MUST BE SUPERVISED BY JUAN GARCIA - CONTACT HIM PRIOR TO PLANNING AND SCHEDULING | HighRise | LISA KIMBALL
64795 | PERTAINING TO SIGN INDICATING FLAMMABLES OR DIESEL FOR THE MAINTENANCE SHOP AND CENTRAL PLANT | HighRise | LISA KIMBALL
64796 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
64797 | NoData | HighRise | LISA KIMBALL
64798 | PROVIDE UL APPROVED RED CAN IN ELEVATOR ROOMS AND ENSURE THEY ARE EMPTIED DAILY | HighRise | LISA KIMBALL
64799 | SUPPLY STAIRWELL SIGN FOR THE PARKING GARAGE (C AND D) | HighRise | LISA KIMBALL
64800 | Facility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system must be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED FOR GARAGE " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED FOR GARAGE " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - N/A - REQUIRED IF BOILERS ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
64801 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
64802 | PEDESTRIAN DOORS AND/OR MAG LOCKS AND EMERGENCY RELEASE BUTTONS ARE NEEDED IN THE PARKING GARAGE TO ENABLE PEDESTRIANS TO ESCAPE IN CASE OF EMERGENCY | HighRise | LISA KIMBALL
64803 | REMOVE AND DISCONTINUE STORAGE IN EXIT ACCESSES, EXITS OR EXIT DISCHARGES - KEEP THE BACK EXIT OF THE DELI FREE FROM OBTRUCTIONS AT ALL TIMES THE BUILDING IS OCCUPIED | HighRise | LISA KIMBALL
64804 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE MAINTENANCE ROOM ON THE GROUND FLOOR ROOM AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
64805 | A COPIES OF PERMITS (IF NEEDED) AND A CERTIFICATE OF OCCUPANCY FOR THE DELI MUST BE POSTED IN THE BUSINESS | HighRise | LISA KIMBALL
64806 | IF THE DELI HAS AN OCCUPANCY LOAD OF MORE THAN 50 - THE OCCUPANCY LOAD MUST BE POSTED CONSPICUOUSLY NEAR THE ENTRANCE | HighRise | LISA KIMBALL
64807 | OBTAIN ALL REQUIRED PERMITS AND CERTIFICATES OF OCCUPANCY FROM THE HOUSTON PERMITTING CENTER THE DELI WILL REQUIRE AN ASSEMBLY PERMIT (P2) IF THE OCCUPANCY LOAD IS MORE THAN 50 PERSONS | HighRise | LISA KIMBALL
64808 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
64809 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
64810 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
64811 | THE MOBILITY IMPAIRED LIST WAS LAST UPDATED IN 2016 - THIS LIST MUST BE UPDATED EVERY 6 MONTHS | HighRise | LISA KIMBALL
64812 | NoData | HighRise | LISA KIMBALL
64813 | LETTER RECIEVED; NO FURTHER ACTION NECESSARY | HighRise | LISA KIMBALL
64814 | A SIGN OR ADHESIVE STATING "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED" MUST BE POSTED ON OR NEAR THE FRONT ENTRANCE DOOR OF THE DELI | HighRise | LISA KIMBALL
64815 | PROVIDE A FLAMMABLE STORAGE CABINET FOR THE MAINTENANCE SHOP IF NEEDED | HighRise | LISA KIMBALL
64816 | ALL ELECTRICAL CIRCUIT BREAKERS IN ELECTRICAL PANELS MUST BE CLEARLY AND CORRECTLY LABELED - CABINETS #2, 3 AND 4 IN 2L ON THE 2ND FLOOR THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH (ADD "ELECTRICAL ROOM" TO THE MECHANICAL ROOMS) ON THE 8TH, 7TH, 6TH, 5TH, 4TH AND 3RD FLOORS | HighRise | LISA KIMBALL
64817 | PROVIDE SIGN TO INDICATE FLAMMABLES OR DIESEL IN THE MAINTENANCE SHOP AND CENTRAL PLANT | HighRise | LISA KIMBALL
64818 | SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
64819 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
64820 | EVIDENCE OF INCOMPLETE AND NON FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED - ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE | HighRise | LISA KIMBALL
64821 | THE "MECHANICAL ROOM" MUST ALSO BE MARKED "ELEVATOR ROOM" FOR IDENTIFICATION | HighRise | LISA KIMBALL
64822 | SEVERAL DOORS IN THE STAIRWELL DO NOT LATCH CLOSED | HighRise | LISA KIMBALL
64823 | NoData | HighRise | LISA KIMBALL
64824 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION | HighRise | LISA KIMBALL
64825 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION | HighRise | LISA KIMBALL
64826 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
64827 | PERTAINING TO PLACEMENT AND DISTANCE OF FIRE EXTINGUISHERS NEEDED THROUGHOUT THE PARKING GARAGE ENSURE THAT FIRE EXTINGUISHERS ARE SUPPLIED, OBVIOUS AND ACCESSIBLE IN THE PARKING GARAGE (AN S-2) | HighRise | LISA KIMBALL
64828 | NoData | HighRise | LISA KIMBALL
64829 | THE SUPPLEMENTAL INFO SHEET MUST BE UPDATED PROVIDE THE 8X 11 LAMINATED LEGEND CARD IN COLOR THE FDB MUST BE DOUBLE LOCKED SO IT CAN BE ACCESSED BY HFD AND BUILDING MANAGEMENT PROVIDE THE COMBINATION OF THE ROOF LOCK ON ALL 5 KEY RINGS AND IN THE BINDER READ AND REVIEW LSB STANDARD 6; FULL COMPLIANCE OF PROVIDING A PROPERLY SUPPLIED FIRE DEPOSITORY BOX IS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
64830 | FIRE PHONES AND ALL JACKS MUST BE TESTED BY A CERTIFIED COMPANY | HighRise | LISA KIMBALL
64831 | THE ANSUL SYSTEM IN THE DELI WAS LAST INSPECTED IN SEPTEMBER 2014 - THIS SYSTEM MUST BE INSPECTED AND TAGGED AT LEAST EVERY 6 MONTHS | HighRise | LISA KIMBALL
64832 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION | HighRise | LISA KIMBALL
64833 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION | HighRise | LISA KIMBALL
64834 | THE LOCK-OUT/TAG-OUT EQUIPMENT AND SETS MUST BE READILY ACCESSIBLE AND PROPERLY LABELED - SUPPLY EQUIPMENT FOR THE ELEVATOR ROOM ON THE GROUND FLOOR: - PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS - A MINIMUM TWO (2) LOCK-OUT/TAG-OUT SETS FOR 4 TO 6 ELEVATORS - A MINIMUM THREE (3) LOCK-OUT/TAG-OUT SETS FOR 7 OR MORE ELEVATORS | HighRise | LISA KIMBALL
64835 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION | HighRise | LISA KIMBALL
64836 | DOOR CLOSERS FOUND ON THE 3RD FLOOR (STAIR B), THE 2ND FLOOR AND THE GROUND FLOOR (STAIR A) ARE NOT WORKING PROPERLY - ENSURE DOORS ARE LATCHING SHUT ON ALL EXIT STAIRWELL DOORS | HighRise | LISA KIMBALL
64837 | FIRE EXTINGUISHERS IN THE STAIRWELLS ARE NOT A SUBSTITUTE FOR EXTINGUISHERS REQUIRED ON EACH FLOOR IN THE HALLS/CORRIDORS - FIRE EXTINGUISHERS MUST BE CONSPICUOUSLY LOCATED, READILY AVAILABLE AND ALONG "NORMAL PATHS OF TRAVEL" - REMOVE AND RELOCATE FIRE EXTIGUISHERS FROM THE STAIRWELLS ON THE 8TH, 4TH, 3RD AND 2ND FLOORS | HighRise | LISA KIMBALL
64838 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION | HighRise | LISA KIMBALL
64839 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION | HighRise | LISA KIMBALL
64840 | PLEASE CONTACT INSPECTOR JUAN GARCIA BY EMAIL AT Juan.Garcia3@houstontx.gov OR 281.896.7084 WITH QUESTIONS CONCERNING EVACUATION DRILLS, FIRE WARDEN TRAINING, ETC | HighRise | LISA KIMBALL
64841 | THE VENT HOOD SYSTEM IN THE DELI MUST BE INSPECTED AND SERVICED AT LEAST EVERY 6 MONTHS THE VENT HOOD REQUIRES CLEANING | HighRise | LISA KIMBALL
64842 | PROVIDE CAP (MISSING) FOR 3" CONNECTION IN GARAGE | HighRise | LISA KIMBALL
64843 | THE FIRE ALARM MUST DISPLAYS "TROUBLES" AND MUST BE INVESTIGATED AND RECTIFIED | HighRise | LISA KIMBALL
64844 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT OR SERVICE THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
64845 | ENSURE A SET OF INDEPENDENT SERVICE KEYS ARE ACCESSIBLE AND PROVIDED OUTSIDE OF THE FIRE DEPOSITORY BOX FOR EMERGENCIES | HighRise | LISA KIMBALL
64983 | NoData | HighRise | LISA KIMBALL
65092 | NoData | HighRise | LISA KIMBALL
65101 | CITATIONS WILL BEWRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT METWITHIN 30 DAYS | HighRise | LISA KIMBALL
65102 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30 CALENDARDAYS | HighRise | LISA KIMBALL
65103 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
65104 | NoData | HighRise | LISA KIMBALL
65105 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIREDIF THE HIGH-RISE DOES NOT HAVE ANY OF THESESYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED)DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30 CALENDAR DAYS | HighRise | LISA KIMBALL
65106 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
65107 | EVIDENCE OF INCOMPLETE ORNON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONINGSYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRECODE | HighRise | LISA KIMBALL
65108 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
65109 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
65110 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIREPROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY ORNON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEMIS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
65111 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
65112 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
65113 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERAL ALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
65114 | Take the Fire Warden Certification class online through thefollowing link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottomto click on High-rise Fire Warden CertificationClass.Print out the certificate of completion and keep it in a safeplace where it can be accessed upon demand. REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Riseor Mid-Rise Atruim Certification Training may send attendees to the followingmonthly seminars at no cost. Monthly seminars are available for managementemployees and tenant fire wardens of high-rise buildings who need to becertified. Certificates shall be valid for a period of five years from the dateof training.There is no charge for attending theseseminars. The only cost incurred may be parking fees, if applicable. Manybuildings will have different fire safety features. The building managementfrom each building represented is required to inform its employees and FireWardens of their specific fire safety features to complete the certification. Please note this training is not valid forMid Rise Evacuation Training. For information on mid rise training please visitthe HFD Mid Rise Fire Certication Webpage.Additional training availability information:The Houston Fire Department has set up and implemented a list of all high-risebuildings for Fire Safety Plan approvals. This list was set up to ensure thatpriority is given to buildings that have the greatest need while also providingeach building an equal opportunity. The list of buildings is separated into twogroups based on whether the building is an occupancy where people sleep, suchas hotel, apartments, and condominiums or those buildings where people do notsleep, such as office buildings. Buildings are then sub-grouped by no sprinklersystem, partial sprinkler system, or complete sprinkler systems before sortingby building height. The highest priority building is the residential buildingthat is non-sprinklered, and the tallest in height. Our goal is to provide theneeded services to approve each building within a two-year cycle. Buildingsdesiring to expedite the process also have three additional options. 1. The monthly openhigh-rise certification seminar is for buildings that have requested to send alimited number of fire wardens and building management employees to a classthat is open to all high-rise buildings. The class information is not specificto any particular building and requires building management to supplement thetraining with their building specifics.2. An inspector/instructorin the Life Safety Bureau, Public Education Section - High-rise Fire SafetyPlan Approvals, may be obtained to provide training outside his regular workhours on an overtime basis. This may be done by contacting Diana Cardenas bye-mail at:diana.cardenas@houstontx.gov. This should be done prior to payment of arequired permit fee so that an instructor can be assigned to made contact withthe requesting party, to assist the requesting party with information on theapplication for over-time training and payment of the permit fees, and toschedule a mutually convenient training date.A City of Houston permit fee is required to schedule an inspector/instructor.The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019).3. Having a City of HoustonFire Marshal approved consultant perform the training. The process to receivean approved Fire Safety Plan consist of the three following essential trainingelements conducted by persons, institutions or companies approved by the FireMarshal according to regulations established by the Fire Marshal: aconsultation with building management, an approved certification training forFire Wardens and building employees, and a fire drill supervised by persons,institutions or companies approved by the Fire Marshal. | HighRise | LISA KIMBALL
65115 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS | HighRise | LISA KIMBALL
65116 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL SUBMIT ACOMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINEDFIRE WARDENS | HighRise | LISA KIMBALL
65117 | Concerningfire drills during COVID-19, a link can be found by going to the "Resources" andthen clicking on "Notices"https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/ | HighRise | LISA KIMBALL
65118 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
65119 | MEMBERS OF THE FIRESAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
65120 | NoData | HighRise | LISA KIMBALL
65135 | NoData | HighRise | LISA KIMBALL
65141 | NoData | HighRise | LISA KIMBALL
65144 | NoData | HighRise | LISA KIMBALL
65145 | NoData | HighRise | LISA KIMBALL
65203 | NoData | HighRise | LISA KIMBALL
65216 | NoData | HighRise | LISA KIMBALL
65220 | NoData | HighRise | LISA KIMBALL
65222 | NoData | HighRise | LISA KIMBALL
65225 | NoData | HighRise | LISA KIMBALL
65230 | NoData | HighRise | LISA KIMBALL
65266 | NoData | HighRise | LISA KIMBALL
65268 | NoData | HighRise | LISA KIMBALL
65276 | NoData | HighRise | LISA KIMBALL
65279 | NoData | HighRise | LISA KIMBALL
65286 | NoData | HighRise | LISA KIMBALL
65317 | CITATIONS WILL BEWRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT METWITHIN 30 DAYS | HighRise | LISA KIMBALL
65318 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30CALENDAR DAYS | HighRise | LISA KIMBALL
65319 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
65320 | NoData | HighRise | LISA KIMBALL
65321 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIREDIF THE HIGH-RISE DOES NOT HAVE ANY OF THESESYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED)DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30 CALENDAR DAYS | HighRise | LISA KIMBALL
65322 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
65323 | EVIDENCE OF INCOMPLETE ORNON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONINGSYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRECODE | HighRise | LISA KIMBALL
65324 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
65325 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
65326 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY AREPLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT ORSERVICE TO THE OWNER/OCCUPANT AND TO THE JURISDICTION – BY PHONE 713.884.3143AND EMAIL AT HFD.DISPATCH3@houstontx.gov THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THESYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
65327 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
65328 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
65329 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERAL ALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
65330 | Take the Fire Warden Certification class online through thefollowing link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottomto click on High-rise Fire Warden CertificationClass.Print out the certificate of completion and keep it in a safeplace where it can be accessed upon demand. REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Riseor Mid-Rise Atruim Certification Training may send attendees to the followingmonthly seminars at no cost. Monthly seminars are available for managementemployees and tenant fire wardens of high-rise buildings who need to becertified. Certificates shall be valid for a period of five years from the dateof training.There is no charge for attending theseseminars. The only cost incurred may be parking fees, if applicable. Manybuildings will have different fire safety features. The building managementfrom each building represented is required to inform its employees and FireWardens of their specific fire safety features to complete the certification. Please note this training is not valid forMid Rise Evacuation Training. For information on mid rise training please visitthe HFD Mid Rise Fire Certication Webpage.Additional training availability information:The Houston Fire Department has set up and implemented a list of all high-risebuildings for Fire Safety Plan approvals. This list was set up to ensure thatpriority is given to buildings that have the greatest need while also providingeach building an equal opportunity. The list of buildings is separated into twogroups based on whether the building is an occupancy where people sleep, suchas hotel, apartments, and condominiums or those buildings where people do notsleep, such as office buildings. Buildings are then sub-grouped by no sprinklersystem, partial sprinkler system, or complete sprinkler systems before sortingby building height. The highest priority building is the residential buildingthat is non-sprinklered, and the tallest in height. Our goal is to provide theneeded services to approve each building within a two-year cycle. Buildingsdesiring to expedite the process also have three additional options. 1. The monthly openhigh-rise certification seminar is for buildings that have requested to send alimited number of fire wardens and building management employees to a classthat is open to all high-rise buildings. The class information is not specificto any particular building and requires building management to supplement thetraining with their building specifics.2. An inspector/instructorin the Life Safety Bureau, Public Education Section - High-rise Fire SafetyPlan Approvals, may be obtained to provide training outside his regular workhours on an overtime basis. This may be done by contacting Diana Cardenas bye-mail at:diana.cardenas@houstontx.gov. This should be done prior to payment of arequired permit fee so that an instructor can be assigned to made contact withthe requesting party, to assist the requesting party with information on theapplication for over-time training and payment of the permit fees, and toschedule a mutually convenient training date.A City of Houston permit fee is required to schedule an inspector/instructor.The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019).3. Having a City of HoustonFire Marshal approved consultant perform the training. The process to receivean approved Fire Safety Plan consist of the three following essential trainingelements conducted by persons, institutions or companies approved by the FireMarshal according to regulations established by the Fire Marshal: aconsultation with building management, an approved certification training forFire Wardens and building employees, and a fire drill supervised by persons,institutions or companies approved by the Fire Marshal. | HighRise | LISA KIMBALL
65331 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS | HighRise | LISA KIMBALL
65332 | SUBMIT ACOMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINEDFIRE WARDENS HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
65333 | Concerningfire drills during COVID-19, a link can be found by going to the "Resources" andthen clicking on "Notices"https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/ | HighRise | LISA KIMBALL
65334 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
65335 | MEMBERS OF THEFIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
65336 | NoData | HighRise | LISA KIMBALL
65347 | PROVIDE EVIDENCE OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP THIS INFORMATION ON SITE PROVIDE DOCUMENTATION OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP POSTED ON SITE WITH ALL OTHER PERMITS, WITHIN THE ELEVATOR CAR OR WITHIN 10 FEET OF THE CALL BUTTONS | HighRise | LISA KIMBALL
65348 | HOUSEKEEPING IS REQUIRED IN THE 1ST FLOOR ELEVATOR/MECHANICAL ROOM | HighRise | LISA KIMBALL
65349 | SUPPLY THE CODE FOR ENTRY IN THE 911 BOX SPPLY A SIGN STATING "911 BOX 9@CORNER OF MAIN AND POLK) HAS CODE FOR ACCESS | HighRise | LISA KIMBALL
65350 | FIRE EXTINGUISHERS ARE REQUIRED IN ALL ELEVATOR ROOMS, ELECTRICAL ROOMS, IT ROOMS, GENERATOR ROOMS, MECHANICAL ROOMS AND WHERE FLAMMABLES ARE STORED PROVIDE FIRE EXTINGUISHERS IN THE EQUIPMENT ROOM (AT EACH DOOR) AND IN THE BREAK ROOM ON THE SECOND FLOOR | HighRise | LISA KIMBALL
65351 | PROVIDE COVERS MECHANICAL/ELECTRICAL ROOMS ON THE 1ST AND 2ND FLOORS FOR OPEN JUNCTION BOXES | HighRise | LISA KIMBALL
65352 | THE BACK EXIT DOORS WHICH ARE LOCATED IN THE LOADING DOCK MUST BE IDENTIFIED AND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS | HighRise | LISA KIMBALL
65353 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOST RECENT TEST EXIT SIGNS WERE FOUND OUT/NOT ILLUMINATED ON THE 2ND FLOOR NEAR THE MECHANICAL/ELECTRICAL ROOM - REPAIR OR REPLACE THEM IMMEDIATELY | HighRise | LISA KIMBALL
65354 | PROVIDE ADDITIONAL EXIT SIGNS ON THE WALL IN THE STAIRWELL ON THE GROUND FLOOR (LEAVING THE CLASS AREA) TO DETER OCCUPANTS FROM CONTINUING BACK TO THE STAIRS AND AWAY FROM THE ACTUAL EXIT | HighRise | LISA KIMBALL
65355 | NoData | HighRise | LISA KIMBALL
65356 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
65357 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
65358 | NoData | HighRise | LISA KIMBALL
65359 | PROVIDE A UL APPROVED RED CAN IN THE ELEVATOR ROOM AND ENSURE IT IS EMPTIED DAILY | HighRise | LISA KIMBALL
65360 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIRE A LETTER - PROVIDE A PHOTOCOPY OF THESE PERMITS. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - REQUIRED IF BOILER ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
65361 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED | HighRise | LISA KIMBALL
65362 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE MECHANICAL/ELECTRICAL ROOMS ON THE 1ST AND 2ND FLOORS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
65363 | NO 'PIGGYBACKING' OF MULTIPLE EXTENSION CORDS ALLOWED - USE ONLY ONE UL APPROVED, SURGE-PROTECTED EXTENSION CORD FROM THE WALL TO THE APPLIANCE OR APPLIANCES IN THE MASS CHALLENGE ROOM UNDER THE TABLE AND IN OFFICES NEARBY - | HighRise | LISA KIMBALL
65364 | PERMITS THE INSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS: Key Box Permit - Flammable and Combustible Permit - Fire Alarm Permit - Elevator Operating Permit - Boiler Permit - Other - Assembly, Access Gates, Batteries, etc. - Certificate of Occupancies - Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
65365 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
65366 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
65367 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
65368 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENT APPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
65369 | SUPPLY A LETTER INDICATING 1313 MAIN IS IN COMPLIANCE WITH APPENDIX J | HighRise | LISA KIMBALL
65370 | THE ELECTRICAL ROOM ON THE CLAY SIDE MUST BE IDENTIFIED AND LABELED AS SUCH | HighRise | LISA KIMBALL
65371 | PROVIDE SIGN ON THE DOOR OF THE EQUIPMENT ROOM (FROM THE GARAGE AND FROM THE TENANT SIDE) TO INDICATE THE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
65372 | SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
65373 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
65374 | NO CITY MAG LOCK STICKER WAS FOUND ON THE LOADING DOCK DOOR - ENSURE IT IS TESTED AND STICKERED EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE | HighRise | LISA KIMBALL
65375 | THE LOCATION OF THE ELEVATOR ROOM MUST BE IDENTIFIED AND LABELED AS SUCH ON THE DOOR AND ALL DOORS LEADING TO IT THE AIR HANDLER ROOM DOOR MUST ALSO STATE "MECHANICAL ROOM" AND "ELECTRICAL ROOM" | HighRise | LISA KIMBALL
65376 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRE CODE OFFICIAL IS DEPENDENT UPON SUCCESSFUL COMPLETION OF THREE COMPONENTS - CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF A SUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
65377 | EACH MEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
65378 | ATTENDANCE AT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH- RISE FIRE WARDENS | HighRise | LISA KIMBALL
65379 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
65380 | PROVIDE A KEY TO THE FIRE ALARM PANEL OF 1313 MAIN IN THE FIRE DEPOSITORY BOX AND BEHIND THE FRONT DESK; SUPPLY A LABEL INDICATING THE LOCATION OF THE KEYS ON THE FIRE ALARM PANEL | HighRise | LISA KIMBALL
65381 | SUBMIT A COMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS | HighRise | LISA KIMBALL
65382 | NoData | HighRise | LISA KIMBALL
65383 | MANICURE THE LANDSCAPING TO REVEAL THE HIDDEN HYDRANT ON MAIN STREET ENSURE LANDSCAPING DOES NOT OBSCURE FIRE DEPARTMENT ELEMENTS AND/OR FIRE HYDRANTS | HighRise | LISA KIMBALL
65384 | REMOVE AND DISCONTINUE USE OF UNAPPROVED EXTENSION CORD IN THE MASS CHALLENGE ROOM UNDER THE TABLE AND IN OFFICES NEARBY - ONLY UL APPROVED, SURGE PROTECTED CORDS ARE SAFE FOR TEMPORARY USE | HighRise | LISA KIMBALL
65385 | FDC SIGN MUST BE UPDATED - REVIEW LSB #2 SECTION 2.5.4.3 TO REVISE THE FDC SIGN WITH NECESSARY CORRECTIONS AND ENSURE ALL PERTINENT INFORMATION IS INCLUDED Approved signs of weather-resistant materials, with not less than one inch high legible block lettering on a highly contrasting background, shall be placed on or immediately adjacent to all fire department connections and provide the following information: 1. Type of system - STANDPIPE, SPRINKLER, STANDPIPE / SPRINKLER, DRY PIPE SPRINKLER, etc. 2. Which building or structure, or what portion, zone, and floors of the building or structure the FDC serve. i. Ex: FLOORS B1 - 12; LEVELS 1 - 8; HIGH ZONE FLRS 21 - 40; etc. 3. On standpipe and combination standpipe/sprinkler systems - whether there are pressure regulating valves (PRV) or pressure reducing devices (PRD) on the system. System pressures shall also be indicated on all wet standpipe and combination standpipe/sprinkler systems. Examples: NO PRV/PRD (System Pres. 100 PSI) PRD Levels 1 - 7 (System Pres. 150 PSI) PRV Floors 1 - 10 (System Pres. 175 PSI) | HighRise | LISA KIMBALL
65386 | THE LOCK-OUT/TAG-OUT EQUIPMENT AND SETS (SET = 1 LOCK + 1 TAG) MUST BE READILY ACCESSIBLE IN THE ELEVATOR ROOM AND PROPERLY LABELED: PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS | HighRise | LISA KIMBALL
65387 | NoData | HighRise | LISA KIMBALL
65388 | ALL OCCUPANTS OF THE BUILDING SHALL PARTICIPATE IN THE FIRE DRILLS AS REQUIRED BY THE CODE OFFICIAL AND THE FIRE CODE | HighRise | LISA KIMBALL
65389 | APPROVAL OF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFUL COMPLETION OF SEVERALALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF A COMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
65390 | REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Rise or Mid-Rise Atruim Certification Training may send attendees to the following monthly seminars at no cost. Monthly seminars are available for management employees and tenant fire wardens of high-rise buildings who need to be certified. Certificates shall be valid for a period of five years from the date of training. There is no charge for attending these seminars. The only cost incurred may be parking fees, if applicable. Many buildings will have different fire safety features. The building management from each building represented is required to inform its employees and Fire Wardens of their specific fire safety features to complete the certification. Please note this training is not valid for Mid Rise Evacuation Training. For information on mid-rise training please visit the HFD Mid Rise Fire Certification Webpage. Additional training availability information: The Houston Fire Department has set up and implemented a list of all high- rise buildings for Fire Safety Plan approvals. This list was set up to ensure that priority is given to buildings that have the greatest need while also providing each building an equal opportunity. The list of buildings is separated into two groups based on whether the building is an occupancy where people sleep, such as hotel, apartments, and condominiums or those buildings where people do not sleep, such as office buildings. Buildings are then sub- grouped by no sprinkler system, partial sprinkler system, or complete sprinkler systems before sorting by building height. The highest priority building is the residential building that is non-sprinklered, and the tallest in height. Our goal is to provide the needed services to approve each building within a two-year cycle. Buildings desiring to expedite the process also have three additional options. The monthly open high-rise certification seminar is for buildings that have requested to send a limited number of fire wardens and building management employees to a class that is open to all high-rise buildings. The class information is not specific to any particular building and requires building management to supplement the training with their building specifics. An inspector/instructor in the Life Safety Bureau, Public Education Section - High-rise Fire Safety Plan Approvals, may be obtained to provide training outside his regular work hours on an overtime basis. This may be done by contacting Diana Cardenas by e-mail at: diana.cardenas@houstontx.gov. This should be done prior to payment of a required permit fee so that an instructor can be assigned to made contact with the requesting party, to assist the requesting party with information on the application for over-time training and payment of the permit fees, and to schedule a mutually convenient training date. A City of Houston permit fee is required to schedule an inspector/instructor. The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019). Having a City of Houston Fire Marshal approved consultant perform the training. The process to receive an approved Fire Safety Plan consist of the three following essential training elements conducted by persons, institutions or companies approved by the Fire Marshal according to regulations established by the Fire Marshal: a consultation with building management, an approved certification training for Fire Wardens and building employees, and a fire drill supervised by persons, institutions or companies approved by the Fire Marshal. THE CERTIFICATE OF COMPLETION OF FIRE WARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
65391 | REMOVE ALL EVIDENCE OF INACTIVE/NON FUNCTIONING (TELEPHONE AND TELEPHONE BOX AT THE LOADING DOCK DOOR) OR REPAIR IT TO ENABLE A FULLY FUNCTIONAL SYSTEM | HighRise | LISA KIMBALL
65392 | NoData | HighRise | LISA KIMBALL
65393 | PROVIDE 2 ELEVATOR INDEPENDENT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX WHERE 24 HOUR SECURITY IS PROVIDED, INDEPENDANT SERVICE KEYS MAY BE KEPT SECURED AT THE SECURITY CONSOL AND MADE READILY AVAILABLE TO THE FIRE DEPARTMENT UPON REQUEST - A NOTE OR SIGN IN THE FCR REGUARDING THE ALTERNATE PLACEMENT IS SUGGESTED | HighRise | LISA KIMBALL
65394 | THE FIRE ALARM MUST BE TESTED, INSPECTED, TAGGED, MAINTAINED AND FULLY/PROPERLY FUNCTIONING - THE FIRE ALARM WAS YELLOW-TAGGED ON 06/18/19 CALL CERTIFIED TESTING COMPANY TO CONDUCT ANNUAL INSPECTION OF THE SYSTEM PROVIDE A KEY IN A CONVENIENT LOCATION FOR THE FIRE ALARM PANEL AND LABEL THE PANEL INDICATION THE LOCATION OF THE KEY | HighRise | LISA KIMBALL
65395 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
65400 | PROVIDE EVIDENCE OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP THIS INFORMATION ON SITE PROVIDE DOCUMENTATION OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP POSTED ON SITE WITH ALL OTHER PERMITS, WITHIN THE ELEVATOR CAR OR WITHIN 10 FEET OF THE CALL BUTTONS | HighRise | LISA KIMBALL
65401 | HOUSEKEEPING IS REQUIRED IN THE 1ST FLOOR ELEVATOR/MECHANICAL ROOM | HighRise | LISA KIMBALL
65402 | SUPPLY THE CODE FOR ENTRY IN THE 911 BOX SPPLY A SIGN STATING "911 BOX 9@CORNER OF MAIN AND POLK) HAS CODE FOR ACCESS | HighRise | LISA KIMBALL
65403 | FIRE EXTINGUISHERS ARE REQUIRED IN ALL ELEVATOR ROOMS, ELECTRICAL ROOMS, IT ROOMS, GENERATOR ROOMS, MECHANICAL ROOMS AND WHERE FLAMMABLES ARE STORED PROVIDE FIRE EXTINGUISHERS IN THE EQUIPMENT ROOM (AT EACH DOOR) AND IN THE BREAK ROOM ON THE SECOND FLOOR | HighRise | LISA KIMBALL
65404 | PROVIDE COVERS MECHANICAL/ELECTRICAL ROOMS ON THE 1ST AND 2ND FLOORS FOR OPEN JUNCTION BOXES | HighRise | LISA KIMBALL
65405 | THE BACK EXIT DOORS WHICH ARE LOCATED IN THE LOADING DOCK MUST BE IDENTIFIED AND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS | HighRise | LISA KIMBALL
65406 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOST RECENT TEST EXIT SIGNS WERE FOUND OUT/NOT ILLUMINATED ON THE 2ND FLOOR NEAR THE MECHANICAL/ELECTRICAL ROOM - REPAIR OR REPLACE THEM IMMEDIATELY | HighRise | LISA KIMBALL
65407 | PROVIDE ADDITIONAL EXIT SIGNS ON THE WALL IN THE STAIRWELL ON THE GROUND FLOOR (LEAVING THE CLASS AREA) TO DETER OCCUPANTS FROM CONTINUING BACK TO THE STAIRS AND AWAY FROM THE ACTUAL EXIT | HighRise | LISA KIMBALL
65408 | NoData | HighRise | LISA KIMBALL
65409 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
65410 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
65411 | NoData | HighRise | LISA KIMBALL
65412 | PROVIDE A UL APPROVED RED CAN IN THE ELEVATOR ROOM AND ENSURE IT IS EMPTIED DAILY | HighRise | LISA KIMBALL
65413 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIRE A LETTER - PROVIDE A PHOTOCOPY OF THESE PERMITS. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - REQUIRED IF BOILER ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
65414 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED | HighRise | LISA KIMBALL
65415 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE MECHANICAL/ELECTRICAL ROOMS ON THE 1ST AND 2ND FLOORS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
65416 | NO 'PIGGYBACKING' OF MULTIPLE EXTENSION CORDS ALLOWED - USE ONLY ONE UL APPROVED, SURGE-PROTECTED EXTENSION CORD FROM THE WALL TO THE APPLIANCE OR APPLIANCES IN THE MASS CHALLENGE ROOM UNDER THE TABLE AND IN OFFICES NEARBY - | HighRise | LISA KIMBALL
65417 | PERMITS THE INSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS: Key Box Permit - Flammable and Combustible Permit - Fire Alarm Permit - Elevator Operating Permit - Boiler Permit - Other - Assembly, Access Gates, Batteries, etc. - Certificate of Occupancies - Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
65418 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
65419 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
65420 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
65421 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENT APPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
65422 | SUPPLY A LETTER INDICATING 1313 MAIN IS IN COMPLIANCE WITH APPENDIX J | HighRise | LISA KIMBALL
65423 | THE ELECTRICAL ROOM ON THE CLAY SIDE MUST BE IDENTIFIED AND LABELED AS SUCH | HighRise | LISA KIMBALL
65424 | PROVIDE SIGN ON THE DOOR OF THE EQUIPMENT ROOM (FROM THE GARAGE AND FROM THE TENANT SIDE) TO INDICATE THE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
65425 | SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
65426 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
65427 | NO CITY MAG LOCK STICKER WAS FOUND ON THE LOADING DOCK DOOR - ENSURE IT IS TESTED AND STICKERED EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE | HighRise | LISA KIMBALL
65428 | THE LOCATION OF THE ELEVATOR ROOM MUST BE IDENTIFIED AND LABELED AS SUCH ON THE DOOR AND ALL DOORS LEADING TO IT THE AIR HANDLER ROOM DOOR MUST ALSO STATE "MECHANICAL ROOM" AND "ELECTRICAL ROOM" | HighRise | LISA KIMBALL
65429 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRE CODE OFFICIAL IS DEPENDENT UPON SUCCESSFUL COMPLETION OF THREE COMPONENTS - CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF A SUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
65430 | EACH MEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
65431 | ATTENDANCE AT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH- RISE FIRE WARDENS | HighRise | LISA KIMBALL
65432 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
65433 | PROVIDE A KEY TO THE FIRE ALARM PANEL OF 1313 MAIN IN THE FIRE DEPOSITORY BOX AND BEHIND THE FRONT DESK; SUPPLY A LABEL INDICATING THE LOCATION OF THE KEYS ON THE FIRE ALARM PANEL | HighRise | LISA KIMBALL
65434 | SUBMIT A COMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS | HighRise | LISA KIMBALL
65435 | NoData | HighRise | LISA KIMBALL
65436 | MANICURE THE LANDSCAPING TO REVEAL THE HIDDEN HYDRANT ON MAIN STREET ENSURE LANDSCAPING DOES NOT OBSCURE FIRE DEPARTMENT ELEMENTS AND/OR FIRE HYDRANTS | HighRise | LISA KIMBALL
65437 | REMOVE AND DISCONTINUE USE OF UNAPPROVED EXTENSION CORD IN THE MASS CHALLENGE ROOM UNDER THE TABLE AND IN OFFICES NEARBY - ONLY UL APPROVED, SURGE PROTECTED CORDS ARE SAFE FOR TEMPORARY USE | HighRise | LISA KIMBALL
65438 | FDC SIGN MUST BE UPDATED - REVIEW LSB #2 SECTION 2.5.4.3 TO REVISE THE FDC SIGN WITH NECESSARY CORRECTIONS AND ENSURE ALL PERTINENT INFORMATION IS INCLUDED Approved signs of weather-resistant materials, with not less than one inch high legible block lettering on a highly contrasting background, shall be placed on or immediately adjacent to all fire department connections and provide the following information: 1. Type of system - STANDPIPE, SPRINKLER, STANDPIPE / SPRINKLER, DRY PIPE SPRINKLER, etc. 2. Which building or structure, or what portion, zone, and floors of the building or structure the FDC serve. i. Ex: FLOORS B1 - 12; LEVELS 1 - 8; HIGH ZONE FLRS 21 - 40; etc. 3. On standpipe and combination standpipe/sprinkler systems - whether there are pressure regulating valves (PRV) or pressure reducing devices (PRD) on the system. System pressures shall also be indicated on all wet standpipe and combination standpipe/sprinkler systems. Examples: NO PRV/PRD (System Pres. 100 PSI) PRD Levels 1 - 7 (System Pres. 150 PSI) PRV Floors 1 - 10 (System Pres. 175 PSI) | HighRise | LISA KIMBALL
65439 | THE LOCK-OUT/TAG-OUT EQUIPMENT AND SETS (SET = 1 LOCK + 1 TAG) MUST BE READILY ACCESSIBLE IN THE ELEVATOR ROOM AND PROPERLY LABELED: PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS | HighRise | LISA KIMBALL
65440 | NoData | HighRise | LISA KIMBALL
65441 | ALL OCCUPANTS OF THE BUILDING SHALL PARTICIPATE IN THE FIRE DRILLS AS REQUIRED BY THE CODE OFFICIAL AND THE FIRE CODE | HighRise | LISA KIMBALL
65442 | APPROVAL OF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFUL COMPLETION OF SEVERALALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF A COMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
65443 | REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Rise or Mid-Rise Atruim Certification Training may send attendees to the following monthly seminars at no cost. Monthly seminars are available for management employees and tenant fire wardens of high-rise buildings who need to be certified. Certificates shall be valid for a period of five years from the date of training. There is no charge for attending these seminars. The only cost incurred may be parking fees, if applicable. Many buildings will have different fire safety features. The building management from each building represented is required to inform its employees and Fire Wardens of their specific fire safety features to complete the certification. Please note this training is not valid for Mid Rise Evacuation Training. For information on mid-rise training please visit the HFD Mid Rise Fire Certification Webpage. Additional training availability information: The Houston Fire Department has set up and implemented a list of all high- rise buildings for Fire Safety Plan approvals. This list was set up to ensure that priority is given to buildings that have the greatest need while also providing each building an equal opportunity. The list of buildings is separated into two groups based on whether the building is an occupancy where people sleep, such as hotel, apartments, and condominiums or those buildings where people do not sleep, such as office buildings. Buildings are then sub- grouped by no sprinkler system, partial sprinkler system, or complete sprinkler systems before sorting by building height. The highest priority building is the residential building that is non-sprinklered, and the tallest in height. Our goal is to provide the needed services to approve each building within a two-year cycle. Buildings desiring to expedite the process also have three additional options. The monthly open high-rise certification seminar is for buildings that have requested to send a limited number of fire wardens and building management employees to a class that is open to all high-rise buildings. The class information is not specific to any particular building and requires building management to supplement the training with their building specifics. An inspector/instructor in the Life Safety Bureau, Public Education Section - High-rise Fire Safety Plan Approvals, may be obtained to provide training outside his regular work hours on an overtime basis. This may be done by contacting Diana Cardenas by e-mail at: diana.cardenas@houstontx.gov. This should be done prior to payment of a required permit fee so that an instructor can be assigned to made contact with the requesting party, to assist the requesting party with information on the application for over-time training and payment of the permit fees, and to schedule a mutually convenient training date. A City of Houston permit fee is required to schedule an inspector/instructor. The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019). Having a City of Houston Fire Marshal approved consultant perform the training. The process to receive an approved Fire Safety Plan consist of the three following essential training elements conducted by persons, institutions or companies approved by the Fire Marshal according to regulations established by the Fire Marshal: a consultation with building management, an approved certification training for Fire Wardens and building employees, and a fire drill supervised by persons, institutions or companies approved by the Fire Marshal. THE CERTIFICATE OF COMPLETION OF FIRE WARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
65444 | REMOVE ALL EVIDENCE OF INACTIVE/NON FUNCTIONING (TELEPHONE AND TELEPHONE BOX AT THE LOADING DOCK DOOR) OR REPAIR IT TO ENABLE A FULLY FUNCTIONAL SYSTEM | HighRise | LISA KIMBALL
65445 | NoData | HighRise | LISA KIMBALL
65446 | PROVIDE 2 ELEVATOR INDEPENDENT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX WHERE 24 HOUR SECURITY IS PROVIDED, INDEPENDANT SERVICE KEYS MAY BE KEPT SECURED AT THE SECURITY CONSOL AND MADE READILY AVAILABLE TO THE FIRE DEPARTMENT UPON REQUEST - A NOTE OR SIGN IN THE FCR REGUARDING THE ALTERNATE PLACEMENT IS SUGGESTED | HighRise | LISA KIMBALL
65447 | THE FIRE ALARM MUST BE TESTED, INSPECTED, TAGGED, MAINTAINED AND FULLY/PROPERLY FUNCTIONING - THE FIRE ALARM WAS YELLOW-TAGGED ON 06/18/19 CALL CERTIFIED TESTING COMPANY TO CONDUCT ANNUAL INSPECTION OF THE SYSTEM PROVIDE A KEY IN A CONVENIENT LOCATION FOR THE FIRE ALARM PANEL AND LABEL THE PANEL INDICATION THE LOCATION OF THE KEY | HighRise | LISA KIMBALL
65448 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
65635 | NoData | HighRise | LISA KIMBALL
65640 | NoData | HighRise | LISA KIMBALL
65641 | NoData | HighRise | LISA KIMBALL
65643 | NoData | HighRise | LISA KIMBALL
65649 | NoData | HighRise | LISA KIMBALL
65669 | NoData | HighRise | LISA KIMBALL
65673 | NoData | HighRise | LISA KIMBALL
65687 | NoData | HighRise | LISA KIMBALL
65691 | NoData | HighRise | LISA KIMBALL
65706 | NoData | HighRise | LISA KIMBALL
65727 | NoData | HighRise | LISA KIMBALL
65736 | NoData | HighRise | LISA KIMBALL
65740 | NoData | HighRise | LISA KIMBALL
65751 | NoData | HighRise | LISA KIMBALL
65752 | NoData | HighRise | LISA KIMBALL
65754 | NoData | HighRise | LISA KIMBALL
65757 | NoData | HighRise | LISA KIMBALL
65759 | NoData | HighRise | LISA KIMBALL
65760 | NoData | HighRise | LISA KIMBALL
65761 | NoData | HighRise | LISA KIMBALL
65762 | NoData | HighRise | LISA KIMBALL
66857 | NoData | HighRise | LISA KIMBALL
67142 | THE ALARM SYSTEM IS RED TAGGED - RED TAG WAS ISSUED 12/31/2020 AND SYSTEM MUST BESERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
67143 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
67144 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
67145 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit - (K1) REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMFlammable and Combustible Permit - (F7) REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMFire Alarm Permit -REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMElevator Operating Permit -REQUIRED; TO BE POSTED IN THE ELEVATOR ROOM OR WITHIN 10FT OF THE ELEVATOR CALL BUTTONSBoiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancy -REQUIRED; TO BE POSTEDFire Depository Box Permit - (K1)REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMThese are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30CALENDAR DAYS | HighRise | LISA KIMBALL
67399 | NoData | HighRise | LISA KIMBALL
67400 | EMERGENCY EXIT ANDEGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOSTRECENT TEST EXIT SIGNS WERE FOUNDOUT/NOT ILLUMINATED ON THE FRONT DOOR AND IN THE HALLWAY -REPAIR OR REPLACE THEM IMMEDIATELY | HighRise | LISA KIMBALL
67401 | EMERGENCY EXIT ANDEGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOSTRECENT TEST BOTH EXIT SIGNS WERE FOUNDOUT/NOT ILLUMINATED -REPAIR OR REPLACE THEM IMMEDIATELY | HighRise | LISA KIMBALL
67402 | THE BACK EXIT DOOR MUST BE IDENTIFIEDAND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS | HighRise | LISA KIMBALL
67403 | ENSURE THAT A SMOKEDETECTOR IS PROVIDED IN THE HALLWAY WHERE THE MASSAGE ROOMS ARE LOCATED | HighRise | LISA KIMBALL
67404 | PROVIDE A SMOKE DETECTOR IN THE HALLWAY | HighRise | LISA KIMBALL
67405 | CONTACT A CERTIFIEDPLUMBER TO CONDUCT A GAS TEST IF GAS TEST WAS CONDUCTED MORE THAN FIVE YEARSAGO | HighRise | LISA KIMBALL
67406 | A PERMITAND A LICENSED PLUMBER MUST BE OBTAINED PRIOR TO CONDUCTING A GAS TEST -CONTACT THE HOUSTON PERMITTING CENTER 832.394.8811 FOR MORE INFORMATION | HighRise | LISA KIMBALL
67407 | CONTACT A CERTIFIEDPLUMBER TO CONDUCT A GAS TEST IF GAS TEST WAS CONDUCTED MORE THAN FIVE YEARSAGO PROVIDE EVIDENCE OFLAST GAS TEST AND KEEP DOCUMENTS/PROOF OF TESTING ON SITE AND READY FORINSPECTION AT ALL TIMES A PERMITAND A LICENSED PLUMBER MUST BE OBTAINED PRIOR TO CONDUCTING A GAS TEST -CONTACT THE HOUSTON PERMITTING CENTER 832.394.8811 FOR MORE INFORMATION | HighRise | LISA KIMBALL
67408 | PROVIDE AN EXIT SIGNON THE ROOM WHICH LEADS TO THE REAR EXIT AND ANOTHER ONE ON THE ACTUAL EXIT DOOR | HighRise | LISA KIMBALL
67409 | PROVIDE AN EXIT SIGNON THE ROOM WHICH LEADS TO THE REAR EXIT AND ON THE REAR EXIT DOOR | HighRise | LISA KIMBALL
67410 | THE CERTIFICATE OF OCCUPANCY AND ALLREQUIRED PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES | HighRise | LISA KIMBALL
67411 | OBTAIN CERTIFICATE OFOCCUPANCY FROM THE HOUSTON PERMITTING CENTER THE CERTIFICATE OF OCCUPANCY AND ALLREQUIRED PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES | HighRise | LISA KIMBALL
67412 | NoData | HighRise | LISA KIMBALL
67413 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THEPROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THEPREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEALALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURINGSUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIREDPRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THEFIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THATARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
67414 | A SIGN OR ADHESIVE STATING "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING ISOCCUPIED" MUST BE POSTED ON OR NEAR THE FRONT ENTRANCE DOOR AND THE ROOM TO THE REAR EXIT DOOR AND THE REAR EXIR DOOR ALL SECURITY GRILLSAND SECURITY GRILL DOORS SHALL REMAIN OPEN (AND SECURED AND LOCKED IN THE OPENPOSITION) WHILE THE BUSINESS IS OCCUPIED, OPEN AND OPERATING | HighRise | LISA KIMBALL
67415 | A SIGNOR ADHESIVE STATING "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED" MUST BEPOSTED ON OR NEAR THE FRONT ENTRANCE DOOR AND THE BACK EXIT DOOR THE SECURITY GATE ON THE EXTERIOR REAR EXIT MUST REMAIN UNLOCKED DURING BUSINESS HOURS | HighRise | LISA KIMBALL
67689 | NoData | HighRise | LISA KIMBALL
67690 | MEMBERS OF THE FIRESAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
67691 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR | HighRise | LISA KIMBALL
67692 | Concerningfire drills during COVID-19, a link can be found by going to the "Resources" andthen clicking on "Notices"https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/ | HighRise | LISA KIMBALL
67693 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL | HighRise | LISA KIMBALL
67694 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS | HighRise | LISA KIMBALL
67695 | Take the Fire Warden Certification class online through the following link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottom to click onHigh-rise Fire Warden Certification Class.Print out the certificate of completion and keep it in a safe place where it can be accessed upon demand. REGISTER FOR FIRE WARDEN TRAINING AThttps://houstontx.gov/fire/HFMO/highrisecert.htmlAny Building Manager in need of High-Riseor Mid-Rise Atruim Certification Training may send attendees to the followingmonthly seminars at no cost. Monthly seminars are available for managementemployees and tenant fire wardens of high-rise buildings who need to becertified. Certificates shall be valid for a period of five years from the dateof training.There is no charge for attending theseseminars. The only cost incurred may be parking fees, if applicable. Manybuildings will have different fire safety features. The building managementfrom each building represented is required to inform its employees and FireWardens of their specific fire safety features to complete the certification. Please note this training is not valid forMid Rise Evacuation Training. For information on mid rise training please visitthe HFD Mid Rise Fire Certication Webpage.Additional training availability information:The Houston Fire Department has set up and implemented a list of all high-risebuildings for Fire Safety Plan approvals. This list was set up to ensure thatpriority is given to buildings that have the greatest need while also providingeach building an equal opportunity. The list of buildings is separated into twogroups based on whether the building is an occupancy where people sleep, suchas hotel, apartments, and condominiums or those buildings where people do notsleep, such as office buildings. Buildings are then sub-grouped by no sprinklersystem, partial sprinkler system, or complete sprinkler systems before sortingby building height. The highest priority building is the residential buildingthat is non-sprinklered, and the tallest in height. Our goal is to provide theneeded services to approve each building within a two-year cycle. Buildingsdesiring to expedite the process also have three additional options. 1. The monthly openhigh-rise certification seminar is for buildings that have requested to send alimited number of fire wardens and building management employees to a classthat is open to all high-rise buildings. The class information is not specificto any particular building and requires building management to supplement thetraining with their building specifics.2. An inspector/instructorin the Life Safety Bureau, Public Education Section - High-rise Fire SafetyPlan Approvals, may be obtained to provide training outside his regular workhours on an overtime basis. This may be done by contacting Diana Cardenas bye-mail at:diana.cardenas@houstontx.gov. This should be done prior to payment of arequired permit fee so that an instructor can be assigned to made contact withthe requesting party, to assist the requesting party with information on theapplication for over-time training and payment of the permit fees, and toschedule a mutually convenient training date.A City of Houston permit fee is required to schedule an inspector/instructor.The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019).3. Having a City of HoustonFire Marshal approved consultant perform the training. The process to receivean approved Fire Safety Plan consist of the three following essential trainingelements conducted by persons, institutions or companies approved by the FireMarshal according to regulations established by the Fire Marshal: aconsultation with building management, an approved certification training forFire Wardens and building employees, and a fire drill supervised by persons,institutions or companies approved by the Fire Marshal. | HighRise | LISA KIMBALL
67696 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERAL ALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1 | HighRise | LISA KIMBALL
67697 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE | HighRise | LISA KIMBALL
67698 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN | HighRise | LISA KIMBALL
67699 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIREPROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY ORNON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEMIS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
67700 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
67701 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
67702 | EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE | HighRise | LISA KIMBALL
67703 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
67704 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIREDIF THE HIGH-RISE DOES NOT HAVE ANY OF THESESYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED)DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30 CALENDAR DAYS | HighRise | LISA KIMBALL
67705 | NoData | HighRise | LISA KIMBALL
67706 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
67707 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30 CALENDARDAYS | HighRise | LISA KIMBALL
67708 | CITATIONS WILL BE WRITTEN AFTER 2REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT METWITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
67762 | NoData | HighRise | LISA KIMBALL
67829 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRESUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALSAND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ONSITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
67830 | WHERE LOCAL FIRE MARSHAL APPROVALS AREREQUIRED BY REGULATORY AGENCIES, APPROVED FIRE SAFETY AND EVACUATION PLANSSHALL BE PREPARED, MAINTAINED AND POSTED IN GROUP E OCCUPANCIES | HighRise | LISA KIMBALL
67831 | NoData | HighRise | LISA KIMBALL
67832 | INFORMATION TO BE INCLUDED IN FIRE EVACUATIONPLANS | HighRise | LISA KIMBALL
67833 | POST ADDRESS CONSPICUOUSLY - THE LOCATION MUST HAVE A NUMERICAL ADDRESS WHICH IS CLEARLY VISIBLE FROM THE STREET | HighRise | LISA KIMBALL
67834 | THE CERTIFICATE OF OCCUPANCY AND ALLREQUIRED PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES | HighRise | LISA KIMBALL
67835 | MISSING ILLUMINATED EMERGENCY EXIT SIGNS MUST BE INSTALLED AND TESTED | HighRise | LISA KIMBALL
67836 | INFORMATION TO BE INCLUDED IN FIRE SAFETYPLANS | HighRise | LISA KIMBALL
67837 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
67838 | OBTAIN A CERTIFICATE OF OCCUPANCY AND ANY OTHER PERMITS REQUIRED PER THE CODE | HighRise | LISA KIMBALL
67839 | NoData | HighRise | LISA KIMBALL
67840 | REMOVE DEADBOLT (PLAYGROUND EXIT) AND LOCKING DOOR HANDLE (FRONT ENTRY/EXIT) WHICH ARE BEING USED IN CONJUNCTION WITH PANIC HARDWARE | HighRise | LISA KIMBALL
67854 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY -PROVIDE EVIDENCE OF MOST RECENT TEST AND ENSURE ALL EXIT LIGHTS AND EMERGENCY LIGHTS/EYEBALLS ARE ILLUMINATING/FUNCTIONING - THE EXIT LIGHT AT THE FRONT ENTRANCE IS NOT ILLUMINATING | HighRise | LISA KIMBALL
67855 | ALL HOODVENTS AND HOOD SUPPRESSION SYSTEMS MUST BE INSPECTED AND SERVICED AT LEASTEVERY 6 MONTHS - PROVIDE PROOF OF LAST INSPECTION AND CLEANING | HighRise | LISA KIMBALL
67856 | THE CERTIFICATE OFOCCUPANCY AND FIRE ALARM PERMIT MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES - POST THE MOST RECENT FIRE PERMIT | HighRise | LISA KIMBALL
67857 | FIRE ALARM PANEL IS BLUE TAGGED 10FEB20 AND LAST SENSITIVITY TEST CONDUCTED 1JUN26FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - AUG2020 EMERGENCY ESCAPE MAPS ARE ALL POSTED IN PLACE IN EACH CLASSROOM ALL FIRE DRILLS CONDUCTED MONTHLYANSUL SYSTEM IS BLUE TAGGED AUG2020 | HighRise | LISA KIMBALL
67874 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
67875 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - RECIEVED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - RECIEVED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - RECIEVED " Electronic Locks -Semi Annual - RECIEVED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - RECIEVED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - RECIEVED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - RECIEVED " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - RECIEVED " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
67876 | CABINETS CONTAINING FIRE FIGHTING EQUIPMENT MUST INDICATE THE EQUIPMENT CONTAINED THEREIN - "FIRE HOSE" AND/OR "FIRE EXTINGUISHER" - CORRECTLY IDENTIFY CONTENTS OF CABINET ON THE 3RD FLOOR | HighRise | LISA KIMBALL
67877 | RECEIVED; NO FURTHER ACTION NECESSARY | HighRise | LISA KIMBALL
67878 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
67879 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
67880 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
67881 | THE MOBILITY IMPAIRED LIST MUST BE UPDATED EVERY 6 MONTHS | HighRise | LISA KIMBALL
67882 | PROVIDE 2 ELEVATOR INDEPENDANT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX | HighRise | LISA KIMBALL
67883 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
67884 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
67885 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
67886 | THE EXIT DOOR ON THE 14TH FLOOR STAIR B DOES NOT LATCH CLOSED | HighRise | LISA KIMBALL
67887 | ALL ELECTRICAL ROOMS, HVAC ROOMS, MECHANICAL ROOMS, IT ROOMS, ELEVATOR ROOMS, FIRE SPRINKLER RISER ROOMS, FIRE ALARM ROOMS AND TRANSFORMER ROOMS MUST BE LABELED AS SUCH FOR READY IDENTIFICATION - ID THE "PIT" AND ELEVATOR ROOM ON THE 10TH FLOOR, ID THE MECHANICAL ROOM ON THE 3RD FLOOR, ID THE MECHANICAL ROOM ALSO AS "DRY PIPE" ON THE 3RD FLOOR AND ACCESS TO THE GARAGE ELEVATORS THROUGH SUITE 620 | HighRise | LISA KIMBALL
67888 | PROVIDE DOCUMENTATION OR LETTER TO ENSURE ALL FIREPHONES AND JACKS (IN THE BUILDING ON ALL FLOORS) HAVE BEEN TESTED BY AN APPROVED, CERTIFIED FIRE PROTECTION COMPANY AND FUNCTIONING PROPERLY FIREFIGHTER PHONES AND ALL JACKS IN THE BUILDING MUST BE TESTED ANNUALLY | HighRise | LISA KIMBALL
67889 | ADD FOBS FOR ENTRY TO ALL 5 SETS OF KEYS IN THE FDB WRITE CODE FOR ENTRY TO PUMP ROOM ON KEY TAG TO PUMP ROOM (ON ALL 5 SETS) READ AND REVIEW LSB STANDARD 6; FULL COMPLIANCE OF PROVIDING A PROPERLY SUPPLIED FIRE DEPOSITORY BOX IS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
67890 | PERTAINING TO PLACEMENT AND DISTANCE OF FIRE EXTINGUISHERS NEEDED THROUGHOUT THE PARKING GARAGE ENSURE THAT ENOUGH FIRE EXTINGUISHERS ARE SUPPLIED, OBVIOUS AND ACCESSIBLE IN THE PARKING GARAGE (AN S-2) NO FIRE EXTINGUISHERS WERE FOUND IN THE PARKING GARAGE - SUPPLY FIRE EXTINGUISHERS ON ALL LEVELS IN DISTANCES PRESCRIBED BY THE FIRE CODE | HighRise | LISA KIMBALL
67891 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
67892 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
67893 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
67894 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
67895 | DOOR CLOSER FOUND ON THE 14TH FLOOR (STAIR B) IS NOT WORKING PROPERLY - ENSURE DOORS ARE LATCHING SHUT ON ALL EXIT STAIRWELL DOORS | HighRise | LISA KIMBALL
67896 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
67897 | PROVIDE SIGN ON THE DOOR OF THE PRESSURE WASHING CAGE IN THE GARAGE TO INDICATE THE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
67898 | THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH - IDENTIFY ACCESS TO THE ELECTRICAL ROOM THROUGH SUITE 350 | HighRise | LISA KIMBALL
67899 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
67900 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
67901 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
67902 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
67903 | OBTAIN ALL REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER - F7 (FLAMMABLE LIQUIDS PERMIT) AND K1 (KEY BOX PERMIT) ARE DUE THE ALARM PERMIT COULD NOT BE LOCATED IN OUR SYSTEM VIA MY SEARCH - PLEASE VISIT THE HOUSTON PERMITTING CENTER AND OBTAIN THE FIRE ALARM PERMIT | HighRise | LISA KIMBALL
67904 | THE EXIT DOOR ON THE 14TH FLOOR STAIR B IS STICKING - ENSURE ALL EXIT DOORS ARE CAPABLE OF OPENING WITH EASE | HighRise | LISA KIMBALL
67905 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE ELEVATOR ROOM ON THE GROUND FLOOR IN JOE'S OFFICE & THE ELCTRICAL ROOM, ON THE 6TH FLOOR, MECHANICAL ROOMS ON THE 12TH & 13TH FLOORS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
67906 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
67907 | ENSURE THE EMERGENCY "RE-ENTRY" BUTTON ON THE FIRE ALARM PANEL IS HIGHLIGHTED OR CONSPICUOUSLY LABELED | HighRise | LISA KIMBALL
67908 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
67909 | NoData | HighRise | LISA KIMBALL
67910 | THE BACK EXIT DOOR AND ABOVE ACCESS GATE CONTROL TO SUITE 700 SHOULD BE LABELED "SUITE 700 ACCESS GATE CONTROL" | HighRise | LISA KIMBALL
67911 | PROVIDE A COVER PLATE FOR EXPOSED ELECTRICAL OUTLET BEHIND THE UPS BOX ON THE GROUND FLOOR | HighRise | LISA KIMBALL
67912 | ALL FIRE DETECTION AND FIRE SUPPRESSION ELEMENTS MUST BE FULLY FUNCTIONAL AND BLUE TAGGED | HighRise | LISA KIMBALL
67913 | INSPECT ALL FIRE DETECTION AND FIRE SUPPRESSION EQUIPMENT TO ENSURE FUNCTIONALITY | HighRise | LISA KIMBALL
67914 | THE FIRE ALARM IS RED TAGGED DUE TO A SPRINKLER ACCIDENT ON THE 2ND FLOOR; ENSURE ALL FIRE DETECTION EQUIPMENT (WIRING, CONNECTIONS, DETECTORS, PANELS, ETC) WHICH WAS EXPOSED TO WATER IS NOT DAMAGED OR REPLACED IF DAMAGED. | HighRise | LISA KIMBALL
67915 | NOTIFICATIONMUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OFSERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT OR SERVICE TO THEOWNER/OCCUPANT AND TO THE JURISDICTION – BY PHONE 713.884.3143 AND EMAIL AT HFD.DISPATCH3@houstontx.govTHE FIREDEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMALOPERATIONAL STATUS | HighRise | LISA KIMBALL
67916 | POST CERTIFICATE OF OCCUPANCY CONSPICUOUSLY ON SITE | HighRise | LISA KIMBALL
67921 | THE ALARM SYSTEM IS RED TAGGED - RED TAG WAS ISSUED 12/31/2020 AND SYSTEM MUST BESERVICED OR REPAIRED IMMEDIATELY | HighRise | LISA KIMBALL
67922 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
67923 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
67924 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit - (K1) REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMFlammable and Combustible Permit - (F7) REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMFire Alarm Permit -REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMElevator Operating Permit -REQUIRED; TO BE POSTED IN THE ELEVATOR ROOM OR WITHIN 10FT OF THE ELEVATOR CALL BUTTONSBoiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancy -REQUIRED; TO BE POSTEDFire Depository Box Permit - (K1)REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMThese are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30CALENDAR DAYS | HighRise | LISA KIMBALL
68495 | PROVIDE SIGN ON THE DOOR OF THE PRESSURE WASHING CAGE IN THE GARAGE TO INDICATE THE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
68496 | ADD FOBS FOR ENTRY TO ALL 5 SETS OF KEYS IN THE FDB WRITE CODE FOR ENTRY TO PUMP ROOM ON KEY TAG TO PUMP ROOM (ON ALL 5 SETS) READ AND REVIEW LSB STANDARD 6; FULL COMPLIANCE OF PROVIDING A PROPERLY SUPPLIED FIRE DEPOSITORY BOX IS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
68497 | THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH - IDENTIFY ACCESS TO THE ELECTRICAL ROOM THROUGH SUITE 350 | HighRise | LISA KIMBALL
68498 | THE EXIT DOOR ON THE 14TH FLOOR STAIR B DOES NOT LATCH CLOSED | HighRise | LISA KIMBALL
68499 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - RECIEVED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - RECIEVED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - RECIEVED " Electronic Locks -Semi Annual - RECIEVED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - RECIEVED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - RECIEVED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - RECIEVED " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - RECIEVED " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS | HighRise | LISA KIMBALL
68500 | RECEIVED; NO FURTHER ACTION NECESSARY | HighRise | LISA KIMBALL
68501 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE | HighRise | LISA KIMBALL
68502 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
68503 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
68504 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
68505 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
68507 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
68508 | PROVIDE 2 ELEVATOR INDEPENDANT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX | HighRise | LISA KIMBALL
68509 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
68510 | CABINETS CONTAINING FIRE FIGHTING EQUIPMENT MUST INDICATE THE EQUIPMENT CONTAINED THEREIN - "FIRE HOSE" AND/OR "FIRE EXTINGUISHER" - CORRECTLY IDENTIFY CONTENTS OF CABINET ON THE 3RD FLOOR | HighRise | LISA KIMBALL
68511 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
68512 | ALL ELECTRICAL ROOMS, HVAC ROOMS, MECHANICAL ROOMS, IT ROOMS, ELEVATOR ROOMS, FIRE SPRINKLER RISER ROOMS, FIRE ALARM ROOMS AND TRANSFORMER ROOMS MUST BE LABELED AS SUCH FOR READY IDENTIFICATION - ID THE "PIT" AND ELEVATOR ROOM ON THE 10TH FLOOR, ID THE MECHANICAL ROOM ON THE 3RD FLOOR, ID THE MECHANICAL ROOM ALSO AS "DRY PIPE" ON THE 3RD FLOOR AND ACCESS TO THE GARAGE ELEVATORS THROUGH SUITE 620 | HighRise | LISA KIMBALL
68513 | PROVIDE DOCUMENTATION OR LETTER TO ENSURE ALL FIREPHONES AND JACKS (IN THE BUILDING ON ALL FLOORS) HAVE BEEN TESTED BY AN APPROVED, CERTIFIED FIRE PROTECTION COMPANY AND FUNCTIONING PROPERLY FIREFIGHTER PHONES AND ALL JACKS IN THE BUILDING MUST BE TESTED ANNUALLY | HighRise | LISA KIMBALL
68514 | PERTAINING TO PLACEMENT AND DISTANCE OF FIRE EXTINGUISHERS NEEDED THROUGHOUT THE PARKING GARAGE ENSURE THAT ENOUGH FIRE EXTINGUISHERS ARE SUPPLIED, OBVIOUS AND ACCESSIBLE IN THE PARKING GARAGE (AN S-2) NO FIRE EXTINGUISHERS WERE FOUND IN THE PARKING GARAGE - SUPPLY FIRE EXTINGUISHERS ON ALL LEVELS IN DISTANCES PRESCRIBED BY THE FIRE CODE | HighRise | LISA KIMBALL
68515 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS | HighRise | LISA KIMBALL
68516 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
68517 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
68518 | DOOR CLOSER FOUND ON THE 14TH FLOOR (STAIR B) IS NOT WORKING PROPERLY - ENSURE DOORS ARE LATCHING SHUT ON ALL EXIT STAIRWELL DOORS | HighRise | LISA KIMBALL
68519 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
68520 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE | HighRise | LISA KIMBALL
68521 | THE MOBILITY IMPAIRED LIST MUST BE UPDATED EVERY 6 MONTHS | HighRise | LISA KIMBALL
68522 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE | HighRise | LISA KIMBALL
68523 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
68524 | OBTAIN ALL REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER - F7 (FLAMMABLE LIQUIDS PERMIT) AND K1 (KEY BOX PERMIT) ARE DUE THE ALARM PERMIT COULD NOT BE LOCATED IN OUR SYSTEM VIA MY SEARCH - PLEASE VISIT THE HOUSTON PERMITTING CENTER AND OBTAIN THE FIRE ALARM PERMIT | HighRise | LISA KIMBALL
68525 | THE EXIT DOOR ON THE 14TH FLOOR STAIR B IS STICKING - ENSURE ALL EXIT DOORS ARE CAPABLE OF OPENING WITH EASE | HighRise | LISA KIMBALL
68526 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE ELEVATOR ROOM ON THE GROUND FLOOR IN JOE'S OFFICE & THE ELCTRICAL ROOM, ON THE 6TH FLOOR, MECHANICAL ROOMS ON THE 12TH & 13TH FLOORS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
68527 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE) | HighRise | LISA KIMBALL
68528 | ENSURE THE EMERGENCY "RE-ENTRY" BUTTON ON THE FIRE ALARM PANEL IS HIGHLIGHTED OR CONSPICUOUSLY LABELED | HighRise | LISA KIMBALL
68529 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY | HighRise | LISA KIMBALL
68530 | NoData | HighRise | LISA KIMBALL
68531 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL | HighRise | LISA KIMBALL
68532 | THE BACK EXIT DOOR AND ABOVE ACCESS GATE CONTROL TO SUITE 700 SHOULD BE LABELED "SUITE 700 ACCESS GATE CONTROL" | HighRise | LISA KIMBALL
68533 | PROVIDE A COVER PLATE FOR EXPOSED ELECTRICAL OUTLET BEHIND THE UPS BOX ON THE GROUND FLOOR | HighRise | LISA KIMBALL
69302 | ALL EMERGENCY EQUIPMENT IS INSPECTED PER ESTABLISHED INTERVALSAND DOCUMENTED - ALL DOCUMENTATION IS POSTED OR ORGANIZED AND KEPT ONSITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
69303 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
69304 | NO VIOLATIONS FOUND CERTIFICATE OF OCCUPANCY POSTED (45 OCCUPANTS) ALL EMERGENCY LIGHTS AND EXIT LIGHTS INSPECTED AND PASSED FEBRUARY 2020 ALL FIRE EXTINGUISHERS TAGGED JANUARY 2021 | HighRise | LISA KIMBALL
70039 | BLUE TAG ON FIRE ALARM DATED 1/20/21; LAST SENSITIVITY TEST N/A - SYSTEM IS SELF TESTING FIRE ALARM PERMIT HFD20036891 IS CURRENT LAST GAS TEST CONDUCTED 11/20/20 CERTIFICATE OF OCCUPANCY IS POSTED - 155 TOTAL FIRE EXTINGUISHERS TAGGED JUNE 2020 EXIT LIGHTS LAST CHECKED AND ALL OPERABLE IN JANUARY 2021 | HighRise | LISA KIMBALL
70040 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
70468 | THE FIREALARM PERMIT WAS ISSUED 2/11/19 AND IS EXPIRED; THIS PERMIT MUST BE RENEWED ANNUALLY | HighRise | LISA KIMBALL
70471 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN ALL LIGHT FIXTURES IN CHILD CARE AREAS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR | HighRise | LISA KIMBALL
70472 | ALL EMERGENCY EXIT SIGNS ARE ILLUMINATED, TESTED AND WORKING THERE IS A STRONG SMELL OF SEWAGE AND SOILED CARPET AT THE ENTRANCE OF THE BUILDING; IT APPEARS RAW SEWAGE IS COMIING IN FROM THE RESTAURANT NEXT DOOR; INVESTIGATE PROBLEM WITH THE OWNER OF THE STRIP CENTER AND ENSURE THIS PROBLEM IS CORRECTED IMMEDIATELY | HighRise | LISA KIMBALL
70473 | THE ALARM SYSTEM IS BLUE TAGGED - TAGS WAS ISSUED 1/23/20 (PAST DUE FOR INSPECTION) AND SYSTEM MUST BE INSPECTED IMMEDIATELY | HighRise | LISA KIMBALL
70474 | FIRE DRILLS MUST BE CONDUCTED MONTHLY | HighRise | LISA KIMBALL
70475 | PROVIDE EVIDENCE OF MONTHLY FIRE DRILLS – KEEP THESE RECORDS ON SITE FOR ATLEAST 3 YEARS ENSURE FIRE DRILLS ARECONDUCTED MONTHLY, WITHOUT FAIL | HighRise | LISA KIMBALL
70476 | NoData | HighRise | LISA KIMBALL
70477 | THE FIRE EXTINGUISHERS ARE TAGGED/INSPECTED NOVEMBER 2019 AND ARE ALL PAT DUE - INSPECT AND TAG ALL EXTINGUISHERS IMMEDIATELY | HighRise | LISA KIMBALL
70478 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THEPROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THEPREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEALALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURINGSUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIREDPRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THEFIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THATARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
70479 | THE CERTIFICATE OF OCCUPANCY AND ALLREQUIRED PERMITS ARE POSTED CONSPICUOUSLY | HighRise | LISA KIMBALL
71477 | NoData | HighRise | LISA KIMBALL
71693 | NoData | HighRise | LISA KIMBALL
72539 | CERTIFICATE OF OCCUPANCY IS VISIBLY POSTED ON SITE EMERGENCY EGRESS AND EXIT LIGHTS OPERATIONAL - TESTED OCT 2020 P2 PERMIT POSTED - EXPIRES 5/9/21 FIRE ALARM PERMIT IS POSTED ON SITE - VALID UNTIL 11/17/21 FIRE ALARM PANEL IS BLUE TAGGED - 10/09/20 FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - OCT 2020 EMERGENCY ESCAPE MAPS ARE ALL POSTED IN PLACE IN EACH CLASSROOM K EXTINGUISHER BLUE TAGGED AND INSPECTED OCT 2020 ANSUL SYSTEM IS BLUE TAGGED - OCT 2020 GAS TEST CONDUCTED AND PASSED 1/8/20 | HighRise | LISA KIMBALL
72540 | CERTIFICATE OF OCCUPANCY IS VISIBLY POSTED ON SITE EMERGENCY EGRESS AND EXIT LIGHTS OPERATIONAL - TESTED OCT 2020 P2 PERMIT POSTED - EXPIRES 5/9/21 FIRE ALARM PERMIT IS POSTED ON SITE - VALID UNTIL 11/17/21 FIRE ALARM PANEL IS BLUE TAGGED - 10/09/20 FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - OCT 2020 EMERGENCY ESCAPE MAPS ARE ALL POSTED IN PLACE IN EACH CLASSROOM K EXTINGUISHER BLUE TAGGED AND INSPECTED OCT 2020 ANSUL SYSTEM IS BLUE TAGGED - OCT 2020 GAS TEST CONDUCTED AND PASSED 1/8/20 | HighRise | LISA KIMBALL
72541 | VENT HOODS MUST BE CLEANED AT TIMELY INTERVALS - ALL CLEANINGS MUST BE RECORDED AND DOCUMENTS KEPT ON SITE | HighRise | LISA KIMBALL
72542 | VENT HOODS MUST BE CLEANED AT TIMELY INTERVALS - ALL CLEANINGS MUST BE RECORDED AND DOCUMENTS KEPT ON SITE | HighRise | LISA KIMBALL
72543 | FIRE DRILLS MUST BE CONDUCTED MONTHLY IN COMPLIANCE WITH MONTHLY FIRE DRILLS - LAST CONDUCTED 01/2020; THE BUILDING HAS ONLY EMPLOYEES AND NO STUDENTS AFTER THIS DATE DUE TO COVID-19 RESTRICTIONS IT IS SUGGESTED THAT MONTHLY FIRE DRILLS RESUME (TO PREPARE FOR THE RETURN OF STUDENTS) AND TO CONTINUE THE PRACTICE - PRACTICE MAKES PERFECT! | HighRise | LISA KIMBALL
72544 | FIRE DRILLS MUST BE CONDUCTED MONTHLY IN COMPLIANCE WITH MONTHLY FIRE DRILLS - LAST CONDUCTED 01/2020; THE BUILDING HAS ONLY EMPLOYEES AND NO STUDENTS AFTER THIS DATE DUE TO COVID-19 RESTRICTIONS IT IS SUGGESTED THAT MONTHLY FIRE DRILLS RESUME (TO PREPARE FOR THE RETURN OF STUDENTS) AND TO CONTINUE THE PRACTICE - PRACTICE MAKES PERFECT! | HighRise | LISA KIMBALL
72545 | NoData | HighRise | LISA KIMBALL
72546 | NoData | HighRise | LISA KIMBALL
72547 | PROVIDEEVIDENCE OF MONTHLY FIRE DRILLS – KEEP THESE RECORDS ON SITE FOR AT LEAST 3YEARS ENSURE FIRE DRILLS ARE CONDUCTED MONTHLY, WITHOUTFAIL | HighRise | LISA KIMBALL
72548 | PROVIDEEVIDENCE OF MONTHLY FIRE DRILLS – KEEP THESE RECORDS ON SITE FOR AT LEAST 3YEARS ENSURE FIRE DRILLS ARE CONDUCTED MONTHLY, WITHOUTFAIL | HighRise | LISA KIMBALL
72549 | VENT HOODS MUST BECLEANED AT TIMELY INTERVALS - ALL CLEANINGS MUST BE RECORDED AND DOCUMENTS KEPTON SITE | HighRise | LISA KIMBALL
72550 | VENT HOODS MUST BECLEANED AT TIMELY INTERVALS - ALL CLEANINGS MUST BE RECORDED AND DOCUMENTS KEPTON SITE | HighRise | LISA KIMBALL
72551 | NoData | HighRise | LISA KIMBALL
72552 | NoData | HighRise | LISA KIMBALL
72553 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
72554 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
72555 | NoData | HighRise | LISA KIMBALL
72556 | NoData | HighRise | LISA KIMBALL
72557 | CITATIONS WILL BE ISSUED IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
72558 | CITATIONS WILL BE ISSUED IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 30 DAYS | HighRise | LISA KIMBALL
72801 | NoData | HighRise | LISA KIMBALL
73591 | NoData | HighRise | LISA KIMBALL
73674 | NoData | HighRise | LISA KIMBALL
74009 | NoData | HighRise | LISA KIMBALL
74180 | SEVERAL REMINDERS AND EXTRA TIME ALLOWED TO PAY FOR b1 PERMIT; STILL REMAINS UNPAID. ADD RE-INSPECTION FEE AND MUST BE PAID IN 10 DAYS | HighRise | LISA KIMBALL
74306 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRESUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALSAND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ONSITE FOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
74307 | WHERE LOCAL FIRE MARSHAL APPROVALS AREREQUIRED BY REGULATORY AGENCIES, APPROVED FIRE SAFETY AND EVACUATION PLANSSHALL BE PREPARED, MAINTAINED AND POSTED IN GROUP E OCCUPANCIES | HighRise | LISA KIMBALL
74308 | NoData | HighRise | LISA KIMBALL
74309 | INFORMATION TO BE INCLUDED IN FIRE EVACUATIONPLANS | HighRise | LISA KIMBALL
74310 | POST ADDRESS CONSPICUOUSLY - THE LOCATION MUST HAVE A NUMERICAL ADDRESS WHICH IS CLEARLY VISIBLE FROM THE STREET | HighRise | LISA KIMBALL
74311 | THE CERTIFICATE OF OCCUPANCY AND ALLREQUIRED PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES | HighRise | LISA KIMBALL
74312 | MISSING ILLUMINATED EMERGENCY EXIT SIGNS MUST BE INSTALLED AND TESTED | HighRise | LISA KIMBALL
74313 | INFORMATION TO BE INCLUDED IN FIRE SAFETYPLANS | HighRise | LISA KIMBALL
74314 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
74315 | OBTAIN A CERTIFICATE OF OCCUPANCY AND ANY OTHER PERMITS REQUIRED PER THE CODE | HighRise | LISA KIMBALL
74316 | NoData | HighRise | LISA KIMBALL
74317 | NoData | HighRise | LISA KIMBALL
74318 | FAILURE TO FOLLOW UP ON CORRECTING VIOLATIONS | HighRise | LISA KIMBALL
74319 | REMOVE DEADBOLT (PLAYGROUND EXIT) AND LOCKING DOOR HANDLE (FRONT ENTRY/EXIT) WHICH ARE BEING USED IN CONJUNCTION WITH PANIC HARDWARE | HighRise | LISA KIMBALL
74322 | NoData | HighRise | LISA KIMBALL
75104 | NoData | HighRise | LISA KIMBALL
75129 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSIONEQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS ANDDOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITEFOR FIRE MARSHAL INSPECTION | HighRise | LISA KIMBALL
75130 | THE SPRINKLER SYSTEM IS RED TAGGED - A RED TAG WAS ISSUED IN 02/17/21 AND MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY REPAIRS ARE INDICATED ON THE FIRE ALARM BUT THE FIRE ALARM PANEL READS "OFF - NORMAL" AND THE SUPERVISORY LIGHT IS ILLUMINATED; REPAIR THE FIRE ALARM PANEL AND REMOVE IT FROM SUPERVISORY MODE | HighRise | LISA KIMBALL
75131 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS PANEL READS SUPERVISORY MODE THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS | HighRise | LISA KIMBALL
75132 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
75133 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTIONFEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90DAYS | HighRise | LISA KIMBALL
75700 | NoData | HighRise | LISA KIMBALL
75714 | NoData | HighRise | LISA KIMBALL
76659 | NoData | HighRise | LISA KIMBALL
76810 | NoData | HighRise | LISA KIMBALL
78235 | NoData | HighRise | LISA KIMBALL
79007 | NoData | HighRise | LISA KIMBALL
79258 | NoData | HighRise | LISA KIMBALL
79259 | NoData | HighRise | LISA KIMBALL
79260 | NoData | HighRise | LISA KIMBALL
79451 | NoData | HighRise | LISA KIMBALL
79452 | NoData | HighRise | LISA KIMBALL
79470 | NoData | HighRise | LISA KIMBALL
79471 | NoData | HighRise | LISA KIMBALL
79472 | NoData | HighRise | LISA KIMBALL
79473 | NoData | HighRise | LISA KIMBALL
79474 | NoData | HighRise | LISA KIMBALL
79475 | NoData | HighRise | LISA KIMBALL
79476 | NoData | HighRise | LISA KIMBALL
79477 | NoData | HighRise | LISA KIMBALL
79478 | NoData | HighRise | LISA KIMBALL
79479 | NoData | HighRise | LISA KIMBALL
79480 | NoData | HighRise | LISA KIMBALL
79481 | NoData | HighRise | LISA KIMBALL
79482 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY | HighRise | LISA KIMBALL
79483 | EVIDENCE OF INCOMPLETE ORNON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONINGSYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRECODE | HighRise | LISA KIMBALL
79484 | ENSURE ALL CONTENTS ARE FULLY COMPLIANT WITH LSB 5 (INCLUDED IN DOCUMENTS ATTACHED TO THE EMAIL) SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED | HighRise | LISA KIMBALL
79485 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED "Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIREDIF THE HIGH-RISE DOES NOT HAVE ANY OF THESESYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED)DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30 CALENDAR DAYS | HighRise | LISA KIMBALL
79486 | NoData | HighRise | LISA KIMBALL
79487 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD | HighRise | LISA KIMBALL
79488 | NoData | HighRise | LISA KIMBALL
79489 | NoData | HighRise | LISA KIMBALL
79490 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTIONFEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90DAYS | HighRise | LISA KIMBALL
79912 | NoData | HighRise | LISA KIMBALL
80225 | NoData | HighRise | LISA KIMBALL