64559 | Take the Fire Warden Certification class online through the following link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottom to click onHigh-rise Fire Warden Certification Class.Print out the certificate of completion and keep it in a safe place where it can be accessed upon demand. REGISTER FOR FIRE WARDEN TRAINING AThttps://houstontx.gov/fire/HFMO/highrisecert.htmlAny Building Manager in need of High-Riseor Mid-Rise Atruim Certification Training may send attendees to the followingmonthly seminars at no cost. Monthly seminars are available for managementemployees and tenant fire wardens of high-rise buildings who need to becertified. Certificates shall be valid for a period of five years from the dateof training.There is no charge for attending theseseminars. The only cost incurred may be parking fees, if applicable. Manybuildings will have different fire safety features. The building managementfrom each building represented is required to inform its employees and FireWardens of their specific fire safety features to complete the certification. Please note this training is not valid forMid Rise Evacuation Training. For information on mid rise training please visitthe HFD Mid Rise Fire Certication Webpage.Additional training availability information:The Houston Fire Department has set up and implemented a list of all high-risebuildings for Fire Safety Plan approvals. This list was set up to ensure thatpriority is given to buildings that have the greatest need while also providingeach building an equal opportunity. The list of buildings is separated into twogroups based on whether the building is an occupancy where people sleep, suchas hotel, apartments, and condominiums or those buildings where people do notsleep, such as office buildings. Buildings are then sub-grouped by no sprinklersystem, partial sprinkler system, or complete sprinkler systems before sortingby building height. The highest priority building is the residential buildingthat is non-sprinklered, and the tallest in height. Our goal is to provide theneeded services to approve each building within a two-year cycle. Buildingsdesiring to expedite the process also have three additional options. 1. The monthly openhigh-rise certification seminar is for buildings that have requested to send alimited number of fire wardens and building management employees to a classthat is open to all high-rise buildings. The class information is not specificto any particular building and requires building management to supplement thetraining with their building specifics.2. An inspector/instructorin the Life Safety Bureau, Public Education Section - High-rise Fire SafetyPlan Approvals, may be obtained to provide training outside his regular workhours on an overtime basis. This may be done by contacting Diana Cardenas bye-mail at:diana.cardenas@houstontx.gov. This should be done prior to payment of arequired permit fee so that an instructor can be assigned to made contact withthe requesting party, to assist the requesting party with information on theapplication for over-time training and payment of the permit fees, and toschedule a mutually convenient training date.A City of Houston permit fee is required to schedule an inspector/instructor.The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019).3. Having a City of HoustonFire Marshal approved consultant perform the training. The process to receivean approved Fire Safety Plan consist of the three following essential trainingelements conducted by persons, institutions or companies approved by the FireMarshal according to regulations established by the Fire Marshal: aconsultation with building management, an approved certification training forFire Wardens and building employees, and a fire drill supervised by persons,institutions or companies approved by the Fire Marshal.
64560 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS
64561 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL
64562 | Concerningfire drills during COVID-19, a link can be found by going to the "Resources" andthen clicking on "Notices"https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/
64563 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR
64564 | MEMBERS OF THE FIRESAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR
64565 | NoData
64566 | NoData
64567 | NoData
64568 | CITATIONS WILL BE WRITTEN AFTER 2REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT METWITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 30 DAYS
64569 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30 CALENDARDAYS
64570 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
64571 | NoData
64572 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIREDIF THE HIGH-RISE DOES NOT HAVE ANY OF THESESYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED)DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30 CALENDAR DAYS
64573 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED
64574 | EVIDENCE OF INCOMPLETE ORNON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONINGSYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRECODE
64575 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE
64576 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY
64577 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIREPROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY ORNON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEMIS RESTORED TO NORMAL OPERATIONAL STATUS
64578 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN
64579 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE
64580 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERAL ALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1
64581 | Take the Fire Warden Certification class online through thefollowing link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottomto click on High-rise Fire Warden CertificationClass.Print out the certificate of completion and keep it in a safeplace where it can be accessed upon demand. REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Riseor Mid-Rise Atruim Certification Training may send attendees to the followingmonthly seminars at no cost. Monthly seminars are available for managementemployees and tenant fire wardens of high-rise buildings who need to becertified. Certificates shall be valid for a period of five years from the dateof training.There is no charge for attending theseseminars. The only cost incurred may be parking fees, if applicable. Manybuildings will have different fire safety features. The building managementfrom each building represented is required to inform its employees and FireWardens of their specific fire safety features to complete the certification. Please note this training is not valid forMid Rise Evacuation Training. For information on mid rise training please visitthe HFD Mid Rise Fire Certication Webpage.Additional training availability information:The Houston Fire Department has set up and implemented a list of all high-risebuildings for Fire Safety Plan approvals. This list was set up to ensure thatpriority is given to buildings that have the greatest need while also providingeach building an equal opportunity. The list of buildings is separated into twogroups based on whether the building is an occupancy where people sleep, suchas hotel, apartments, and condominiums or those buildings where people do notsleep, such as office buildings. Buildings are then sub-grouped by no sprinklersystem, partial sprinkler system, or complete sprinkler systems before sortingby building height. The highest priority building is the residential buildingthat is non-sprinklered, and the tallest in height. Our goal is to provide theneeded services to approve each building within a two-year cycle. Buildingsdesiring to expedite the process also have three additional options. 1. The monthly openhigh-rise certification seminar is for buildings that have requested to send alimited number of fire wardens and building management employees to a classthat is open to all high-rise buildings. The class information is not specificto any particular building and requires building management to supplement thetraining with their building specifics.2. An inspector/instructorin the Life Safety Bureau, Public Education Section - High-rise Fire SafetyPlan Approvals, may be obtained to provide training outside his regular workhours on an overtime basis. This may be done by contacting Diana Cardenas bye-mail at:diana.cardenas@houstontx.gov. This should be done prior to payment of arequired permit fee so that an instructor can be assigned to made contact withthe requesting party, to assist the requesting party with information on theapplication for over-time training and payment of the permit fees, and toschedule a mutually convenient training date.A City of Houston permit fee is required to schedule an inspector/instructor.The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019).3. Having a City of HoustonFire Marshal approved consultant perform the training. The process to receivean approved Fire Safety Plan consist of the three following essential trainingelements conducted by persons, institutions or companies approved by the FireMarshal according to regulations established by the Fire Marshal: aconsultation with building management, an approved certification training forFire Wardens and building employees, and a fire drill supervised by persons,institutions or companies approved by the Fire Marshal.
64582 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS
64583 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRE CODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS - CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF A SUPERVISED FIRE DRILL SUBMIT A COMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINEDFIRE WARDENS
64584 | Concerningfire drills during COVID-19, a link can be found by going to the "Resources" andthen clicking on "Notices"https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/
64585 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR
64586 | MEMBERS OF THE FIRESAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR
64587 | NoData
64588 | HOUSEKEEPING IS REQUIRED IN THE GROUND FLOOR MECHANICAL ROOM (BY KRUP)
64589 | FIRE EXTINGUISHERS ARE REQUIRED IN ALL ELEVATOR ROOMS, ELECTRICAL ROOMS, IT ROOMS, GENERATOR ROOMS AND MECHANICAL ROOMS PROVIDE A FIRE EXTINGUISHER IN THE FIRE CONTROL ROOM AND THE MECHANICAL ROOM IN THE GARAGE
64590 | PROVIDE BLANKS OR COVERS FOR MISSING TEETH, CIRCUITS OR VOIDS IN THE ELECTRICAL PANEL IN THE MECHANICAL ROOMS ON THE ROOF AND THE 11TH FLOORS
64591 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOST RECENT TEST EXIT SIGNS WERE FOUND OUT/NOT ILLUMINATED ON THE 8TH FLOOR ABOVE 803 - REPAIR OR REPLACE THEM IMMEDIATELY
64592 | THE FIRE ALARM SYSTEM IS YELLOW TAGGED - A YELLOW TAG WAS ISSUED IN 14AUG19 AND MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY
64593 | PROVIDE EXIT SIGNS ON THE EXTERIOR SIDE AT THE GROUND LEVEL TO IDENTIFY STAIR C
64594 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64595 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL
64596 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY
64597 | NoData
64598 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - N/A - REQUIRED IF BOILERS ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS
64599 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE)
64600 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN UTILITY ROOMS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR - PROVIDE PROTECTION ON BULBS IN THE 11TH FLOOR ELEVATOR ROOM, THE ELECTRICAL ROOMS ON THE 11TH, 7TH AND 6TH FLOORS, STAIR B ON THE 8TH FLOOR, THE MECHANICAL ROOMS ON THE ROOF, 10TH, 9TH AND GROUND FLOOR AND IN THE DELI
64601 | THE CERTIFICATE OF OCCUPANCY AND ALL PERMITS SHOULD BE POSTED IN THE RESPECTIVE BUSINESS (DELI)
64602 | OBTAIN ALL REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER - THE DELI REQUIRES A CERTIFICATE OF OCCUPANCY
64603 | DOORS TO/FROM THE GARAGE REQUIRE MAG LOCK APPROVAL FROM THE BUILDING DEPARTMENT ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION
64604 | ENSURE THE OPENING FORCE FOR THE DOOR LATCH ON THE 11TH FLOOR (STAIR A) AND THE 10TH FLOOR (STAIR B) RELEASE WHEN SUBJECTED TO A FORCE OF NO MORE THAN 15LBS
64605 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE
64606 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE
64607 | THE MOBILITY IMPAIRED LIST MUST BE UPDATED EVERY 6 MONTHS - LAST UPDATED MARCH 2017
64608 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64609 | RECEIVED; NO FURTHER ACTION NECESSARY
64610 | THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH (WHICH IS INSIDE THE "MECHANICAL ROOM") ON THE 11TH, 10TH, 9TH, 8TH, 7TH AND 6TH FLOORS
64611 | PROVIDE SIGN ON THE DOOR OF THE GROUND FLOOR ENGINE SHOP TO INDICATE THE PRESENCE OF DIESEL
64612 | SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED
64613 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
64614 | EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE REPLACE CIELING TILES OR TURN THE SPRINKLER HEADS UP IN THE ELECTRICAL ROOMS ON THE 9TH, 8TH, 7TH, 6TH, 5TH, 4TH, 3RD AND 2ND FLOORS
64615 | DOOR CLOSERS FOUND ON THE 8TH FLOOR (STAIR B) IS NOT WORKING PROPERLY - ENSURE DOORS ARE LATCHING SHUT ON ALL EXIT STAIRWELL DOORS
64616 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64617 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64618 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64619 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS
64620 | REMOVE AND DISCONTINUE STORAGE OF GASOLINE FUELED EQUIPTMENT IN THE FIRE PUMP ROOM
64621 | READ AND REVIEW LSB STANDARD 6; FULL COMPLIANCE OF PROVIDING A PROPERLY SUPPLIED FIRE DEPOSITORY BOX IS REQUIRED IMMEDIATELY
64622 | PROVIDE DOCUMENTATION OR LETTER TO ENSURE ALL FIREPHONES AND JACKS (IN THE BUILDING ON ALL FLOORS) HAVE BEEN TESTED BY AN APPROVED, CERTIFIED FIRE PROTECTION COMPANY AND FUNCTIONING PROPERLY ENSURE 2 FIRE PHONES ARE PROVIDED
64623 | INDICATE DIRECTION AND LOCATION OF FIRE COMMAND ROOM FROM THE ENTRANCE OF THE BUILDING
64624 | THE ANSUL SYSTEM IN THE DELI WAS LAST INSPECTED AND TAGGED OCTOBER 2016 - ENSURE THE SYSTEM IS INSPECTED AND BLUE TAGGED EVERY 6 MONTHS
64625 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64626 | REMOVE AND DISCONTINUE USE OF UNAPPROVED EXTENSION CORD (BROWN EXTENSION CORD IN THE DELI) - ONLY UL APPROVED, SURGE PROTECTED CORDS ARE SAFE FOR TEMPORARY USE
64627 | ENSURE A SIGN POSTED NEXT TO THE CALL BUTTONS IN THE ELEVATOR LOBBY ON THE 3RD FLOOR WHICH INCLUDES A PICTORIAL OR DIAGRAM OF A MAP SHOWING THE FLOOR LAYOUT AND EXACT LOCATION OF THE EXITS IN RELATION TO THE ELEVATORS
64628 | THE EXIT DOOR IN STAIR A DOES NOT LATCH CLOSED DOOR CLOSERS FOUND ON THE 10TH FLOOR (STAIR A), 9TH FLOOR (STAIR A), 6TH FLOOR (STAIR B), THE 2ND FLOOR (STAIR B) AND THE GROUND FLOOR (STAIR C) ARE NOT WORKING PROPERLY - ENSURE DOORS ARE LATCHING SHUT ON ALL EXIT STAIRWELL DOORS
64629 | CABINETS CONTAINING FIRE FIGHTING EQUIPMENT MUST INDICATE THE EQUIPTMENT CONTAINED THEREIN - "FIRE HOSE" AND/OR "FIRE EXTINGUISHER" - CABINETS MUST BE CORRECTLY MARKED ON THE 8TH FLOOR, 7TH FLOOR, 6TH FLOOR, 4TH FLOOR, GROUND FLOOR AND THROUGHOUT THE GARAGE
64630 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64631 | THE CLASS K FIRE EXTINGUISHER IN THE DELI MUST BE INSPECTED ANNUALLY - LAST INSPECTION WAS OCTOBER 2016
64632 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64633 | ALL FIRE EXTINGUISHERS MUST HAVE A CURRENT TAG INDICATING DATE OF LAST ANNUAL INSPECTION OR SERVICE/MAINTENANCE - EXTINGUISHER IN THE DELI LAST INSPECTED AND TAGGED IN OCTOBER 2016 AND THE EXTIGUISHER IN THE ELEVATOR ROOM ON THE ROOF WAS LAST INSPECTED IN MAY 2017
64634 | PROVIDE 2 ELEVATOR INDEPENDANT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX
64635 | PROVIDE 2 ELEVATOR HOISTWAY KEYS/TOOLS (OF EACH TYPE) IN THE FIRE DEPOSITORY BOX - ONLY ONE IS PROVIDED
64636 | THE HOOD VENTS AND HOOD SUPPRESSION SYSTEM IN THE DELI MUST BE INSPECTED AND SERVICED - ENSURE THIS IS CONDUCTED AS SOON AS POSSIBLE AND COMPLIES WITH THE FIRE CODE IN THE FUTURE ALL VENT HOOD SUPPRESSION SYSTEMS MUST BE INSPECTED AND SERVICED AT LEAST EVERY 6 MONTHS - MAINTAIN EVIDENCE ON SITE OR STICKER THE EQUIPMENT INDICATING SERVICE DATE
64637 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS
64638 | NoData
64639 | NoData
64640 | NoData
64641 | NoData
64642 | NoData
64643 | NoData
64644 | NoData
64645 | PROVIDE A COVER PLATE FOR EXPOSED ELECTRICAL OUTLET BEHIND THE UPS BOX ON THE GROUND FLOOR
64646 | THE BACK EXIT DOOR AND ABOVE ACCESS GATE CONTROL TO SUITE 700 SHOULD BE LABELED "SUITE 700 ACCESS GATE CONTROL"
64647 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64648 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL
64649 | NoData
64650 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY
64651 | ENSURE THE EMERGENCY "RE-ENTRY" BUTTON ON THE FIRE ALARM PANEL IS HIGHLIGHTED OR CONSPICUOUSLY LABELED
64652 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - RECIEVED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - RECIEVED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - RECIEVED " Electronic Locks -Semi Annual - RECIEVED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - RECIEVED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - RECIEVED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - RECIEVED " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - RECIEVED " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS
64653 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE)
64654 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE ELEVATOR ROOM ON THE GROUND FLOOR IN JOE'S OFFICE & THE ELCTRICAL ROOM, ON THE 6TH FLOOR, MECHANICAL ROOMS ON THE 12TH & 13TH FLOORS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR
64655 | THE EXIT DOOR ON THE 14TH FLOOR STAIR B IS STICKING - ENSURE ALL EXIT DOORS ARE CAPABLE OF OPENING WITH EASE
64656 | OBTAIN ALL REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER - F7 (FLAMMABLE LIQUIDS PERMIT) AND K1 (KEY BOX PERMIT) ARE DUE THE ALARM PERMIT COULD NOT BE LOCATED IN OUR SYSTEM VIA MY SEARCH - PLEASE VISIT THE HOUSTON PERMITTING CENTER AND OBTAIN THE FIRE ALARM PERMIT
64657 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION
64658 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE
64659 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE
64660 | THE MOBILITY IMPAIRED LIST MUST BE UPDATED EVERY 6 MONTHS
64661 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64662 | RECEIVED; NO FURTHER ACTION NECESSARY
64663 | THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH - IDENTIFY ACCESS TO THE ELECTRICAL ROOM THROUGH SUITE 350
64664 | PROVIDE SIGN ON THE DOOR OF THE PRESSURE WASHING CAGE IN THE GARAGE TO INDICATE THE PRESENCE OF DIESEL
64665 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
64666 | DOOR CLOSER FOUND ON THE 14TH FLOOR (STAIR B) IS NOT WORKING PROPERLY - ENSURE DOORS ARE LATCHING SHUT ON ALL EXIT STAIRWELL DOORS
64667 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64668 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64669 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64670 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS
64671 | PERTAINING TO PLACEMENT AND DISTANCE OF FIRE EXTINGUISHERS NEEDED THROUGHOUT THE PARKING GARAGE ENSURE THAT ENOUGH FIRE EXTINGUISHERS ARE SUPPLIED, OBVIOUS AND ACCESSIBLE IN THE PARKING GARAGE (AN S-2) NO FIRE EXTINGUISHERS WERE FOUND IN THE PARKING GARAGE - SUPPLY FIRE EXTINGUISHERS ON ALL LEVELS IN DISTANCES PRESCRIBED BY THE FIRE CODE
64672 | ADD FOBS FOR ENTRY TO ALL 5 SETS OF KEYS IN THE FDB WRITE CODE FOR ENTRY TO PUMP ROOM ON KEY TAG TO PUMP ROOM (ON ALL 5 SETS) READ AND REVIEW LSB STANDARD 6; FULL COMPLIANCE OF PROVIDING A PROPERLY SUPPLIED FIRE DEPOSITORY BOX IS REQUIRED IMMEDIATELY
64673 | PROVIDE DOCUMENTATION OR LETTER TO ENSURE ALL FIREPHONES AND JACKS (IN THE BUILDING ON ALL FLOORS) HAVE BEEN TESTED BY AN APPROVED, CERTIFIED FIRE PROTECTION COMPANY AND FUNCTIONING PROPERLY FIREFIGHTER PHONES AND ALL JACKS IN THE BUILDING MUST BE TESTED ANNUALLY
64674 | ALL ELECTRICAL ROOMS, HVAC ROOMS, MECHANICAL ROOMS, IT ROOMS, ELEVATOR ROOMS, FIRE SPRINKLER RISER ROOMS, FIRE ALARM ROOMS AND TRANSFORMER ROOMS MUST BE LABELED AS SUCH FOR READY IDENTIFICATION - ID THE "PIT" AND ELEVATOR ROOM ON THE 10TH FLOOR, ID THE MECHANICAL ROOM ON THE 3RD FLOOR, ID THE MECHANICAL ROOM ALSO AS "DRY PIPE" ON THE 3RD FLOOR AND ACCESS TO THE GARAGE ELEVATORS THROUGH SUITE 620
64675 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64676 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64677 | THE EXIT DOOR ON THE 14TH FLOOR STAIR B DOES NOT LATCH CLOSED
64678 | CABINETS CONTAINING FIRE FIGHTING EQUIPMENT MUST INDICATE THE EQUIPMENT CONTAINED THEREIN - "FIRE HOSE" AND/OR "FIRE EXTINGUISHER" - CORRECTLY IDENTIFY CONTENTS OF CABINET ON THE 3RD FLOOR
64679 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64680 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
64681 | PROVIDE 2 ELEVATOR INDEPENDANT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX
64682 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS
64683 | Failure to service red tagged systems will be subject to citations and re-inspection fees.
64684 | Fire alarm system is red tagged and must be serviced within 72 hours
64685 | A Fire Department stand-by may be required if red-tagged system is not serviced in a timely manner.
64686 | NoData
64687 | NoData
64688 | NoData
64689 | NoData
64690 | NoData
64691 | NoData
64692 | NoData
64693 | NoData
64694 | NoData
64695 | NoData
64696 | NoData
64697 | NoData
64698 | NoData
64699 | NoData
64700 | NoData
64701 | NoData
64702 | NoData
64703 | NoData
64704 | NoData
64705 | NoData
64706 | NoData
64707 | NoData
64708 | NoData
64709 | NoData
64710 | NoData
64711 | NoData
64712 | NoData
64713 | NoData
64714 | NoData
64715 | NoData
64716 | NoData
64717 | NoData
64718 | NoData
64719 | NoData
64720 | NoData
64721 | NoData
64722 | NoData
64723 | NoData
64724 | NoData
64725 | NoData
64726 | NoData
64727 | NoData
64728 | NoData
64729 | ol check, ol is 99, about 9 persons in club. issued permit renewal notice, p2 requested by G.O. Insp back in feb,2013. reinspect on 11-23-13. current permit expired in dec. 2012
64730 | NoData
64731 | NoData
64732 | WIRES FOUND HANGING FROM THE CIELING IN THE MAINTENANCE ROOM ON THE GROUND FLOOR MUST BE CAPPED AND SECURED IN THE JUNCTION BOX
64733 | THE LIGHTS ARE NOT OPERATING IN THE STAIRWELL BETWEEN THE 3RD AND 2ND FLOOR AND MUST BE REPAIRED OR REPLACED
64734 | A YELLOW TAGGED WAS DISCOVERED IN ON THE STANDPIPE IN THE STAIRWELL - SYSTEM MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY
64735 | IDENTIFY AND LABEL THE FIRE DEPARTMENT TEST CONNECTION ON THE ROOF
64736 | A FIRE DRILL MUST BE SUPERVISED BY JUAN GARCIA - CONTACT HIM PRIOR TO PLANNING AND SCHEDULING
64737 | PERTAINING TO SIGN INDICATING FLAMMABLES OR DIESEL FOR THE MAINTENANCE SHOP AND CENTRAL PLANT
64738 | NoData
64739 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY
64740 | PROVIDE UL APPROVED RED CAN IN ELEVATOR ROOMS AND ENSURE THEY ARE EMPTIED DAILY
64741 | SUPPLY STAIRWELL SIGN FOR THE PARKING GARAGE (C AND D)
64742 | Facility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system must be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED FOR GARAGE " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED FOR GARAGE " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - N/A - REQUIRED IF BOILERS ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS
64743 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE)
64744 | PEDESTRIAN DOORS AND/OR MAG LOCKS AND EMERGENCY RELEASE BUTTONS ARE NEEDED IN THE PARKING GARAGE TO ENABLE PEDESTRIANS TO ESCAPE IN CASE OF EMERGENCY
64745 | REMOVE AND DISCONTINUE STORAGE IN EXIT ACCESSES, EXITS OR EXIT DISCHARGES - KEEP THE BACK EXIT OF THE DELI FREE FROM OBTRUCTIONS AT ALL TIMES THE BUILDING IS OCCUPIED
64746 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE MAINTENANCE ROOM ON THE GROUND FLOOR ROOM AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR
64747 | A COPIES OF PERMITS (IF NEEDED) AND A CERTIFICATE OF OCCUPANCY FOR THE DELI MUST BE POSTED IN THE BUSINESS
64748 | IF THE DELI HAS AN OCCUPANCY LOAD OF MORE THAN 50 - THE OCCUPANCY LOAD MUST BE POSTED CONSPICUOUSLY NEAR THE ENTRANCE
64749 | OBTAIN ALL REQUIRED PERMITS AND CERTIFICATES OF OCCUPANCY FROM THE HOUSTON PERMITTING CENTER THE DELI WILL REQUIRE AN ASSEMBLY PERMIT (P2) IF THE OCCUPANCY LOAD IS MORE THAN 50 PERSONS
64750 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION
64751 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE
64752 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE
64753 | THE MOBILITY IMPAIRED LIST WAS LAST UPDATED IN 2016 - THIS LIST MUST BE UPDATED EVERY 6 MONTHS
64754 | NoData
64755 | LETTER RECIEVED; NO FURTHER ACTION NECESSARY
64756 | A SIGN OR ADHESIVE STATING "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED" MUST BE POSTED ON OR NEAR THE FRONT ENTRANCE DOOR OF THE DELI
64757 | PROVIDE A FLAMMABLE STORAGE CABINET FOR THE MAINTENANCE SHOP IF NEEDED
64758 | ALL ELECTRICAL CIRCUIT BREAKERS IN ELECTRICAL PANELS MUST BE CLEARLY AND CORRECTLY LABELED - CABINETS #2, 3 AND 4 IN 2L ON THE 2ND FLOOR THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH (ADD "ELECTRICAL ROOM" TO THE MECHANICAL ROOMS) ON THE 8TH, 7TH, 6TH, 5TH, 4TH AND 3RD FLOORS
64759 | PROVIDE SIGN TO INDICATE FLAMMABLES OR DIESEL IN THE MAINTENANCE SHOP AND CENTRAL PLANT
64760 | SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED
64761 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
64762 | EVIDENCE OF INCOMPLETE AND NON FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED - ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE
64763 | THE "MECHANICAL ROOM" MUST ALSO BE MARKED "ELEVATOR ROOM" FOR IDENTIFICATION
64764 | SEVERAL DOORS IN THE STAIRWELL DO NOT LATCH CLOSED
64765 | NoData
64766 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION
64767 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION
64768 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS
64769 | PERTAINING TO PLACEMENT AND DISTANCE OF FIRE EXTINGUISHERS NEEDED THROUGHOUT THE PARKING GARAGE ENSURE THAT FIRE EXTINGUISHERS ARE SUPPLIED, OBVIOUS AND ACCESSIBLE IN THE PARKING GARAGE (AN S-2)
64770 | NoData
64771 | THE SUPPLEMENTAL INFO SHEET MUST BE UPDATED PROVIDE THE 8X 11 LAMINATED LEGEND CARD IN COLOR THE FDB MUST BE DOUBLE LOCKED SO IT CAN BE ACCESSED BY HFD AND BUILDING MANAGEMENT PROVIDE THE COMBINATION OF THE ROOF LOCK ON ALL 5 KEY RINGS AND IN THE BINDER READ AND REVIEW LSB STANDARD 6; FULL COMPLIANCE OF PROVIDING A PROPERLY SUPPLIED FIRE DEPOSITORY BOX IS REQUIRED IMMEDIATELY
64772 | FIRE PHONES AND ALL JACKS MUST BE TESTED BY A CERTIFIED COMPANY
64773 | THE ANSUL SYSTEM IN THE DELI WAS LAST INSPECTED IN SEPTEMBER 2014 - THIS SYSTEM MUST BE INSPECTED AND TAGGED AT LEAST EVERY 6 MONTHS
64774 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION
64775 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION
64776 | THE LOCK-OUT/TAG-OUT EQUIPMENT AND SETS MUST BE READILY ACCESSIBLE AND PROPERLY LABELED - SUPPLY EQUIPMENT FOR THE ELEVATOR ROOM ON THE GROUND FLOOR: - PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS - A MINIMUM TWO (2) LOCK-OUT/TAG-OUT SETS FOR 4 TO 6 ELEVATORS - A MINIMUM THREE (3) LOCK-OUT/TAG-OUT SETS FOR 7 OR MORE ELEVATORS
64777 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION
64778 | DOOR CLOSERS FOUND ON THE 3RD FLOOR (STAIR B), THE 2ND FLOOR AND THE GROUND FLOOR (STAIR A) ARE NOT WORKING PROPERLY - ENSURE DOORS ARE LATCHING SHUT ON ALL EXIT STAIRWELL DOORS
64779 | FIRE EXTINGUISHERS IN THE STAIRWELLS ARE NOT A SUBSTITUTE FOR EXTINGUISHERS REQUIRED ON EACH FLOOR IN THE HALLS/CORRIDORS - FIRE EXTINGUISHERS MUST BE CONSPICUOUSLY LOCATED, READILY AVAILABLE AND ALONG "NORMAL PATHS OF TRAVEL" - REMOVE AND RELOCATE FIRE EXTIGUISHERS FROM THE STAIRWELLS ON THE 8TH, 4TH, 3RD AND 2ND FLOORS
64780 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION
64781 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION
64782 | PLEASE CONTACT INSPECTOR JUAN GARCIA BY EMAIL AT Juan.Garcia3@houstontx.gov OR 281.896.7084 WITH QUESTIONS CONCERNING EVACUATION DRILLS, FIRE WARDEN TRAINING, ETC
64783 | THE VENT HOOD SYSTEM IN THE DELI MUST BE INSPECTED AND SERVICED AT LEAST EVERY 6 MONTHS THE VENT HOOD REQUIRES CLEANING
64784 | PROVIDE CAP (MISSING) FOR 3" CONNECTION IN GARAGE
64785 | THE FIRE ALARM MUST DISPLAYS "TROUBLES" AND MUST BE INVESTIGATED AND RECTIFIED
64786 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT OR SERVICE THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS
64787 | ENSURE A SET OF INDEPENDENT SERVICE KEYS ARE ACCESSIBLE AND PROVIDED OUTSIDE OF THE FIRE DEPOSITORY BOX FOR EMERGENCIES
64788 | NoData
64789 | NoData
64790 | WIRES FOUND HANGING FROM THE CIELING IN THE MAINTENANCE ROOM ON THE GROUND FLOOR MUST BE CAPPED AND SECURED IN THE JUNCTION BOX
64791 | THE LIGHTS ARE NOT OPERATING IN THE STAIRWELL BETWEEN THE 3RD AND 2ND FLOOR AND MUST BE REPAIRED OR REPLACED
64792 | A YELLOW TAGGED WAS DISCOVERED IN ON THE STANDPIPE IN THE STAIRWELL - SYSTEM MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY
64793 | IDENTIFY AND LABEL THE FIRE DEPARTMENT TEST CONNECTION ON THE ROOF
64794 | A FIRE DRILL MUST BE SUPERVISED BY JUAN GARCIA - CONTACT HIM PRIOR TO PLANNING AND SCHEDULING
64795 | PERTAINING TO SIGN INDICATING FLAMMABLES OR DIESEL FOR THE MAINTENANCE SHOP AND CENTRAL PLANT
64796 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY
64797 | NoData
64798 | PROVIDE UL APPROVED RED CAN IN ELEVATOR ROOMS AND ENSURE THEY ARE EMPTIED DAILY
64799 | SUPPLY STAIRWELL SIGN FOR THE PARKING GARAGE (C AND D)
64800 | Facility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system must be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED FOR GARAGE " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED FOR GARAGE " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - N/A - REQUIRED IF BOILERS ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS
64801 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE)
64802 | PEDESTRIAN DOORS AND/OR MAG LOCKS AND EMERGENCY RELEASE BUTTONS ARE NEEDED IN THE PARKING GARAGE TO ENABLE PEDESTRIANS TO ESCAPE IN CASE OF EMERGENCY
64803 | REMOVE AND DISCONTINUE STORAGE IN EXIT ACCESSES, EXITS OR EXIT DISCHARGES - KEEP THE BACK EXIT OF THE DELI FREE FROM OBTRUCTIONS AT ALL TIMES THE BUILDING IS OCCUPIED
64804 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE MAINTENANCE ROOM ON THE GROUND FLOOR ROOM AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR
64805 | A COPIES OF PERMITS (IF NEEDED) AND A CERTIFICATE OF OCCUPANCY FOR THE DELI MUST BE POSTED IN THE BUSINESS
64806 | IF THE DELI HAS AN OCCUPANCY LOAD OF MORE THAN 50 - THE OCCUPANCY LOAD MUST BE POSTED CONSPICUOUSLY NEAR THE ENTRANCE
64807 | OBTAIN ALL REQUIRED PERMITS AND CERTIFICATES OF OCCUPANCY FROM THE HOUSTON PERMITTING CENTER THE DELI WILL REQUIRE AN ASSEMBLY PERMIT (P2) IF THE OCCUPANCY LOAD IS MORE THAN 50 PERSONS
64808 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION
64809 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE
64810 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE
64811 | THE MOBILITY IMPAIRED LIST WAS LAST UPDATED IN 2016 - THIS LIST MUST BE UPDATED EVERY 6 MONTHS
64812 | NoData
64813 | LETTER RECIEVED; NO FURTHER ACTION NECESSARY
64814 | A SIGN OR ADHESIVE STATING "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED" MUST BE POSTED ON OR NEAR THE FRONT ENTRANCE DOOR OF THE DELI
64815 | PROVIDE A FLAMMABLE STORAGE CABINET FOR THE MAINTENANCE SHOP IF NEEDED
64816 | ALL ELECTRICAL CIRCUIT BREAKERS IN ELECTRICAL PANELS MUST BE CLEARLY AND CORRECTLY LABELED - CABINETS #2, 3 AND 4 IN 2L ON THE 2ND FLOOR THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH (ADD "ELECTRICAL ROOM" TO THE MECHANICAL ROOMS) ON THE 8TH, 7TH, 6TH, 5TH, 4TH AND 3RD FLOORS
64817 | PROVIDE SIGN TO INDICATE FLAMMABLES OR DIESEL IN THE MAINTENANCE SHOP AND CENTRAL PLANT
64818 | SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED
64819 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
64820 | EVIDENCE OF INCOMPLETE AND NON FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED - ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE
64821 | THE "MECHANICAL ROOM" MUST ALSO BE MARKED "ELEVATOR ROOM" FOR IDENTIFICATION
64822 | SEVERAL DOORS IN THE STAIRWELL DO NOT LATCH CLOSED
64823 | NoData
64824 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION
64825 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION
64826 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS
64827 | PERTAINING TO PLACEMENT AND DISTANCE OF FIRE EXTINGUISHERS NEEDED THROUGHOUT THE PARKING GARAGE ENSURE THAT FIRE EXTINGUISHERS ARE SUPPLIED, OBVIOUS AND ACCESSIBLE IN THE PARKING GARAGE (AN S-2)
64828 | NoData
64829 | THE SUPPLEMENTAL INFO SHEET MUST BE UPDATED PROVIDE THE 8X 11 LAMINATED LEGEND CARD IN COLOR THE FDB MUST BE DOUBLE LOCKED SO IT CAN BE ACCESSED BY HFD AND BUILDING MANAGEMENT PROVIDE THE COMBINATION OF THE ROOF LOCK ON ALL 5 KEY RINGS AND IN THE BINDER READ AND REVIEW LSB STANDARD 6; FULL COMPLIANCE OF PROVIDING A PROPERLY SUPPLIED FIRE DEPOSITORY BOX IS REQUIRED IMMEDIATELY
64830 | FIRE PHONES AND ALL JACKS MUST BE TESTED BY A CERTIFIED COMPANY
64831 | THE ANSUL SYSTEM IN THE DELI WAS LAST INSPECTED IN SEPTEMBER 2014 - THIS SYSTEM MUST BE INSPECTED AND TAGGED AT LEAST EVERY 6 MONTHS
64832 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION
64833 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION
64834 | THE LOCK-OUT/TAG-OUT EQUIPMENT AND SETS MUST BE READILY ACCESSIBLE AND PROPERLY LABELED - SUPPLY EQUIPMENT FOR THE ELEVATOR ROOM ON THE GROUND FLOOR: - PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS - A MINIMUM TWO (2) LOCK-OUT/TAG-OUT SETS FOR 4 TO 6 ELEVATORS - A MINIMUM THREE (3) LOCK-OUT/TAG-OUT SETS FOR 7 OR MORE ELEVATORS
64835 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION
64836 | DOOR CLOSERS FOUND ON THE 3RD FLOOR (STAIR B), THE 2ND FLOOR AND THE GROUND FLOOR (STAIR A) ARE NOT WORKING PROPERLY - ENSURE DOORS ARE LATCHING SHUT ON ALL EXIT STAIRWELL DOORS
64837 | FIRE EXTINGUISHERS IN THE STAIRWELLS ARE NOT A SUBSTITUTE FOR EXTINGUISHERS REQUIRED ON EACH FLOOR IN THE HALLS/CORRIDORS - FIRE EXTINGUISHERS MUST BE CONSPICUOUSLY LOCATED, READILY AVAILABLE AND ALONG "NORMAL PATHS OF TRAVEL" - REMOVE AND RELOCATE FIRE EXTIGUISHERS FROM THE STAIRWELLS ON THE 8TH, 4TH, 3RD AND 2ND FLOORS
64838 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION
64839 | CONTACT INSPECTOR JUAN GARCIA FOR INFORMATION
64840 | PLEASE CONTACT INSPECTOR JUAN GARCIA BY EMAIL AT Juan.Garcia3@houstontx.gov OR 281.896.7084 WITH QUESTIONS CONCERNING EVACUATION DRILLS, FIRE WARDEN TRAINING, ETC
64841 | THE VENT HOOD SYSTEM IN THE DELI MUST BE INSPECTED AND SERVICED AT LEAST EVERY 6 MONTHS THE VENT HOOD REQUIRES CLEANING
64842 | PROVIDE CAP (MISSING) FOR 3" CONNECTION IN GARAGE
64843 | THE FIRE ALARM MUST DISPLAYS "TROUBLES" AND MUST BE INVESTIGATED AND RECTIFIED
64844 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT OR SERVICE THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS
64845 | ENSURE A SET OF INDEPENDENT SERVICE KEYS ARE ACCESSIBLE AND PROVIDED OUTSIDE OF THE FIRE DEPOSITORY BOX FOR EMERGENCIES
64846 | NoData
64847 | NoData
64848 | NoData
64849 | NoData
64850 | NoData
64851 | NoData
64852 | NoData
64853 | NoData
64854 | Repair is required for the exit sign located over the doorway, in the infant building, leading to the exit gate.
64855 | To maintain compliance with the State of Texas, a gas leak test is required at least every two(2) years for this business type.
64856 | NoData
64857 | NoData
64858 | NoData
64859 | NoData
64860 | NoData
64861 | NoData
64862 | NoData
64863 | NoData
64864 | NoData
64865 | NoData
64866 | NoData
64867 | NoData
64868 | NoData
64869 | NoData
64870 | NoData
64871 | NoData
64872 | NoData
64873 | NoData
64874 | NoData
64875 | NoData
64876 | OIL ALL 911 BOXES ON THE WEST SIDE OF BUILDING FOR EASY OPENING. COMPLIANCE WITHIN 30 DAYS.
64877 | NoData
64878 | NoData
64879 | INFORMATION ONLYFire Extinguisher expire 2-2021Fire Alarm Panel expire 2-19-2021
64880 | NoData
64881 | NoData
64882 | NoData
64883 | NoData
64884 | NoData
64885 | NoData
64886 | Please make sure access gates/key box permits are updated. expired on 09/21/2019
64887 | Please make sure access gates/key box permits are updated. expired on 09/21/2019
64888 | Please provide date of last 5 year gas test. If date is prior to 10/31/2015, please schedule another 5 year gas test for property.
64889 | a smoke alarm shall be installed inside all sleeping rooms and along pathway to main exit discharge.
64890 | blue reflector placed on driveway/parking lot marking location of fire hydrant
64891 | All weather 18"x18" "HFD" sign with the number _______ indicating the number of fire hydrants located on property.
64892 | visually inspect all attic spaces for draft stops compliance.
64893 | all electrical panel doors shall have the proper unit number added to the outside door
64894 | NoData
64895 | If previous gas test is older that 5 years, please schedule another gas test with a licensed plumber
64896 | Proper placement of working smoke alarms
64897 | Blue reflectors
64898 | 18"x18" - "HFD 09" all weather sign
64899 | visually inspect all attic spaces for solid draft stop construction
64900 | Identify all electrical panels with proper unit numbers.
64901 | Please make sure all trash is placed inside dumpsters.
64902 | Clear and maintain aisle clearance.
64903 | Replace missing ceiling tiles.
64904 | Mount the fire extinguishers placed on the ground.
64905 | Fire extinguishers are due for annual inspection before the end of 12/2020.
64906 | Clear and maintain 36 inches of clearance in front of the breaker panels.
64907 | Have someone inspect, test, and repair all exit signs and make sure they are illuminated correctly and the backup batteries will illuminate the signs during a power outage.
64908 | Must secure compressed gas containers to a fixed object with chain, rope, or other material to prevent containers from falling.
64909 | It is the owner/occupants responsibility to correct all fire code violations.
64910 | Please clear out anything blocking the rear exits, including boxes, shelving, and other obstructions. Make sure all marked exits are clear of obstructions.
64911 | Repair or replace Exit sign located at the front of building. Exit signs shall be illuminated at all times.
64912 | Remove extension cord that is being run through the ceiling. No extension cords can be ran through the ceiling.
64913 | NoData
64914 | NoData
64915 | NoData
64916 | Please renew expired Access Gate permit (a4)permit expired on 12/9/2020.
64917 | NoData
64918 | NoData
64919 | NoData
64920 | NoData
64921 | NoData
64922 | NoData
64923 | NoData
64924 | NoData
64925 | NoData
64926 | Renew fire prevention permits that will expire in 12/2020.
64927 | Clear and maintain 3 feet of clearance around the spray booth.
64928 | Have a licensed fire protection company inspect and tag the spray booth extinguishing system.
64929 | NoData
64930 | NoData
64931 | NoData
64932 | NoData
64933 | NoData
64934 | NoData
64935 | NoData
64936 | NoData
64937 | NoData
64938 | NoData
64939 | NoData
64940 | NoData
64941 | NoData
64942 | NoData
64943 | NoData
64944 | NoData
64945 | LSB STANDARD 01 REV. 05 INSTALLATION AND MAINTENANCE OF PORTABLE FIRE EXTINGUISHERS 1.3.1 Annual Maintenance. All fire extinguishers shall have a current annual inspection tag by an approved licensed fire protection equipment company. All servicing, testing, maintenance and tagging of listed portable fire extinguishers shall be conducted annually by qualified personnel in accordance with LSB Standard 02, Inspection and Testing of Fire Protection and Life-Safety Equipment. Fire extinguishers on floor 7 and 8 need to inspected and tagged. Compliance within 30 days
64946 | NoData
64947 | NoData
64948 | Gas test permit required prior to testing the system.
64949 | Gas test required every 5 years by a licensed plumber.
64950 | NoData
64951 | NoData
64952 | Unpermitted and/or unapproved gate barriers must be corrected for emergency access
64953 | NoData
64954 | NoData
64955 | NoData
64956 | NoData
64957 | NoData
64958 | NoData
64959 | NoData
64960 | NoData
64961 | NoData
64962 | NoData
64963 | NoData
64964 | NoData
64965 | NoData
64966 | NoData
64967 | NoData
64968 | NoData
64969 | NoData
64970 | NoData
64971 | NoData
64972 | NoData
64973 | NoData
64974 | NoData
64975 | NoData
64976 | NoData
64977 | NoData
64978 | Move exit sign in hallway leading to front door above door or higher so when door is open it does not block the view of the exit door.
64979 | NoData
64980 | NoData
64981 | NoData
64982 | NoData
64983 | NoData
64984 | NoData
64985 | NoData
64986 | Have the emergency lighting tested and replace any inoperable lighting.
64987 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
64988 | Clear and maintain 18 inches of ceiling clearance.
64989 | Have a licensed fire protection company perform a 5 year FDC test and correct and deficiencies.
64990 | Have a licensed fire protection company perform an annual sprinkler inspection and correct any deficiencies.
64991 | Correct the yellow tagged fire alarm panel.
64992 | Ensure fire extinguishers are unobstructed.
64993 | Clear and maintain 36 inches of working space in front of the breaker panels.
64994 | NoData
64995 | NoData
64996 | NoData
64997 | NoData
64998 | NoData
64999 | NoData
65000 | NoData
65001 | NoData
65002 | NoData
65003 | NoData
65004 | NoData
65005 | NoData
65006 | NoData
65007 | NoData
65008 | NoData
65009 | NoData
65010 | NoData
65011 | NoData
65012 | NoData
65013 | NoData
65014 | NoData
65015 | NoData
65016 | NoData
65017 | NoData
65018 | Clear and maintain ceiling clearance.
65019 | Remove obstructions in front of the side exit.
65020 | Clear and maintain clearance in front of breaker panels.
65021 | NoData
65022 | NoData
65023 | NoData
65024 | NoData
65025 | NoData
65026 | FIX ALARM MALFUNCTION.
65027 | NoData
65028 | NoData
65029 | NoData
65030 | NoData
65031 | NoData
65032 | NoData
65033 | NoData
65034 | NoData
65035 | NoData
65036 | NoData
65037 | NoData
65038 | NoData
65039 | NoData
65040 | NoData
65041 | NoData
65042 | NoData
65043 | NoData
65044 | NoData
65045 | NoData
65046 | NoData
65047 | NoData
65048 | NoData
65049 | NoData
65050 | NoData
65051 | NoData
65052 | NoData
65053 | NoData
65054 | NoData
65055 | NoData
65056 | NoData
65057 | NoData
65058 | NoData
65059 | NoData
65060 | NoData
65061 | NoData
65062 | NoData
65063 | NoData
65064 | NoData
65065 | NoData
65066 | NoData
65067 | NoData
65068 | NoData
65069 | Obtain F7 (flammable liquids) and K1 (key box)permits.
65070 | Label elevator mainline disconnect switches.
65071 | Label the exterior of the doors leading to the Electrical/Fire Pump room.
65072 | Provide keys for the fire pump, mechanical rooms and elevator fire service keys in the key box.
65073 | NoData
65074 | NoData
65075 | NoData
65076 | NoData
65077 | NoData
65078 | NoData
65079 | NoData
65080 | NoData
65081 | NoData
65082 | NoData
65083 | NoData
65084 | NoData
65085 | NoData
65086 | NoData
65087 | NoData
65088 | NoData
65089 | NO VIOLATIONS TO FACILITY AT THIS TIME
65090 | NoData
65091 | NoData
65092 | NoData
65093 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
65094 | NoData
65095 | LAST INSPECTED 11/2019 - CURRENT ANNUAL INSPECTION REQUIRED. ADDRESS ISSUES NOTED ON YELLOW TAG FROM LAST ANNUAL INSPECTION.
65096 | Post the occupant load.
65097 | Have the emergency lighting tested and repair any inoperable lighting.
65098 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
65099 | NoData
65100 | NoData
65101 | CITATIONS WILL BEWRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT METWITHIN 30 DAYS
65102 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30 CALENDARDAYS
65103 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
65104 | NoData
65105 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIREDIF THE HIGH-RISE DOES NOT HAVE ANY OF THESESYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED)DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30 CALENDAR DAYS
65106 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED
65107 | EVIDENCE OF INCOMPLETE ORNON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONINGSYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRECODE
65108 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE
65109 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY
65110 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIREPROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY ORNON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEMIS RESTORED TO NORMAL OPERATIONAL STATUS
65111 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN
65112 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE
65113 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERAL ALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1
65114 | Take the Fire Warden Certification class online through thefollowing link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottomto click on High-rise Fire Warden CertificationClass.Print out the certificate of completion and keep it in a safeplace where it can be accessed upon demand. REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Riseor Mid-Rise Atruim Certification Training may send attendees to the followingmonthly seminars at no cost. Monthly seminars are available for managementemployees and tenant fire wardens of high-rise buildings who need to becertified. Certificates shall be valid for a period of five years from the dateof training.There is no charge for attending theseseminars. The only cost incurred may be parking fees, if applicable. Manybuildings will have different fire safety features. The building managementfrom each building represented is required to inform its employees and FireWardens of their specific fire safety features to complete the certification. Please note this training is not valid forMid Rise Evacuation Training. For information on mid rise training please visitthe HFD Mid Rise Fire Certication Webpage.Additional training availability information:The Houston Fire Department has set up and implemented a list of all high-risebuildings for Fire Safety Plan approvals. This list was set up to ensure thatpriority is given to buildings that have the greatest need while also providingeach building an equal opportunity. The list of buildings is separated into twogroups based on whether the building is an occupancy where people sleep, suchas hotel, apartments, and condominiums or those buildings where people do notsleep, such as office buildings. Buildings are then sub-grouped by no sprinklersystem, partial sprinkler system, or complete sprinkler systems before sortingby building height. The highest priority building is the residential buildingthat is non-sprinklered, and the tallest in height. Our goal is to provide theneeded services to approve each building within a two-year cycle. Buildingsdesiring to expedite the process also have three additional options. 1. The monthly openhigh-rise certification seminar is for buildings that have requested to send alimited number of fire wardens and building management employees to a classthat is open to all high-rise buildings. The class information is not specificto any particular building and requires building management to supplement thetraining with their building specifics.2. An inspector/instructorin the Life Safety Bureau, Public Education Section - High-rise Fire SafetyPlan Approvals, may be obtained to provide training outside his regular workhours on an overtime basis. This may be done by contacting Diana Cardenas bye-mail at:diana.cardenas@houstontx.gov. This should be done prior to payment of arequired permit fee so that an instructor can be assigned to made contact withthe requesting party, to assist the requesting party with information on theapplication for over-time training and payment of the permit fees, and toschedule a mutually convenient training date.A City of Houston permit fee is required to schedule an inspector/instructor.The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019).3. Having a City of HoustonFire Marshal approved consultant perform the training. The process to receivean approved Fire Safety Plan consist of the three following essential trainingelements conducted by persons, institutions or companies approved by the FireMarshal according to regulations established by the Fire Marshal: aconsultation with building management, an approved certification training forFire Wardens and building employees, and a fire drill supervised by persons,institutions or companies approved by the Fire Marshal.
65115 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS
65116 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL SUBMIT ACOMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINEDFIRE WARDENS
65117 | Concerningfire drills during COVID-19, a link can be found by going to the "Resources" andthen clicking on "Notices"https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/
65118 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR
65119 | MEMBERS OF THE FIRESAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR
65120 | NoData
65121 | Provide signage for rainwater pit under parking garage.Provide documentation and signage for Permeable Grass required for fire access road.Provide signage identifying the number of hydrants inside of complex.Provide signage for FDC according to LSB # 2.5.4.3
65122 | 911 Keyboxes are required at all stairwell discharge doors.
65123 | Provide signs for pump room and elevator control room (shutoff).
65124 | Fire extinguishers are required in the courtyard near the cooking appliances.
65125 | Identify fire hydrants with square blue reflectors.
65126 | Fire Depository Box is required for all midrise buildings.
65127 | Remove combustible storage from all equipment rooms.
65128 | Remove items (bicycles) blocking means of egress.
65129 | Provide documentation for sprinkler system annual and 5 year hydrostatic test. All components of system should have a compliance tag attached.
65130 | Fire Alarm System needs annual, audibility and sensitivity test done.
65131 | NoData
65132 | Provide clearance from electrical panels.
65133 | NoData
65134 | NoData
65135 | NoData
65136 | NoData
65137 | NoData
65138 | NoData
65139 | NoData
65140 | NoData
65141 | NoData
65142 | NoData
65143 | NoData
65144 | NoData
65145 | NoData
65146 | NoData
65147 | NoData
65148 | Mount fire extinguishers every 75ft. in hallway. One in kitchen area.
65149 | Provide forms.
65150 | Post evacuation maps in each classroom. Make each map room specific.
65151 | Provide.
65152 | Label electrical room.
65153 | General cleaning needed.
65154 | NoData
65155 | NoData
65156 | NoData
65157 | 109.2 Owner/occupant responsibility. Correction and abatement of violations of this code shall be the responsibility of the owner. If an occupant creates, or allows to be created, hazardous conditions in violation of this code, the occupant shall be held responsible for the abatement of such hazardous conditions.
65158 | NoData
65159 | NoData
65160 | NoData
65161 | NoData
65162 | NoData
65163 | NoData
65164 | CONTACT INSPECTOR REGINALD WOODS FOR COMPLIANCE: 281-922-2306 REGINALD.WOODS@HOUSTONTX.GOV
65165 | REMOVE WELD ON KEY BOX ON GATE
65166 | NoData
65167 | NoData
65168 | NoData
65169 | NoData
65170 | NoData
65171 | Repair ASAP.
65172 | Clear and maintain aisles.
65173 | Provide fire extinguishers for both tire storage areas.
65174 | Mount the fire extinguishers accordingly.
65175 | Have a licensed fire protection company service and tag the fire extinguishers.
65176 | Clear and maintain access to breaker panel.
65177 | Have yellow tagged sprinkler system corrected and tagged.
65178 | The owner/occupant is responsible for correcting all violations listed in this report.
65179 | Red Tagged Sprinkler system shall be made operational prior to reinspection date, which is November 24, 2020.
65180 | The red tagged sprinkler system shall be corrected prior to follow up inspection on November 24, 2020.
65181 | NoData
65182 | O3 (INDUSTRIAL OVENS) PERMIT EXPIRED 11-13-20.
65183 | NoData
65184 | NoData
65185 | The exceptions listed in the IFC2012.903.2 must be met in order to be considered nonrequired. Provide documentation that confirms the rooms meet or exceed the following: Areas are equipped throughout with an automatic smoke detection system in accordance with Section 907.2 and are separated by 1-hour fire barriers constructed in accordance with Section 707 of the International Building Code or not less than 2-hour horizontal assemblies constructed in accordance with Section 711 of the International Building Code, or both.
65186 | Nonrequired fire protection systems shall be maintained or removed.
65187 | Non-required life safety systems or fire protection systems that no longer functions as originally installed shall be removed or the appearance changed so as not to be mistaken for functioning life safety or fire protection equipment.
65188 | Have a licensed fire protection company repair the red tagged alarm panel and correct any deficiencies.
65189 | NoData
65190 | Please renew the A4, access gate permit.Expired 11/13/20.
65191 | NoData
65192 | NoData
65193 | NoData
65194 | NoData
65195 | Post the occupant load.
65196 | Renew the expired permit.
65197 | Repair the broken exit sign located above the side exit. Ensure the emergency lighting is functioning properly.
65198 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
65199 | NoData
65200 | NoData
65201 | NoData
65202 | NoData
65203 | NoData
65204 | NoData
65205 | NoData
65206 | NoData
65207 | NoData
65208 | NoData
65209 | NoData
65210 | NoData
65211 | NoData
65212 | NoData
65213 | NoData
65214 | NoData
65215 | NoData
65216 | NoData
65217 | Fire hydrant being blocked by steel cable from telephone pole.
65218 | NoData
65219 | NoData
65220 | NoData
65221 | NoData
65222 | NoData
65223 | NoData
65224 | NoData
65225 | NoData
65226 | NoData
65227 | NoData
65228 | NoData
65229 | NoData
65230 | NoData
65231 | NoData
65232 | NoData
65233 | NoData
65234 | Test emergency illumination and provide documentation of test.
65235 | Remove obstructions in front of the class K fire extinguisher located in the kitchen.
65236 | Replace the ceiling tiles after the roof is repaired.
65237 | Provide address numbers on the front of the business.
65238 | Ensure the rear exit is maintained clear of storage.
65239 | Clear and maintain space in front of breaker panels.
65240 | Repair the hardware on the rear exit door that requires excessive force to open.
65241 | NoData
65242 | NoData
65243 | NoData
65244 | for informational purpose only
65245 | for informational purpose only
65246 | All items on the map shall be color-coded:1) You are here2) Primary Route3) Secondary Route4) Exit Exterior5) Place of Assembly OutsideEach map shall be posted in relation to where the occupant is standing.
65247 | NoData
65248 | NoData
65249 | NoData
65250 | NoData
65251 | NoData
65252 | NoData
65253 | NoData
65254 | NoData
65255 | NoData
65256 | NoData
65257 | NoData
65258 | NoData
65259 | NoData
65260 | NoData
65261 | NoData
65262 | NoData
65263 | NoData
65264 | NoData
65265 | NoData
65266 | NoData
65267 | NoData
65268 | NoData
65269 | NoData
65270 | NoData
65271 | NoData
65272 | NoData
65273 | NoData
65274 | NoData
65275 | NoData
65276 | NoData
65277 | NoData
65278 | NoData
65279 | NoData
65280 | NoData
65281 | NoData
65282 | NoData
65283 | NoData
65284 | NoData
65285 | NoData
65286 | NoData
65287 | NoData
65288 | NoData
65289 | NoData
65290 | NoData
65291 | NoData
65292 | NoData
65293 | NoData
65294 | NoData
65295 | NoData
65296 | NoData
65297 | NoData
65298 | NoData
65299 | NoData
65300 | NoData
65301 | Repair or replace the emergency illumination on the exit signs.
65302 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
65303 | Provide filler plates for the openings in the breaker panel.
65304 | Provide address numbers on the front of the business.
65305 | Ensure the vent hood is cleaned before the end of 11/2020. Provide documentation of the vent hood suppression system being serviced within the last 6 months or have the vent hood suppression system serviced and tagged.
65306 | Provide documentation of the fire extinguishers being serviced within the last year or have the fire extinguishers serviced and tagged. Replace the used fire extinguisher.
65307 | NoData
65308 | NoData
65309 | Ensure locking bar is removed from the rear exit while the building is occupied.
65310 | Repair the inoperable emergency illumination.
65311 | NoData
65312 | Renew the assembly permit.
65313 | Repair the inoperable emergency illumination on the exit signs.
65314 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
65315 | Clear and maintain clearance in front of the breaker panels.
65316 | Repair the rear exit door.
65317 | CITATIONS WILL BEWRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT METWITHIN 30 DAYS
65318 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30CALENDAR DAYS
65319 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
65320 | NoData
65321 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIREDIF THE HIGH-RISE DOES NOT HAVE ANY OF THESESYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED)DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30 CALENDAR DAYS
65322 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED
65323 | EVIDENCE OF INCOMPLETE ORNON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONINGSYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRECODE
65324 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE
65325 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY
65326 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY AREPLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT ORSERVICE TO THE OWNER/OCCUPANT AND TO THE JURISDICTION – BY PHONE 713.884.3143AND EMAIL AT HFD.DISPATCH3@houstontx.gov THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THESYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS
65327 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN
65328 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE
65329 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERAL ALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1
65330 | Take the Fire Warden Certification class online through thefollowing link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottomto click on High-rise Fire Warden CertificationClass.Print out the certificate of completion and keep it in a safeplace where it can be accessed upon demand. REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Riseor Mid-Rise Atruim Certification Training may send attendees to the followingmonthly seminars at no cost. Monthly seminars are available for managementemployees and tenant fire wardens of high-rise buildings who need to becertified. Certificates shall be valid for a period of five years from the dateof training.There is no charge for attending theseseminars. The only cost incurred may be parking fees, if applicable. Manybuildings will have different fire safety features. The building managementfrom each building represented is required to inform its employees and FireWardens of their specific fire safety features to complete the certification. Please note this training is not valid forMid Rise Evacuation Training. For information on mid rise training please visitthe HFD Mid Rise Fire Certication Webpage.Additional training availability information:The Houston Fire Department has set up and implemented a list of all high-risebuildings for Fire Safety Plan approvals. This list was set up to ensure thatpriority is given to buildings that have the greatest need while also providingeach building an equal opportunity. The list of buildings is separated into twogroups based on whether the building is an occupancy where people sleep, suchas hotel, apartments, and condominiums or those buildings where people do notsleep, such as office buildings. Buildings are then sub-grouped by no sprinklersystem, partial sprinkler system, or complete sprinkler systems before sortingby building height. The highest priority building is the residential buildingthat is non-sprinklered, and the tallest in height. Our goal is to provide theneeded services to approve each building within a two-year cycle. Buildingsdesiring to expedite the process also have three additional options. 1. The monthly openhigh-rise certification seminar is for buildings that have requested to send alimited number of fire wardens and building management employees to a classthat is open to all high-rise buildings. The class information is not specificto any particular building and requires building management to supplement thetraining with their building specifics.2. An inspector/instructorin the Life Safety Bureau, Public Education Section - High-rise Fire SafetyPlan Approvals, may be obtained to provide training outside his regular workhours on an overtime basis. This may be done by contacting Diana Cardenas bye-mail at:diana.cardenas@houstontx.gov. This should be done prior to payment of arequired permit fee so that an instructor can be assigned to made contact withthe requesting party, to assist the requesting party with information on theapplication for over-time training and payment of the permit fees, and toschedule a mutually convenient training date.A City of Houston permit fee is required to schedule an inspector/instructor.The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019).3. Having a City of HoustonFire Marshal approved consultant perform the training. The process to receivean approved Fire Safety Plan consist of the three following essential trainingelements conducted by persons, institutions or companies approved by the FireMarshal according to regulations established by the Fire Marshal: aconsultation with building management, an approved certification training forFire Wardens and building employees, and a fire drill supervised by persons,institutions or companies approved by the Fire Marshal.
65331 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS
65332 | SUBMIT ACOMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINEDFIRE WARDENS HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL
65333 | Concerningfire drills during COVID-19, a link can be found by going to the "Resources" andthen clicking on "Notices"https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/
65334 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR
65335 | MEMBERS OF THEFIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR
65336 | NoData
65337 | NoData
65338 | NoData
65339 | Unpermitted and/or unapproved gate barriers must be corrected for emergency access
65340 | Vent Hoods require 6 month cleaning by a certified company. Cleaning of vent hoods by employees is not acceptable
65341 | P2 required F7 required
65342 | P2 required Permit can be obtained at 1002 Washington Ave (HOUSTON PERMIT CENTER)F7 required Permit can be obtained at 1002 Washington Ave (HOUSTON PERMIT CENTER)First Time permits are not available online. Customer must fill out application online or at facility for First Time Fire Prevention Permits
65343 | Facility requires assembly and combustible waste permits. Neither permit was posted and customer does have knowledge of any permits.
65344 | Vent Hoods require 6 month cleaning by a certified company. Cleaning of vent hoods by employees is not acceptable
65345 | Vent Hoods require 6 month cleaning by a certified company. Cleaning of vent hoods by employees is not acceptable Certificate of occupancy shows an occupant load of 70. Label shall be affixed at entrance of facility indicating occupant load.Facility needs a 5 year gas test by a certified plumber. Plumber must obtain a permit before work can be performed.System does not show record of Gas test for the past 10 years.
65346 | NoData
65347 | PROVIDE EVIDENCE OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP THIS INFORMATION ON SITE PROVIDE DOCUMENTATION OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP POSTED ON SITE WITH ALL OTHER PERMITS, WITHIN THE ELEVATOR CAR OR WITHIN 10 FEET OF THE CALL BUTTONS
65348 | HOUSEKEEPING IS REQUIRED IN THE 1ST FLOOR ELEVATOR/MECHANICAL ROOM
65349 | SUPPLY THE CODE FOR ENTRY IN THE 911 BOX SPPLY A SIGN STATING "911 BOX 9@CORNER OF MAIN AND POLK) HAS CODE FOR ACCESS
65350 | FIRE EXTINGUISHERS ARE REQUIRED IN ALL ELEVATOR ROOMS, ELECTRICAL ROOMS, IT ROOMS, GENERATOR ROOMS, MECHANICAL ROOMS AND WHERE FLAMMABLES ARE STORED PROVIDE FIRE EXTINGUISHERS IN THE EQUIPMENT ROOM (AT EACH DOOR) AND IN THE BREAK ROOM ON THE SECOND FLOOR
65351 | PROVIDE COVERS MECHANICAL/ELECTRICAL ROOMS ON THE 1ST AND 2ND FLOORS FOR OPEN JUNCTION BOXES
65352 | THE BACK EXIT DOORS WHICH ARE LOCATED IN THE LOADING DOCK MUST BE IDENTIFIED AND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS
65353 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOST RECENT TEST EXIT SIGNS WERE FOUND OUT/NOT ILLUMINATED ON THE 2ND FLOOR NEAR THE MECHANICAL/ELECTRICAL ROOM - REPAIR OR REPLACE THEM IMMEDIATELY
65354 | PROVIDE ADDITIONAL EXIT SIGNS ON THE WALL IN THE STAIRWELL ON THE GROUND FLOOR (LEAVING THE CLASS AREA) TO DETER OCCUPANTS FROM CONTINUING BACK TO THE STAIRS AND AWAY FROM THE ACTUAL EXIT
65355 | NoData
65356 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL
65357 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY
65358 | NoData
65359 | PROVIDE A UL APPROVED RED CAN IN THE ELEVATOR ROOM AND ENSURE IT IS EMPTIED DAILY
65360 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIRE A LETTER - PROVIDE A PHOTOCOPY OF THESE PERMITS. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - REQUIRED IF BOILER ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS
65361 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED
65362 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE MECHANICAL/ELECTRICAL ROOMS ON THE 1ST AND 2ND FLOORS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR
65363 | NO 'PIGGYBACKING' OF MULTIPLE EXTENSION CORDS ALLOWED - USE ONLY ONE UL APPROVED, SURGE-PROTECTED EXTENSION CORD FROM THE WALL TO THE APPLIANCE OR APPLIANCES IN THE MASS CHALLENGE ROOM UNDER THE TABLE AND IN OFFICES NEARBY -
65364 | PERMITS THE INSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS: Key Box Permit - Flammable and Combustible Permit - Fire Alarm Permit - Elevator Operating Permit - Boiler Permit - Other - Assembly, Access Gates, Batteries, etc. - Certificate of Occupancies - Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS
65365 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION
65366 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE
65367 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE
65368 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENT APPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN
65369 | SUPPLY A LETTER INDICATING 1313 MAIN IS IN COMPLIANCE WITH APPENDIX J
65370 | THE ELECTRICAL ROOM ON THE CLAY SIDE MUST BE IDENTIFIED AND LABELED AS SUCH
65371 | PROVIDE SIGN ON THE DOOR OF THE EQUIPMENT ROOM (FROM THE GARAGE AND FROM THE TENANT SIDE) TO INDICATE THE PRESENCE OF DIESEL
65372 | SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED
65373 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
65374 | NO CITY MAG LOCK STICKER WAS FOUND ON THE LOADING DOCK DOOR - ENSURE IT IS TESTED AND STICKERED EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE
65375 | THE LOCATION OF THE ELEVATOR ROOM MUST BE IDENTIFIED AND LABELED AS SUCH ON THE DOOR AND ALL DOORS LEADING TO IT THE AIR HANDLER ROOM DOOR MUST ALSO STATE "MECHANICAL ROOM" AND "ELECTRICAL ROOM"
65376 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRE CODE OFFICIAL IS DEPENDENT UPON SUCCESSFUL COMPLETION OF THREE COMPONENTS - CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF A SUPERVISED FIRE DRILL
65377 | EACH MEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR
65378 | ATTENDANCE AT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH- RISE FIRE WARDENS
65379 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS
65380 | PROVIDE A KEY TO THE FIRE ALARM PANEL OF 1313 MAIN IN THE FIRE DEPOSITORY BOX AND BEHIND THE FRONT DESK; SUPPLY A LABEL INDICATING THE LOCATION OF THE KEYS ON THE FIRE ALARM PANEL
65381 | SUBMIT A COMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS
65382 | NoData
65383 | MANICURE THE LANDSCAPING TO REVEAL THE HIDDEN HYDRANT ON MAIN STREET ENSURE LANDSCAPING DOES NOT OBSCURE FIRE DEPARTMENT ELEMENTS AND/OR FIRE HYDRANTS
65384 | REMOVE AND DISCONTINUE USE OF UNAPPROVED EXTENSION CORD IN THE MASS CHALLENGE ROOM UNDER THE TABLE AND IN OFFICES NEARBY - ONLY UL APPROVED, SURGE PROTECTED CORDS ARE SAFE FOR TEMPORARY USE
65385 | FDC SIGN MUST BE UPDATED - REVIEW LSB #2 SECTION 2.5.4.3 TO REVISE THE FDC SIGN WITH NECESSARY CORRECTIONS AND ENSURE ALL PERTINENT INFORMATION IS INCLUDED Approved signs of weather-resistant materials, with not less than one inch high legible block lettering on a highly contrasting background, shall be placed on or immediately adjacent to all fire department connections and provide the following information: 1. Type of system - STANDPIPE, SPRINKLER, STANDPIPE / SPRINKLER, DRY PIPE SPRINKLER, etc. 2. Which building or structure, or what portion, zone, and floors of the building or structure the FDC serve. i. Ex: FLOORS B1 - 12; LEVELS 1 - 8; HIGH ZONE FLRS 21 - 40; etc. 3. On standpipe and combination standpipe/sprinkler systems - whether there are pressure regulating valves (PRV) or pressure reducing devices (PRD) on the system. System pressures shall also be indicated on all wet standpipe and combination standpipe/sprinkler systems. Examples: NO PRV/PRD (System Pres. 100 PSI) PRD Levels 1 - 7 (System Pres. 150 PSI) PRV Floors 1 - 10 (System Pres. 175 PSI)
65386 | THE LOCK-OUT/TAG-OUT EQUIPMENT AND SETS (SET = 1 LOCK + 1 TAG) MUST BE READILY ACCESSIBLE IN THE ELEVATOR ROOM AND PROPERLY LABELED: PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS
65387 | NoData
65388 | ALL OCCUPANTS OF THE BUILDING SHALL PARTICIPATE IN THE FIRE DRILLS AS REQUIRED BY THE CODE OFFICIAL AND THE FIRE CODE
65389 | APPROVAL OF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFUL COMPLETION OF SEVERALALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF A COMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS LISTED IN 18.4.1
65390 | REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Rise or Mid-Rise Atruim Certification Training may send attendees to the following monthly seminars at no cost. Monthly seminars are available for management employees and tenant fire wardens of high-rise buildings who need to be certified. Certificates shall be valid for a period of five years from the date of training. There is no charge for attending these seminars. The only cost incurred may be parking fees, if applicable. Many buildings will have different fire safety features. The building management from each building represented is required to inform its employees and Fire Wardens of their specific fire safety features to complete the certification. Please note this training is not valid for Mid Rise Evacuation Training. For information on mid-rise training please visit the HFD Mid Rise Fire Certification Webpage. Additional training availability information: The Houston Fire Department has set up and implemented a list of all high- rise buildings for Fire Safety Plan approvals. This list was set up to ensure that priority is given to buildings that have the greatest need while also providing each building an equal opportunity. The list of buildings is separated into two groups based on whether the building is an occupancy where people sleep, such as hotel, apartments, and condominiums or those buildings where people do not sleep, such as office buildings. Buildings are then sub- grouped by no sprinkler system, partial sprinkler system, or complete sprinkler systems before sorting by building height. The highest priority building is the residential building that is non-sprinklered, and the tallest in height. Our goal is to provide the needed services to approve each building within a two-year cycle. Buildings desiring to expedite the process also have three additional options. The monthly open high-rise certification seminar is for buildings that have requested to send a limited number of fire wardens and building management employees to a class that is open to all high-rise buildings. The class information is not specific to any particular building and requires building management to supplement the training with their building specifics. An inspector/instructor in the Life Safety Bureau, Public Education Section - High-rise Fire Safety Plan Approvals, may be obtained to provide training outside his regular work hours on an overtime basis. This may be done by contacting Diana Cardenas by e-mail at: diana.cardenas@houstontx.gov. This should be done prior to payment of a required permit fee so that an instructor can be assigned to made contact with the requesting party, to assist the requesting party with information on the application for over-time training and payment of the permit fees, and to schedule a mutually convenient training date. A City of Houston permit fee is required to schedule an inspector/instructor. The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019). Having a City of Houston Fire Marshal approved consultant perform the training. The process to receive an approved Fire Safety Plan consist of the three following essential training elements conducted by persons, institutions or companies approved by the Fire Marshal according to regulations established by the Fire Marshal: a consultation with building management, an approved certification training for Fire Wardens and building employees, and a fire drill supervised by persons, institutions or companies approved by the Fire Marshal. THE CERTIFICATE OF COMPLETION OF FIRE WARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE
65391 | REMOVE ALL EVIDENCE OF INACTIVE/NON FUNCTIONING (TELEPHONE AND TELEPHONE BOX AT THE LOADING DOCK DOOR) OR REPAIR IT TO ENABLE A FULLY FUNCTIONAL SYSTEM
65392 | NoData
65393 | PROVIDE 2 ELEVATOR INDEPENDENT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX WHERE 24 HOUR SECURITY IS PROVIDED, INDEPENDANT SERVICE KEYS MAY BE KEPT SECURED AT THE SECURITY CONSOL AND MADE READILY AVAILABLE TO THE FIRE DEPARTMENT UPON REQUEST - A NOTE OR SIGN IN THE FCR REGUARDING THE ALTERNATE PLACEMENT IS SUGGESTED
65394 | THE FIRE ALARM MUST BE TESTED, INSPECTED, TAGGED, MAINTAINED AND FULLY/PROPERLY FUNCTIONING - THE FIRE ALARM WAS YELLOW-TAGGED ON 06/18/19 CALL CERTIFIED TESTING COMPANY TO CONDUCT ANNUAL INSPECTION OF THE SYSTEM PROVIDE A KEY IN A CONVENIENT LOCATION FOR THE FIRE ALARM PANEL AND LABEL THE PANEL INDICATION THE LOCATION OF THE KEY
65395 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS
65396 | NoData
65397 | NoData
65398 | FIX ALARM MALFUNCTION.
65399 | NoData
65400 | PROVIDE EVIDENCE OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP THIS INFORMATION ON SITE PROVIDE DOCUMENTATION OF ANNUAL ELEVATOR INSPECTION AND PERMIT - KEEP POSTED ON SITE WITH ALL OTHER PERMITS, WITHIN THE ELEVATOR CAR OR WITHIN 10 FEET OF THE CALL BUTTONS
65401 | HOUSEKEEPING IS REQUIRED IN THE 1ST FLOOR ELEVATOR/MECHANICAL ROOM
65402 | SUPPLY THE CODE FOR ENTRY IN THE 911 BOX SPPLY A SIGN STATING "911 BOX 9@CORNER OF MAIN AND POLK) HAS CODE FOR ACCESS
65403 | FIRE EXTINGUISHERS ARE REQUIRED IN ALL ELEVATOR ROOMS, ELECTRICAL ROOMS, IT ROOMS, GENERATOR ROOMS, MECHANICAL ROOMS AND WHERE FLAMMABLES ARE STORED PROVIDE FIRE EXTINGUISHERS IN THE EQUIPMENT ROOM (AT EACH DOOR) AND IN THE BREAK ROOM ON THE SECOND FLOOR
65404 | PROVIDE COVERS MECHANICAL/ELECTRICAL ROOMS ON THE 1ST AND 2ND FLOORS FOR OPEN JUNCTION BOXES
65405 | THE BACK EXIT DOORS WHICH ARE LOCATED IN THE LOADING DOCK MUST BE IDENTIFIED AND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS
65406 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOST RECENT TEST EXIT SIGNS WERE FOUND OUT/NOT ILLUMINATED ON THE 2ND FLOOR NEAR THE MECHANICAL/ELECTRICAL ROOM - REPAIR OR REPLACE THEM IMMEDIATELY
65407 | PROVIDE ADDITIONAL EXIT SIGNS ON THE WALL IN THE STAIRWELL ON THE GROUND FLOOR (LEAVING THE CLASS AREA) TO DETER OCCUPANTS FROM CONTINUING BACK TO THE STAIRS AND AWAY FROM THE ACTUAL EXIT
65408 | NoData
65409 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL
65410 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY
65411 | NoData
65412 | PROVIDE A UL APPROVED RED CAN IN THE ELEVATOR ROOM AND ENSURE IT IS EMPTIED DAILY
65413 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIRE A LETTER - PROVIDE A PHOTOCOPY OF THESE PERMITS. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - REQUIRED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - REQUIRED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - REQUIRED " Electronic Locks -Semi Annual - REQUIRED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - REQUIRED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - REQUIRED IF BOILER ON SITE " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - REQUIRED IF GAS ON SITE " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS
65414 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE). CITATIONS ARE ISSUED AFTER 2 REINSPECTION FEES ARE CHARGED
65415 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE MECHANICAL/ELECTRICAL ROOMS ON THE 1ST AND 2ND FLOORS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR
65416 | NO 'PIGGYBACKING' OF MULTIPLE EXTENSION CORDS ALLOWED - USE ONLY ONE UL APPROVED, SURGE-PROTECTED EXTENSION CORD FROM THE WALL TO THE APPLIANCE OR APPLIANCES IN THE MASS CHALLENGE ROOM UNDER THE TABLE AND IN OFFICES NEARBY -
65417 | PERMITS THE INSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS: Key Box Permit - Flammable and Combustible Permit - Fire Alarm Permit - Elevator Operating Permit - Boiler Permit - Other - Assembly, Access Gates, Batteries, etc. - Certificate of Occupancies - Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS
65418 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION
65419 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE
65420 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE
65421 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENT APPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN
65422 | SUPPLY A LETTER INDICATING 1313 MAIN IS IN COMPLIANCE WITH APPENDIX J
65423 | THE ELECTRICAL ROOM ON THE CLAY SIDE MUST BE IDENTIFIED AND LABELED AS SUCH
65424 | PROVIDE SIGN ON THE DOOR OF THE EQUIPMENT ROOM (FROM THE GARAGE AND FROM THE TENANT SIDE) TO INDICATE THE PRESENCE OF DIESEL
65425 | SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED
65426 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
65427 | NO CITY MAG LOCK STICKER WAS FOUND ON THE LOADING DOCK DOOR - ENSURE IT IS TESTED AND STICKERED EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE
65428 | THE LOCATION OF THE ELEVATOR ROOM MUST BE IDENTIFIED AND LABELED AS SUCH ON THE DOOR AND ALL DOORS LEADING TO IT THE AIR HANDLER ROOM DOOR MUST ALSO STATE "MECHANICAL ROOM" AND "ELECTRICAL ROOM"
65429 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRE CODE OFFICIAL IS DEPENDENT UPON SUCCESSFUL COMPLETION OF THREE COMPONENTS - CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF A SUPERVISED FIRE DRILL
65430 | EACH MEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR
65431 | ATTENDANCE AT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH- RISE FIRE WARDENS
65432 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 30 DAYS
65433 | PROVIDE A KEY TO THE FIRE ALARM PANEL OF 1313 MAIN IN THE FIRE DEPOSITORY BOX AND BEHIND THE FRONT DESK; SUPPLY A LABEL INDICATING THE LOCATION OF THE KEYS ON THE FIRE ALARM PANEL
65434 | SUBMIT A COMPLETED FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS
65435 | NoData
65436 | MANICURE THE LANDSCAPING TO REVEAL THE HIDDEN HYDRANT ON MAIN STREET ENSURE LANDSCAPING DOES NOT OBSCURE FIRE DEPARTMENT ELEMENTS AND/OR FIRE HYDRANTS
65437 | REMOVE AND DISCONTINUE USE OF UNAPPROVED EXTENSION CORD IN THE MASS CHALLENGE ROOM UNDER THE TABLE AND IN OFFICES NEARBY - ONLY UL APPROVED, SURGE PROTECTED CORDS ARE SAFE FOR TEMPORARY USE
65438 | FDC SIGN MUST BE UPDATED - REVIEW LSB #2 SECTION 2.5.4.3 TO REVISE THE FDC SIGN WITH NECESSARY CORRECTIONS AND ENSURE ALL PERTINENT INFORMATION IS INCLUDED Approved signs of weather-resistant materials, with not less than one inch high legible block lettering on a highly contrasting background, shall be placed on or immediately adjacent to all fire department connections and provide the following information: 1. Type of system - STANDPIPE, SPRINKLER, STANDPIPE / SPRINKLER, DRY PIPE SPRINKLER, etc. 2. Which building or structure, or what portion, zone, and floors of the building or structure the FDC serve. i. Ex: FLOORS B1 - 12; LEVELS 1 - 8; HIGH ZONE FLRS 21 - 40; etc. 3. On standpipe and combination standpipe/sprinkler systems - whether there are pressure regulating valves (PRV) or pressure reducing devices (PRD) on the system. System pressures shall also be indicated on all wet standpipe and combination standpipe/sprinkler systems. Examples: NO PRV/PRD (System Pres. 100 PSI) PRD Levels 1 - 7 (System Pres. 150 PSI) PRV Floors 1 - 10 (System Pres. 175 PSI)
65439 | THE LOCK-OUT/TAG-OUT EQUIPMENT AND SETS (SET = 1 LOCK + 1 TAG) MUST BE READILY ACCESSIBLE IN THE ELEVATOR ROOM AND PROPERLY LABELED: PROVIDE AT LEAST ONE (1) LOCK-OUT/TAG-OUT SET FOR 1 TO 3 ELEVATORS
65440 | NoData
65441 | ALL OCCUPANTS OF THE BUILDING SHALL PARTICIPATE IN THE FIRE DRILLS AS REQUIRED BY THE CODE OFFICIAL AND THE FIRE CODE
65442 | APPROVAL OF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFUL COMPLETION OF SEVERALALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF A COMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIRE WARDENS LISTED IN 18.4.1
65443 | REGISTER FOR FIRE WARDEN TRAINING AT https://houstontx.gov/fire/HFMO/highrisecert.html Any Building Manager in need of High-Rise or Mid-Rise Atruim Certification Training may send attendees to the following monthly seminars at no cost. Monthly seminars are available for management employees and tenant fire wardens of high-rise buildings who need to be certified. Certificates shall be valid for a period of five years from the date of training. There is no charge for attending these seminars. The only cost incurred may be parking fees, if applicable. Many buildings will have different fire safety features. The building management from each building represented is required to inform its employees and Fire Wardens of their specific fire safety features to complete the certification. Please note this training is not valid for Mid Rise Evacuation Training. For information on mid-rise training please visit the HFD Mid Rise Fire Certification Webpage. Additional training availability information: The Houston Fire Department has set up and implemented a list of all high- rise buildings for Fire Safety Plan approvals. This list was set up to ensure that priority is given to buildings that have the greatest need while also providing each building an equal opportunity. The list of buildings is separated into two groups based on whether the building is an occupancy where people sleep, such as hotel, apartments, and condominiums or those buildings where people do not sleep, such as office buildings. Buildings are then sub- grouped by no sprinkler system, partial sprinkler system, or complete sprinkler systems before sorting by building height. The highest priority building is the residential building that is non-sprinklered, and the tallest in height. Our goal is to provide the needed services to approve each building within a two-year cycle. Buildings desiring to expedite the process also have three additional options. The monthly open high-rise certification seminar is for buildings that have requested to send a limited number of fire wardens and building management employees to a class that is open to all high-rise buildings. The class information is not specific to any particular building and requires building management to supplement the training with their building specifics. An inspector/instructor in the Life Safety Bureau, Public Education Section - High-rise Fire Safety Plan Approvals, may be obtained to provide training outside his regular work hours on an overtime basis. This may be done by contacting Diana Cardenas by e-mail at: diana.cardenas@houstontx.gov. This should be done prior to payment of a required permit fee so that an instructor can be assigned to made contact with the requesting party, to assist the requesting party with information on the application for over-time training and payment of the permit fees, and to schedule a mutually convenient training date. A City of Houston permit fee is required to schedule an inspector/instructor. The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019). Having a City of Houston Fire Marshal approved consultant perform the training. The process to receive an approved Fire Safety Plan consist of the three following essential training elements conducted by persons, institutions or companies approved by the Fire Marshal according to regulations established by the Fire Marshal: a consultation with building management, an approved certification training for Fire Wardens and building employees, and a fire drill supervised by persons, institutions or companies approved by the Fire Marshal. THE CERTIFICATE OF COMPLETION OF FIRE WARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE
65444 | REMOVE ALL EVIDENCE OF INACTIVE/NON FUNCTIONING (TELEPHONE AND TELEPHONE BOX AT THE LOADING DOCK DOOR) OR REPAIR IT TO ENABLE A FULLY FUNCTIONAL SYSTEM
65445 | NoData
65446 | PROVIDE 2 ELEVATOR INDEPENDENT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX WHERE 24 HOUR SECURITY IS PROVIDED, INDEPENDANT SERVICE KEYS MAY BE KEPT SECURED AT THE SECURITY CONSOL AND MADE READILY AVAILABLE TO THE FIRE DEPARTMENT UPON REQUEST - A NOTE OR SIGN IN THE FCR REGUARDING THE ALTERNATE PLACEMENT IS SUGGESTED
65447 | THE FIRE ALARM MUST BE TESTED, INSPECTED, TAGGED, MAINTAINED AND FULLY/PROPERLY FUNCTIONING - THE FIRE ALARM WAS YELLOW-TAGGED ON 06/18/19 CALL CERTIFIED TESTING COMPANY TO CONDUCT ANNUAL INSPECTION OF THE SYSTEM PROVIDE A KEY IN A CONVENIENT LOCATION FOR THE FIRE ALARM PANEL AND LABEL THE PANEL INDICATION THE LOCATION OF THE KEY
65448 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS
65449 | NoData
65450 | NoData
65451 | NoData
65452 | NoData
65453 | NoData
65454 | NoData
65455 | NoData
65456 | NoData
65457 | NoData
65458 | NoData
65459 | NoData
65460 | NoData
65461 | NoData
65462 | NoData
65463 | NoData
65464 | NoData
65465 | NoData
65466 | NoData
65467 | NoData
65468 | NoData
0 | NoData
1 | P2 PERMIT EXPIRED
2 | NoData
3 | Apply for keybox and fire alarm permit.
4 | NoData
5 | NoData
6 | NoData
7 | NoData
8 | NoData
9 | NoData
10 | NoData
11 | NoData
12 | NoData
13 | NoData
14 | NoData
15 | NoData
16 | NoData
17 | NoData
18 | NoData
19 | NoData
20 | NoData
21 | NoData
22 | NoData
23 | NoData
24 | NoData
25 | NoData
26 | NoData
27 | NoData
28 | NoData
29 | NoData
30 | NoData
31 | NoData
32 | NoData
33 | NoData
34 | NoData
35 | NoData
36 | NoData
37 | NoData
38 | NoData
39 | NoData
40 | NoData
41 | NoData
42 | NoData
43 | NoData
44 | NoData
45 | NoData
46 | NoData
47 | NoData
48 | NoData
49 | NoData
50 | NoData
51 | NoData
52 | NoData
53 | NoData
54 | NoData
55 | NoData
56 | NoData
57 | NoData
58 | NoData
59 | NoData
60 | NoData
61 | NoData
62 | NoData
63 | NoData
64 | NoData
65 | NoData
66 | NoData
67 | NoData
68 | NoData
69 | NoData
70 | NoData
71 | NoData
72 | NoData
73 | NoData
74 | NoData
75 | NoData
76 | NoData
77 | NoData
78 | NoData
79 | NoData
80 | NoData
81 | NoData
82 | NoData
83 | NoData
84 | NoData
85 | NoData
86 | NoData
87 | NoData
88 | NoData
89 | NoData
90 | NoData
91 | NoData
92 | NoData
93 | NoData
94 | NoData
95 | NoData
96 | NoData
97 | NoData
98 | NoData
99 | NoData
100 | NoData
101 | NoData
102 | NoData
103 | NoData
104 | NoData
105 | NoData
106 | NoData
107 | NoData
108 | NoData
109 | NoData
110 | NoData
111 | NoData
112 | NoData
113 | NoData
114 | NoData
115 | NoData
116 | NoData
117 | NoData
118 | NoData
119 | NoData
120 | NoData
121 | NoData
122 | NoData
123 | NoData
124 | NoData
125 | NoData
126 | NoData
127 | NoData
128 | NoData
129 | NoData
130 | NoData
131 | NoData
132 | NoData
133 | NoData
134 | NoData
135 | NoData
136 | NoData
137 | NoData
138 | NoData
139 | NoData
140 | NoData
141 | NoData
142 | NoData
143 | NoData
144 | NoData
145 | NoData
146 | NoData
147 | NoData
148 | NoData
149 | ALL FIRE EXTINGUISHERS SHALL BE INSPECTED AND TAGGED BY A LICENSED FIRE PROTECTION EQUIPMENT COMPANY "ANNUALLY".
150 | MOUNT FIRE EXTINGUISHERS SO THAT THEY ARE NOT HIGHER THAN 5FT AND NO LOWER THAN 4 INCHES FROM THE FLOOR.
151 | ADD 2 FIRE EXTINGUISHERS WITH A MINIMUM FIRE RATING OF 2A-10B:C INSIDE WAREHOUSE. 1 FIRE EXTINGUISHER IS REQUIRED INSIDE AND 2 WITHIN WAREHOUSE.
152 | NoData
153 | NoData
154 | NoData
155 | NoData
156 | OBTAIN AND POST THE FOLLOWING PERMITS: -GATE PERMIT (A4) -911 KEYBOX PERMIT (K1)
157 | NoData
158 | NoData
159 | HAVE A LICENSED FIRE PROTECTION COMPANY CORRECT THE RED TAGGED FIRE ALARM PANEL.
160 | HAVE ALL FIRE EXTINGUISHERS INSPECTED AND TAGGED BY AN APPROVED LICENSED FIRE PROTECTION EQUIPMENT COMPANY.
161 | FIRE EXTINGUISHERS ARE REQUIRED TO BE LOCATED IN THE OFFICE AND WAREHOUSE.
162 | POST CERTIFICATE OF OCCUPANCY IN A PLACE THAT IS READILY AVAILABLE FOR INSPECTION.
163 | NoData
164 | NoData
165 | NoData
166 | NoData
167 | 109.2 Owner/occupant responsibility. Correction and abatement of violations of this code shall be the responsibility of the owner. If an occupant creates, or allows to be created, hazardous conditions in violation of this code, the occupant shall be held responsible for the abatement of such hazardous conditions.
168 | 604.2.3 Exit signs. Emergency power shall be provided for exit signs in accordance with Section 1011.6.3.Compliance: 30 calendar days.
169 | NoData
170 | NoData
171 | NoData
172 | NoData
173 | NoData
174 | NoData
175 | Provide proof of test
176 | Have all Fire Doors Inspected by a Certified Door Company to the NFPA 80 standard.
177 | Have all Fire Doors Inspected by a Certified Door Company to the NFPA 80 standard.
178 | NoData
179 | NoData
180 | NoData
181 | NoData
182 | NoData
183 | NoData
184 | Fire Alarm panels do not have the required tags:Initial Installation TagInstallation CertificateAnnual Inspection Tag
185 | Fire Sprinklers Do not have Current Tags:Annual TagSprinkler Data Plate is missing
186 | FDS signs do not have the required information.
187 | Fire Extinguishers are out of date or missing annual tag.
188 | Install Key Boxes on all secured exterior exits/entrances and place access keys/fobs in the boxes.
189 | Place a Fire Depository Box as required by LSB #6Place all required information and keys in the Fire Depository Box as per LSB #6
190 | Obtain an Access Gate PermitSubmit Plans to Inspector Arnt 713-503-5949
191 | Obtain a Key Box/Fire Depository Box Permit
192 | Maintain and Update the Building File Check List. Comply with all required tests as they come due.
193 | NoData
194 | Obtain a P2 Places of Assembly Permit for the assembly places in excess of 49 maximum occupant load.
195 | Post the maximum occupant load on all areas of Assembly.
196 | NoData
197 | NoData
198 | NoData
199 | NoData
200 | NoData
201 | Replace the light fixture cover located in the workroom.
202 | Make all code violation corrections prior to the compliance date noted on page 1 of the inspection report. Notify the inspecting fire code official when all corrections have been made.
203 | Provide documentation for a current / updated Fire Alarm System Audibility Test. These test are performed every 3 years.
204 | NoData
205 | NoData
206 | NoData
207 | NoData
208 | NoData
209 | NoData
210 | NoData
211 | NoData
212 | NoData
213 | NoData
214 | NoData
215 | NoData
216 | NoData
217 | NoData
218 | NoData
219 | NoData
220 | NoData
221 | NoData
222 | NoData
223 | NoData
224 | Oct-20
225 | Jun-20
226 | NoData
227 | NoData
228 | NoData
229 | NoData
230 | NoData
231 | NoData
232 | NoData
233 | NoData
234 | NoData
235 | NoData
236 | NoData
237 | NoData
238 | NoData
239 | NoData
240 | NoData
241 | NoData
242 | NoData
243 | NoData
244 | NoData
245 | NoData
246 | NoData
247 | NoData
248 | NoData
249 | NoData
250 | NoData
251 | NoData
252 | NoData
253 | NoData
254 | NoData
255 | NoData
256 | NoData
257 | NoData
258 | NoData
259 | NoData
260 | NoData
261 | NoData
262 | NoData
263 | NoData
264 | NoData
265 | NoData
266 | NoData
267 | NoData
268 | NoData
269 | NoData
270 | NoData
271 | NoData
272 | NoData
273 | NoData
274 | NoData
275 | NoData
276 | NoData
277 | NoData
278 | NoData
279 | NoData
280 | NoData
281 | NoData
282 | NoData
283 | NoData
284 | NoData
285 | NoData
286 | NoData
287 | NoData
288 | NoData
289 | NoData
290 | NoData
291 | NoData
292 | NoData
293 | NoData
294 | NoData
295 | NoData
296 | NoData
297 | NoData
298 | NoData
299 | No Fire Code Violations
300 | NoData
301 | NoData
302 | NoData
303 | NoData
304 | NoData
305 | NoData
306 | NoData
307 | F7 Permit is expired. Expired on 3/31/2020. Amount owed for permit
308 | NoData
309 | NoData
310 | NoData
311 | NoData
312 | Correct the Red Tagged Fire Alarm Panel
313 | Correct the Red Tag on the Fire Alarm Panel
314 | NoData
315 | REPAIR OR REPLACE THE EMERGENCY ILLUMINATION ON THE EXIT SIGNS AS WELL AS THE STAND ALONE EMERGENCY LIGHTING TO ENSURE IT IS FULLY OPERATIONAL.
316 | REMOVE STORAGE IN FRONT OF EXIT PATH.
317 | DISCONTINUE THE USE OF EXTENSION CORDS AS A PERMANENT SOURCE OF WIRING.
318 | MOUNT THE FIRE EXTINGUISHERS ACCORDING TO THE CODE LISTED ABOVE.
319 | NoData
320 | POST ADDRESS NUMBERS ON THE FRONT OF THE BUSINESS. NUMBERS ARE REQUIRED TO BE A MINIMUM OF 4 INCHES IN HEIGHT AND PLACED ON A CONTRASTING BACKGROUND.
321 | CLEAR AND MAINTAIN 36 INCHES IN FRONT OF BREAKER PANELS.
322 | #NAME?
323 | NoData
324 | REPLACE MISSING OUTLET AND SWITCH COVERS.
325 | F7 (FLAMMABLE/COMBUSTIBLE STORAGE) PERMIT EXPIRED 12-9-20.
326 | -ENSURE ALL EXITS ARE UNLOCKED WHILE THE BUILDING IS OCCUPIED. -PLACE STICKERS ON EXIT DOORS STATING: "THIS DOOR TO REMAIN UNLOCKED WHEN THE BUILDING IS OCCUPIED".
327 | OBTAIN AND MOUNT AT LEAST 2 FIRE EXTINGUISHERS WITH A MINIMUM RATING OF 2A:10BC TO ENSURE THERE'S AN EXTINGUISHER WITHIN 75 FEET OF UNOBSTRUCTED TRAVEL DISTANCE.
328 | OBTAIN AND POST AN ASSEMBLY PERMIT. OBTAIN PERMIT AT THE HOUSTON PERMITTING CENTER LOCATED AT 1002 WASHINGTON AVE. HOUSTON TX.
329 | KEYBOX
330 | Correct all violations within 30 calendar days.
331 | Provide documentation of annual extinguisher and safety training.
332 | Provide documentation of egress lighting test and correct any deficiencies.
333 | Mag locks must be approved through the City of Houston Building Department. Guideline will be sent to you with contact persons information.If you choose not to go through this process, remove the mag lock on the front entrance.Compliance by 12-11-2020
334 | All forklifts powered by propane or fuel shall have a tagged fire extinguisher mounted on the lift.Compliance by 12-11-2020
335 | Submit a Hazardous Materials Inventory Statement using the guideline provided on the form provided. Compliance by 12-11-2020
336 | Inspected 1/20/2020 and tagged acceptable, but strobes did not sync and fire doors did not close during inspector-observed fire drill.Have alarm system serviced to correct above deficiencies.
337 | Repair/replace broken/missing door closers on fire rated doors. Provide action plan if this cannot be completed by reinspection date on Page 1 of this report.
338 | NoData
339 | Have qualified sprinkler company address all yellow tag issues on the sprinkler system and bring the system back into compliance.Compliance by 5-29-2020
340 | A sign on the medical gas closet door is required to state: "CAUTION: OXIDIZING GASES STORED WITHIN, NO SMOKING".
341 | Provide a filler plate for the opening in the breaker panel.
342 | NoData
343 | NoData
344 | COMPLIANCE DATE: 15 CALENDAR DAYS
345 | (H3) permit is expired at this time
346 | NoData
347 | FOR REFERENCE
348 | The storage height for all hazardous materials must be maintained at or below 8' as required by code.The storage for containers in Bldg A must be maintained at or below this height.
349 | The remaining ASTs to be removed did not store hazardous materials on site but were used for mixing and stored nonhazardous ingredients. Their removal will be complete once the recycling agency is able to demo and accept materials. Most of the equipment and material in this area has been removed.
350 | Hazmat material is being removed from this location by 2/28/2021. There will no longer be any storage of corrosives and will no longer be a need for secondary containment.
351 | The Hazardous Materials Inventory Statement included with this notice must be completed for the indoor and outdoor storage and use of hazardous materials in BLDG A within 30 calendar days.Corrosives pose a health hazard and are considered hazardous.
352 | An Owner's Statement of Intended Use has been included with this notice. This statement is being provided for Bldg A and Bldg D.This statement indicates if either of the buildings will be used for High Piled storage or Hazardous Materials over MAQ. This statement must be completed and returned before our follow up inspection in 30 days.
353 | Application for Certificate of Occupancy are referenced below: - Bldg A: 20093700 (Change of use required from S1 to H4 occupancy) - Bldg B: 20093702 - Bldg C: 20093705 - Bldg D: 20093709
354 | FOR REFERENCE
355 | Maximum Allowable Quantities for Corrosives are as follows:INDOOR STORAGE OUTDOOR STORAGE975 Gallons (liquid) 1950 Gallons (liquid)9,750 Pounds (solid) 19,500 Pounds (solid)To exceed the above listed quantities, an application for an H4 Certificate of Occupancy is required.A guideline is included with this notice which specifies requirements needing to be met to start the Hazmat process.
356 | Any extension cords currently being used as permanent wiring must be removed.This violations applies to all occupancies on location.
357 | Your key box (k1) permit expired on 12-15-2020Renew this permit following the guidelines on the 2nd form.
358 | NoData
359 | PERMIT COMPLIANCE INSPECTION PERFORMED AND FOUND THAT LOCATION IS A STRIP CENTER WITH DIFFERENT SUITES AND BUSINESSES. EACH BUSINESS IS RESPONSIBLE FOR THEIR OWN PERMITS.
360 | WASTE ACCUMULATION AROUND DUMPSTERS NEEDS TO BE TAKEN CARE OF BY THE BUILDING MANAGEMENT.
361 | COMPLIANCE DATE: 15 CALENDAR DAYS
362 | K1 and A4 permit is expired at this time.
363 | NoData
364 | NoData
365 | NoData
366 | Test and replace inoperable emergency illumination.
367 | Have a licensed fire protection company service and tag the fire extinguishers.
368 | Have a licensed fire protection company inspect and repair any deficiencies on the vent hood suppression system.
369 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
370 | Post the occupant load.
371 | Remove locking bar on the rear exit while the building is occupied. Repair hardware if necessary.
372 | COMPLIANCE DATE: 15 CALENDAR DAYS
373 | P2 permit is expired at this time.
374 | NONE OF THE KEYS IN THE 911 KEYBOXES UNLOCKED THE DOORS INTO BUILDING. PLEASE PROVIDE 2 COPIES PER 911 KEYBOX OF DOOR KEYS, THEN CALL ME TO COME BACK OUT AND PUT INTO 911 KEYBOXES.
375 | MAINTAIN EXIT FOR USE IN EMERGENCY SITUATIONS - KEEP CLEAR OF ANY STORAGE
376 | ADDRESS MAINTENANCE ISSUES ON YELLOW TAGS
377 | NoData
378 | Audibility test required every 3 years.
379 | Sensitivity test required every 2 years.
380 | Place sign on doors leading into mechanical, fire alarm panel and electrical rooms.
381 | COMPLIANCE DATE: 15 CALENDAR DAYS
382 | F7 Permit is expired at this time.
383 | Non flammable or combustible liquids:1. Liquids that have no fire point when tested in accordance with ASTM D 92.2. Liquids with a flashpoint greater than 95°F (35°C) in a water-misciblesolution or dispersion with a water and inert (noncombustible) solids contentof more than 80 percent by weight.
384 | Discontinue the use of flammable or combustible spray finishing until appropriate spray room, booth, or space is compliant.
385 | COVER THE OPEN SPACES IN THE ELECTRICAL PANELS WITH BLANK COVERS. ALL OPEN BREAKER SLOTS SHALL BE COVERED.
386 | Sammi Tran
387 | COMPLY WITH ABOUT CODE. STORAGE IN A NON-SPRINKLERED BUILDING SHALL BEEN 24 INCHES.
388 | comply with the about code in the electrical room
389 | Obtain a P-2 Assembly permit to operate a place of assembly of over 49 maximum occupancy. APPLY FOR THE PERMIT A THE FIRE PREVENTION PERMIT OFFICE LOCATED AT 1002 WASHINGTON AVE. HOUSTON TX. 77002. PHONE NUMBER 832-394-8811. HOURS OF BUSINESS: 8:00-3:30 MON.-FRI.
390 | NoData
391 | NoData
392 | NoData
393 | P2
394 | NoData
395 | Obtain a key box permit from the Houston Permitting Center or remove the key box from the gate.
396 | Secure the compressed gas cylinder.
397 | NoData
398 | NoData
399 | NoData
400 | NoData
401 | EXPIRED K1 PERMIT
402 | EXPIRED P2 PERMIT
403 | NEED TO SERVICE ALL FIRE EXTINGUISHERS INCLUDING IN ELEVATOR ROOM.
404 | NEED TO CLEAN STAIRWELLS. NO STORAGE ALLOWED IN STAIRWELLS
405 | NEED TO DO ANNUAL SERVICE TO FIRE PUMP SERVICE.NEED TO DO THE 5 YEAR WATER TANK SERVICE (YELLOW TAGGED)
406 | NEED TO ADD KEY BOXES TO NORTH AND SOUTH ENTRANCES
407 | NEED TO UPDATE KEYS. ADD KEYS TO GENERATOR ROOM AND ANY OTHER CHANGED LOCKS IN COMMON AREAS
408 | NEED TO ADD ANOTHER ELEVATOR HOISTWAY KE. (2 TOTAL)
409 | CONTINUE TO PAY ALL PERMITS UPON DUE DATE
410 | EXPIRED K1 PERMIT
411 | NoData
412 | NoData
413 | NoData
414 | NoData
415 | NoData
416 | NoData
417 | Have a licensed fire protection company service and tag the fire extinguishers.
418 | Have a licensed fire protection company service and tag the spray booth suppression systems.
419 | Discontinue the use of flammable finishes in the booth without a suppression system.
420 | Move the key box to the new gate and enable push button for the electric fence.
421 | Repair the emergency illumination on the exit sign.
422 | Clear and maintain clearance around the spray booths.
423 | NoData
424 | NoData
425 | NoData
426 | PUT UP SIGNS SO THAT LOCATION IS VISIBLE FROM WAREHOUSE FLOOR AND HANG ON BRACKETS PER ABOVE FIRE CODE
427 | PUT UP SIGNS SO THAT LOCATION IS VISIBLE FROM WAREHOUSE FLOOR AND HANG ON BRACKETS PER ABOVE FIRE CODE
428 | CORRECT YELLOW TAG MAINTENANCE ISSUES
429 | FIRE ALARM SYSTEMS SHALL BE TESTED ANNUALLY BY A LICENSED COMPANY AND AN ACCEPTABLE TAGE SHALL BE AFFIXED TO ENSURE SYSTEM IS MAINTAINED IN OPERATIVE CONDITION.STANDPIPE SYSTEMS SHALL BE TESTED ANNUALLY BY A LICENSED COMPANY AND AN ACCEPTABLE TAGE SHALL BE AFFIXED TO ENSURE SYSTEM IS MAINTAINED IN OPERATIVE CONDITION.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
430 | APPLY FOR AND OBTAIN A HIGH-PILED STORAGE PERMIT ANS KEY BOX PERMIT FROM THE CITY OF HOUSTON PERMITTING CENTER LOCATED AT 1002 WASHINGTON AVE. (832-394-9000). COMPLIANCE: WITHIN 30 CALENDAR DAYS.
431 | NoData
432 | NoData
433 | NoData
434 | Conducted General Inspection on 12/31/20 .. No Violations found at this time. Have Fire Alarm System serviced by March 2021.
435 | FYI: Already signed Statement of Compliance.
436 | Already signed Statement of Compliance.
437 | Need a gas leak test performed every 5 years by a licensed plumber. FYI: Last gas leak was 5/12/2010 (#10026701).
438 | FYI: Already signed Statement of Compliance.
439 | NoData
440 | Repair the emergency illumination on the exit sign above the rear exit door.
441 | Post the occupant load.
442 | The kitchen hood suppression system is due for inspection before the end of 12/2020.
443 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
444 | NoData
445 | NoData
446 | NoData
447 | NoData
448 | NoData
449 | NoData
450 | NoData
451 | NoData
452 | NoData
453 | NoData
454 | NoData
455 | NoData
456 | NoData
457 | NoData
458 | NoData
459 | NoData
460 | NoData
461 | NoData
462 | NoData
463 | NoData
464 | NoData
465 | NoData
466 | NoData
467 | NoData
468 | NoData
469 | NoData
470 | NoData
471 | NoData
472 | NoData
473 | NoData
474 | NoData
475 | A compressed gas permit is required for storage/use of oxygen in amounts greater than 504 cubic ft. Obtain permit at the Houston Permitting Center.
476 | K1 permit expired 10-19-20Fire alarm permit expires 1-12-21
477 | FIRE ALARM SYSTEM SHALL BE MAINTAINED IN AN OPERATIVE CONDITION AT ALL TIMES. HAVE FIRE ALARM SYSTEM REPAIRED/REPLACED TO BE IN OPERATIVE CONDITION. THE FIRE ALARM SYSTEM IS NON OPERATIVE/NO POWER PRESENTLY. PROVIDE ACTION PLAN PER FIRE ALARM SYSTEM. FIRE WATCH AGREEMENT CAN BE UPGRADED TO STANDBY PER FIRE MARSHAL. CORRECTION REQUIRED BY OCTOBER 29,2019 TO AVOID CITATION AND/OR RE-INSPECTION FEE.
478 | NoData
479 | Fire protection systems shall be maintained in accordance with the original installation standards for that system.
480 | NoData
481 | P2 permit expired
482 | K1-permit expired
483 | P2-permit expired
484 | in school day care for classrooms 2,3 & 4no violations found at this time
485 | A4-permit expired
486 | P2 permit expired
487 | NoData
488 | NoData
489 | #NAME?
490 | Repair all red tag issues by 1/12/2021.
491 | NoData
492 | p2 permit expired 9/24/2020
493 | P2-permit expired
494 | CORRECT ALL VIOLATIONS TO AVOID BEING ASSESED A REINSPECTION FEE.
495 | COVER THE HOLES THAT WERE MADE FOR THE ELECTRICAL PIPES COMING FROM THE ELECTRICAL PANEL INTO THE CEILING WITH FIRE RATED EXPANDING FOAM.
496 | POST CERTIFICATE OF OCCUPANCY IN A PLACE THAT IS READILY AVAILABLE FOR INSPECTION.
497 | REMOVE 55 GALLON DRUM THAT IS LOCATED IN FRONT OF ELECTRICAL PANEL.
498 | ADD SIGN TO FRONT DOOR THAT READS, "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED". THIS SIGN MUST BE FACING INSIDE PLACE OF BUSINESS.
499 | NoData
500 | The sprinkler system was found to have a yellow tag attached. Contact a licensed fire protection company to have the violations corrected, and ensure a current service tag reflecting the corrections made is attached.
501 | The fire alarm control unit was found to have a yellow tag attached. Contact a licensed fire protection to correct the violations and ensure a current service tag reflecting the corrections made is attached.
502 | P2-permit expired
503 | P-2 permit expired
504 | K1-permit expired
505 | NoData
506 | NoData
507 | K1-permit expired
508 | Provide inspection and service tag.
509 | Provide annual.
510 | Correct 12/16/2019 Yellow tag on Fire Alarm System
511 | NoData
512 | Provide Annual Test and Report.
513 | Provide annual Inspection
514 | Repaint Fire Lane
515 | Provide new Falcon lock
516 | Provide a "fail safe" for the access gate.
517 | Repair or replace the emergency lighting on the exit signs.
518 | 2nd Notice Permit Expired 9/21/2020; Unpaid $385.38
519 | A key box is required for the access gate.
520 | P2-permit expired
521 | NoData
522 | K1-permit expired
523 | Exit gate's toggle switch is inoperable.
524 | Shops, Pool Room
525 | Fire Extinguishers are Red Tagged or missing in ;Office, Storage, Shop, Pool Room, Boiler Room
526 | Smoke alarms are required in each bedroom and immediately outside the bedroom and at the top of any stairs.
527 | Access Gates toggle switch is not installed.
528 | NoData
529 | Access Gates are missing the required fail safe.
530 | NoData
531 | NoData
532 | Have a licensed fire protection company service and tag the vent hood suppression system. The vent hoods are past due for cleaning.
533 | Test and repair any inoperable emergency illumination.
534 | P2 (ASSEMBLY PERMIT) EXPIRED 12-19-20.
535 | ADDED BY MISTAKE
536 | Secure compressed gas cylinders.
537 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
538 | The locked gate in the rear of the restaurant is required to be unlocked while the building is occupied. Replace hardware to open from egress side and lock from the outside if necessary.
539 | NoData
540 | Fire extinguishers due for annual inspection.
541 | Fire alarm system due for annual inspection.
542 | Place sign indicating location of fire alarm panel.
543 | NoData
544 | NoData
545 | NoData
546 | NoData
547 | NoData
548 | NoData
549 | Replace the light fixture cover located in the workroom. All code violations were corrected.
550 | Make all code violation corrections prior to the compliance date noted on page 1 of the inspection report. Notify the inspecting fire code official when all corrections have been made. All code violations were corrected.
551 | Provide documentation for a current / updated Fire Alarm System Audibility Test. These test are performed every 3 years. All code violations were corrected.
552 | NoData
553 | NoData
554 | NoData
555 | NoData
556 | Kimberly Bernard NO VIOLATIONS FOUND AT THIS TIME.
557 | Fire dept. unable to gain access to hydrant. Hydrant needs to be accessed from street. Fence around hydrant leaving a minimum 3 foot clearance.
558 | Manual gate near bldg. 11 needs new falcon lock and key to pad lock for 911 box. Manual gate near bldg. 12 needs key for padlock and another 911 box installed on inside of gate with key to pad lock (Fire trucks unable to turn around and must exit this gate). Automatic gate near bldg. 2 needs new failsafe lock and key for 911 box. This gate needs to be widened the width of the driveway. Fire trucks unable to access due to sharp turn and narrow gate. Main gate needs new falcon lock and two new pad locks for failsafes. Repair failsafe on exit side.Paint all boxes red and lube all locks
559 | No violations found.
560 | COMPLIANCE DATE: 15 CALENDAR DAYS
561 | L1 Permit is expired at this time.
562 | NoData
563 | Please renew expired permit
564 | 109.2 Owner/occupant responsibility. Correction and abatement of violations of this code shall be the responsibility of the owner. If an occupant creates, or allows to be created, hazardous conditions in violation of this code, the occupant shall be held responsible for the abatement of such hazardous conditions.
565 | 506.1 Where required. Where access to or within a structure or an area is restricted because of secured openings or where immediate access is necessary for life-saving or fire-fighting purposes, the fire code official is authorized to require a key box or a fire depository box to be installed in an approved location. The key box shall be of an approved type listed in accordance with UL 1037, and shall contain keys to gain necessary access as required by the fire code official. Key boxes shall be provided in accordance with Houston Fire Department LSB Standard No. 05, “Key Boxes.”
566 | 703.4 Testing. Horizontal and vertical sliding and rolling fire doors shall be inspected and tested annually to confirm proper operation and full closure. Fire doors, fire dampers, and other similar equipment shall be inspected and tested in accordance with Houston Fire Department LSB Standard No. 02, “Inspection and Testing of Fire Protection and Life-Safety Equipment.” A written record shall be maintained and be available to the fire code official.Compliance: 30 calendar days.
567 | 3205.4 Aisle maintenance. When restocking is not being conducted, aisles shall be kept clear of storage, waste material and debris. Fire department access doors, aisles and exit doors shall not be obstructed. During restocking operations using manual stocking methods, a minimum unobstructed aisle width of 24 inches (610 mm) shall be maintained in 48-inch (1219 mm) or smaller aisles, and a minimum unobstructed aisle width of one-half of the required aisle width shall be maintained in aisles greater than 48 inches (1219 mm). During mechanical stocking operations, a minimum unobstructed aisle width of 44 inches (1118 mm) shall be maintained in accordance with Section 3206.9.Compliance: 30 calendar days.
568 | 3201.3 Construction documents. At the time of building permit application for new structures designed to accommodate high-piled storage or for requesting a change of occupancy/use, and at the time of application for a storage permit, plans and specifications shall be submitted for review and approval. In addition to the information required by the International Building Code, the storage permit submittal shall include the information specified in this section. Following approval of the plans, a copy of the approved plans shall be maintained on the premises in an approved location.Compliance: 30 calendar days.
569 | 304.3.3 Capacity exceeding 1.5 cubic yards. Dumpsters and containers with an individual capacity between 1.5 cubic yards [40.5 cubic feet (1.15 m3)] and 15 cubic yards (405 cubic feet) (12 m3) or more shall not be stored in buildings or placed within 5 feet (1524 mm) of combustible walls, metal walls, building openings or combustible roof eave lines. Dumpsters and containers 15 cubic yards (405 cubic feet) (12 m3) capacity, or more, shall be a minimum of 10 feet (3 m) from combustible walls, metal walls, building openings, or roof eave lines. Dumpsters and containers shall not be placed on public sidewalks, streets, or other public property. No rubbish or combustible waste shall be placed, stored, or allowed to accumulate outside of dumpsters or containers. Lids of dumpsters shall be kept closed at all times.Compliance: 30 calendar days.
570 | Provide Annual Inspection on Fire Alarm System
571 | Remove combustible storage
572 | Provide signage "Electrical/Mechanical" on Door
573 | Replace missing ceiling tile
574 | NoData
575 | Provide Annual Testing and Report
576 | Provide Annual Inspection, last known inspection dates 2/2019, 2/2018.
577 | Repaint Fire Lane
578 | NEW, Repair or Correct Fail-safe operations on access gates due to corrosion.
579 | NEW, Provide new Falcon locks on Front Gate due to corrosion.
580 | Correct 9/9/2020 Yellow Tag
581 | NoData
582 | NoData
583 | NoData
584 | C7 (COMPRESSED GAS) M3 (FUEL DISPENSING) A4 (AUTOMATIC ACCESS GATES) PERMITS EXPIRED 12-19-20. RENEW THESE PERMITS WITHIN 10 BUSINESS DAYS TO AVOID BEING CHARGED A REINSPECTION FEE.
585 | NoData
586 | NoData
587 | COMPLIANCE DATE: 15 CALENDAR DAYS
588 | C7 permit is expired at this time.
589 | Obtain a Fire Door Report from a certified fire door inspector and make all repairs to fire doors required. Replace all missing fire rated doors in accordance with the approved plans.
590 | NoData
591 | NoData
592 | No violations found.
593 | NoData
594 | NoData
595 | MISSING (10:B/C) FIRE EXTINGUISHER(S) ON THE FORKLIFT(S) SHALL BE REPLACED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.FIRE EXTINGUISHER (S) ARE REQUIRED EVERY 75 FEET IN THE WAREHOUSE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
596 | THE EXIT PATHWAYS AND EXIT STAIRWAYS LEADING AWAY FROM THE WAREHOUSE SHALL HAVE A CLEAR PATH TO AN AREA OF SAFE REFUGE.COMPLIANCE: WITHIN 7 CALENDAR DAYS.
597 | APPLY FOR AND OBTAIN A ACEES GATE PERMIT AND 911 KEY BOX PERMIT FROM THE CITY OF HOUSTON PERMITTING CENTER LOCATED AT 1002 WASHINGTON AVE. (832-394-9000). COMPLIANCE: WITHIN 30 CALENDAR DAYS.
598 | NoData
599 | Your high piled permit (h2) expired on 12-19-2020. Renew your permit using the information provided . Total amount due $741.11
600 | NO STORAGE PER ABOVE FIRE CODE
601 | NoData
602 | NoData
603 | NoData
604 | HAVE ALL IMPAIRMENTS TO SPRINKLER SYSTEM CORRECTED WITHIN 7 BUSINESS DAYS.
605 | Have a licensed fire protection company service and tag the fire extinguishers.
606 | NoData
607 | NoData
608 | NoData
609 | NoData
610 | The fire alarm was red tagged on 1/5/2021 for phone lines down. Corrections must be made to bring the alarm back into full operational condition within 72 hrs. This includes restoration of the phone lines as well as inspection and retagging by a certified fire alarm company.
611 | The fire alarm was red tagged on 1/5/2021 for phone lines down. Corrections must be made to bring the alarm back into full operational condition within 72 hrs. This includes restoration of the phone lines as well as inspection and retagging by a certified fire alarm company.
612 | NoData
613 | NoData
614 | NoData
615 | NoData
616 | NoData
617 | NoData
618 | NoData
619 | NoData
620 | NoData
621 | NoData
622 | NoData
623 | NoData
624 | NoData
625 | NoData
626 | NoData
627 | NoData
628 | NoData
629 | NoData
630 | NoData
631 | NoData
632 | NoData
633 | NoData
634 | NoData
635 | COMPLIANCE DATE: 15 CALENDAR DAYS
636 | F7 Permit is expired at this time.
637 | NoData
638 | COMPLIANCE DATE: 15 CALENDAR DAYS
639 | P2 permit is expired at this time.
640 | NoData
641 | The fire alarm was red tagged on 1/5/2021 for phone lines down. Corrections must be made to bring the alarm back into full operational condition within 72 hrs. This includes restoration of the phone lines as well as inspection and retagging by a certified fire alarm company.
642 | Portable Fire Extinguisher(s) annual maintenance Dt: 9/20
643 | Keep all exit door(s) and pathways clear. Please remove garbage cans in front of exit. Complied while on site
644 | Commercial Kitchen Hood 6-month extinguisher maintenance Dt: 9/20
645 | K-rated [Kitchen] (Silver) portable fire extinguisher(s) annual maintenance Dt: 9/20
646 | 36" Working clearance must be maintained in front of electrical panels. Complied on site
647 | NoData
648 | 24" clearance must be maintained between ceiling and combustible materials (Non-sprinkled building)
649 | Building identification needs to be clearly marked and legible from main street side
650 | Commercial Kitchen hood requires minimum 6-MONTH inspection for buisness operations. Last performed: 4/19
651 | Commercial Kitchen hood has excessive grease buildup, requires cleaning
652 | Proof of current 5 year gas test required to be on site
653 | Plumber must pull permit prior to performing gas test to be acceptable
654 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs. Illumination for power outage not adequate
655 | Obtain and post Certificate of Occupancy [104.1(9)]. Current yellow application receipt also acceptable
656 | Portable Fire Extinguisher(s) annual maintenance Dt: 1/21
657 | NoData
658 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs
659 | 36" Working clearance must be maintained in front of electrical panels
660 | NoData
661 | 4/2020 - OK
662 | Last inspection 1/7/2020 - Blue, OKNext inspection scheduled 1/26/2021
663 | 3/2018 - OK
664 | Last inspection 1/7/2020 - Blue, OKNext inspection scheduled 1/26/2021
665 | 9/26/2019 - YellowCorrected 10/4/2019 - OK
666 | 7/29/2020 - OK
667 | 11/2020 - OK
668 | Last gas test 3/14/2018 - OK
669 | Monthly drills conducted. Last drill 12/7/2020
670 | 3/15/17 - OK
671 | Correct all violations within 60 calendar days.
672 | Remove all combustible items stored in mechanical room above office.
673 | Conduct and document required annual fire safety training.
674 | Repair hole in fire wall in mechanical room above office.Wires that penetrate fire wall must be in conduit, and gaps around conduit must be sealed with approved fire-stopping material.
675 | Only one obstructed drill documented. At least 50% of fire drill must be obstructed and force occupants to use secondary exits.Conduct and document obstructed drills.
676 | Have egress lighting tested and document the correction of any deficiencies.
677 | Portable Fire Extinguisher(s) annual maintenance Dt: Oct '20
678 | Commercial Kitchen Hood 6-month extinguisher maintenance Dt: Sep '20
679 | K-rated [Kitchen] (Silver) portable fire extinguisher(s) annual maintenance Dt: Oct '20
680 | Commerical Kitchen hood 6-MONTH inspection Dt: Sept '20
681 | 36" Working clearance must be maintained in front of electrical panels. Corrected on site
682 | NoData
683 | 24" clearance must be maintained between ceiling and combustible materials (Non-sprinkled building)
684 | Gas cylinders must be secured. Attach chain to non-movable object in order to keep cylinders upright
685 | COMPLIANCE DATE: 15 CALENDAR DAYS
686 | P2 Permit is expired at this time.
687 | 2/2020 - OK
688 | 1/6/2021 - Blue, OK
689 | New installation 12/2019. Not due until 12/2022.
690 | Correct all violations within 60 calendar days.
691 | Conduct and document required annual fire safety training.
692 | Conduct and document obstructed fire drills.
693 | Conduct and document monthly fire drills.
694 | Obtain smoke detector sensitivity report from alarm company, or obtain signed letter stating that alarm panel internally monitors sensitivity and reports when detectors are out of range.
695 | Have 90 minute test performed on all required exit signs and emergency lights, and provide documentation that any deficiencies were corrected.
696 | The class K fire extinguisher lost pressure.
697 | Vent hoods are due for cleaning before the end of 12/2020.
698 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
699 | NoData
700 | re-inspection fee for expired p2 permit 9/24/2020
701 | NoData
702 | CURRENT INFORMATION -FPS FIRE ALARM SYSTEM ANNUAL INSPECTION DATE: 11/28/2018 ACCEPTABLE BLUE TAG SPRINKLER SYSTEM INSPECTION DATE: 3/13/2019 ACCEPTABLE BLUE TAG ANNUAL FIRE EXTINGUISHER INSPECTION DATE: 6/2019 ANSUL SYSTEM BI-ANNUAL INSPECTION DATE: 7/2019
703 | AN APPROVED LICENSED MASTER ELECTRICIAN OR LICENSED ELECTRICAL SERVICE COMPANY SHALL TEST ALL EMERGENCY LIGHTING SYSTEMS ANNUALLY. LAST TEST DATE: UNKNOWN. PROVIDE WRITTEN DOCUMENTATION/REPORT OF TESTING RESULTS AND MAINTAIN ON FILE FOR FIRE CODE OFFICIAL. ANY FAILURES OF THE EMERGENCY LIGHTING SYSTEM SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
704 | REPAINT FIRE LANE ON BACK OF SCHOOL
705 | THROUGHOUT SCHOOL. VERIFY ALL CLASSROOMS CONTAIN PROPER EVACUATION FLOOR PLANS. FLOOR PLAN: ONE EVACUATION ROUTE FOR PRIMARY. (RED COLOR) ONE EVACUATION ROUTE FOR SECONDARY. (BLUE COLOR) HIGHLIGHT CLASSROOM. POST BY EXIT DOOR OF EACH CLASSROOM AND IN OTHER AREAS OF THE BUILDING NORMALLY OCCUPIED BY STUDENTS.
706 | WHERE A FIRE DEPARTMENT CONNECTION FOR AUTOMATIC SPRINKLER SYSTEM SERVES ONLY A PORTION OF A BUILDING OR A SPECIFIC BUILDING WITHIN A COMPLEX, AN APPROVED SIGN SHALL BE POSTED, INDICATING THE PORTION OF THE BUILDING OR SPECIFIC BUILDING BEING SERVED. THE SIGNS SHALL BE LOCATED ON OR ADJACENT TO THE CONNECTION AND SHALL BE CONSTRUCTED OF DURABLE MATERIAL. PROVIDE SIGNAGE FOR THE FIRE DEPARTMENT CONNECTIONS THAT SERVE THE SPECIFIC SCHOOL
707 | AN AUTHORIZED GENERATOR SERVICE COMPANY SHALL CONDUCT AN ANNUAL LOAD TEST WITH THE AVAILABLE EPSS LOAD AND SUPPLEMENTAL LOADS. PROVIDE DOCUMENTATION/REPORT OF ANNUAL LOAD TESTING.
708 | REPLACE MISSING/DAMAGED CEILING TILES -RISER ROOM, AROUND PIPES
709 | REMOVE ALL SMOKE DETECTOR COVERS -MECHANICAL ROOM 2
710 | PROVIDE PORTABLE FIRE EXTINGUISHER -CAFETERIA BY CUSTODIAL DOOR
711 | REMINDER.
712 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL OF THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY 3 YEARS. LAST AUDIBILITY TEST DATED: UNKNOWN. PROVIDE WRITTEN DOCUMENTATION/REPORT OF AUDIBILITY TEST AND MAINTAIN ON FILE FOR FIRE CODE OFFICIAL. ANY FAILURES OF THE AUDIBILITY TESTING SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
713 | A LICENSED SERVICE COMPANY SHALL CONDUCT HYDROSTATIC AND FLOW TESTS ON ALL FIRE DEPARTMENT CONNECTIONS EVERY 5 YEARS IN CONJUNCTION WITH THE STANDPIPE SYSTEM 5-YEAR TEST. PROVIDE DOCUMENTATION/REPORT AND BLUE TAG OF THE 5-YEAR TEST ON THE FIRE DEPARTMENT CONNECTION
714 | PROVIDE APPROPRIATE SIGN - PLASTIC CONTAINER (WASTE) IN CHEMISTRY STORAGE ROOM
715 | PROVIDE APPROVED COVERS FOR ALL SWITCH AND ELECTRICAL OUTLET BOXES. -AP OFFICE, WALL -ROOM 340, VENT TABLE -ROOM 303, TEACHER'S DESK
716 | MAINTAIN ADEQUATE CLEARANCE TO ALL ELECTRICAL SERVICE EQUIPMENT AT ALL TIMES. MARK THE NECESSARY ELECTRICAL CLEARANCE -814 STORAGE -ELECTRICAL -446 STORAGE -ELECTRICAL
717 | PROVIDE EXIT SIGN -BACK EXIT DOOR (STAFF, 606-609 AREA)
718 | CURRENT INFORMATION -FPS FIRE ALARM SYSTEM ANNUAL INSPECTION DATE: 7/31/2019 ACCEPTABLE BLUE TAG SPRINKLER SYSTEM INSPECTION DATE: 3/11/2019 ACCEPTABLE BLUE TAG 2 ANNUAL FIRE EXTINGUISHER INSPECTION DATE:6/2019 ANSUL SYSTEM BI-ANNUAL INSPECTION DATE:7/2019
719 | A LICENSED SERVICE COMPANY SHALL CONDUCT HYDROSTATIC AND FLOW TESTS ON ALL FIRE DEPARTMENT CONNECTIONS EVERY 5 YEARS IN CONJUNCTION WITH THE STANDPIPE SYSTEM 5-YEAR TEST. PROVIDE DOCUMENTATION AND TAG FOR THE 5TH YEAR FDC HYDRO TEST -OUTSIDE ROOM (2ND FDC) CORRECT YELLOW TAG ON 5TH YEAR FDC HYDRO 6/27/2017 -ROOM 409B (1ST FDC)
720 | REPAINT FIRE LANE IN FRONT AND BACK OF SCHOOL
721 | PROVIDE SIGNAGE "SPRINKLER RISER" ON/BY BOTH INSIDE AND OUTSIDE DOORS WHERE THE SPRINKLER RISER IS LOCATED. -OUTSIDE BOILER ROOM -ROOM 409B
722 | WHERE A FIRE DEPARTMENT CONNECTION FOR AUTOMATIC SPRINKLER SYSTEM SERVES ONLY A PORTION OF A BUILDING OR A SPECIFIC BUILDING WITHIN A COMPLEX, AN APPROVED SIGN SHALL BE POSTED, INDICATING THE PORTION OF THE BUILDING OR SPECIFIC BUILDING BEING SERVED. THE SIGNS SHALL BE LOCATED ON OR ADJACENT TO THE CONNECTION AND SHALL BE CONSTRUCTED OF DURABLE MATERIAL. PROVIDE SIGNAGE FOR THE (2) FIRE DEPARTMENT CONNECTIONS INDICATING WHICH AREAS OF THE BUILDINGS THEY EACH SERVE.
723 | REMINDER: Multi-plug adapters are to be plugged directly into an electrical outlet. Extension cords and/or surge protectors shall not be plugged into each other. PROVIDE ELECTRICAL OUTLET IF NEEDED.
724 | ALL ASSEMBLY, EDUCATIONAL OCCUPANCIES SHALL HAVE A TEST OF THE BUILDINGS NATURAL GAS SYSTEM(S), TO CHECK FOR LEAKAGE, AT LEAST EVERY 5 YEARS. PROVIDE WRITTEN DOCUMENTATION AND/OR REPORT OF TESTING AND RESULTS.
725 | REMOVE ALL STORED COMBUSTIBLE MATERIAL FROM BOILER ROOMS, MECHANICAL ROOMS OR ELECTRICAL EQUIPMENT ROOMS. -534 ELECTRICAL
726 | PROVIDE PORTABLE FIRE EXTINGUISHER -T201 ROOM B -446 STORAGE (ELECTRICAL)
727 | PROVIDE SMOKE DETECTORS -310 WORKROOM (STORAGE) -313 STORAGE -535 WORKROOM -441 ELECTRICAL -427 -325 ELECTRICAL -209 BOTH ELECTRICAL ROOMS NOTE: SUBMIT PLANS TO PLAN CHECKING REGARDING SMOKE DETECTORS TO BE APPROVED
728 | AN APPROVED HVAC COMPANY SHALL CONDUCT A FULL-FUNCTION TEST AND MAINTENANCE ON ALL FIRE DAMPERS AT LEAST EVERY 4 YEARS. PROVIDE DOCUMENTATION FOR TESTING AND ALL NECESSARY REPAIRS.
729 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL OF THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY 3 YEARS. LAST AUDIBILITY TEST DATED: UNKNOWN PROVIDE WRITTEN DOCUMENTATION OF AUDIBILITY TESTING AND ANY DOCUMENTATION REGARDING REPAIRS OF ANY FAILURES
730 | AN APPROVED LICENSED MASTER ELECTRICIAN OR LICENSED ELECTRICAL SERVICE COMPANY SHALL TEST ALL EMERGENCY LIGHTING SYSTEMS ANNUALLY. LAST TEST DATE: UNKNOWN PROVIDE WRITTEN DOCUMENTATION OF TESTING AND RESULTS. ANY FAILURES OF THE EMERGENCY LIGHTING SYSTEM SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
731 | MAINTAIN ADEQUATE CLEARANCE BELOW CEILING AT ALL TIMES. -117 STORAGE -114 OFFICE -113 OFFICE -313
732 | DOORS INTO ELECTRICAL CONTROL PANEL ROOMS SHALL BE MARKED WITH A PLAINLY VISIBLE AND LEGIBLE SIGN STATING 'ELECTRICAL ROOM' OR SIMILAR APPROVED WORDING. LABEL "ELECTRICAL ROOM" -446 STORAGE
733 | PROVIDE APPROVED COVERS FOR ALL SWITCH AND ELECTRICAL OUTLET BOXES. -ROOM 165 -ROOM 102
734 | REPLACE MISSING/DAMAGED CEILING TILES -169 STORAGE -ACTION BASED LEARNING LAB
735 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL OF THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY 3 YEARS. LAST AUDIBILITY TEST DATED: UNKNOWN PROVIDE WRITTEN DOCUMENTATION OF AUDIBILITY TESTING AND ANY DOCUMENTATION REGARDING REPAIRS OF ANY FAILURES
736 | REPAINT FIRE LANE
737 | CURRENT INFORMATION -FPS FIRE ALARM SYSTEM ANNUAL INSPECTION DATE: 1/10/2019 ACCEPTABLE BLUE TAG SPRINKLER SYSTEM INSPECTION DATE: N/A ANNUAL FIRE EXTINGUISHER INSPECTION DATE:6/2019 ANSUL SYSTEM BI-ANNUAL INSPECTION DATE: N/A
738 | CORRECT TROUBLE ALERT ON FIRE ALARM PANEL REMINDER: MARK APPROPRIATE TYPE OF INSPECTION PERFORMED ON INSPECTION TAG
739 | AN APPROVED LICENSED MASTER ELECTRICIAN OR LICENSED ELECTRICAL SERVICE COMPANY SHALL TEST ALL EMERGENCY LIGHTING SYSTEMS ANNUALLY. LAST EMERGENCY LIGHT TEST DATE: UNKNOWN PROVIDE WRITTEN DOCUMENTATION OF TESTING AND RESULTS. ANY FAILURES OF THE EMERGENCY LIGHTING SYSTEM SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
740 | FIRE EXTINGUISHERS SHALL BE INSPECTED ANNUALLY BY A LICENSED FIRE PROTECTION EQUIPMENT COMPANY.
741 | BOILER CERTIFICATE OF OPERATIONS SHALL BE MAINTAINED ON PREMISES. PROVIDE CERTIFICATE FOR #267063
742 | THE OWNER / OCCUPANT SHALL BE HELD RESPONSIBLE FOR THE CORRECTION AND ABATEMENT OF ALL VIOLATIONS LISTED IN THIS NOTICE OF VIOLATIONS REPORT. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
743 | AT THE TIME OF INSPECTION, APPROVED PLANS COULD NOT BE PRESENTED FOR INSPECTION BY THE FIRE MARSHAL. APPROVED PLANS ARE TO BE KEPT ON SITE AT ALL TIMES. IF APPROVED PLANS CANNOT BE LOCATED, A REQUEST TO THE BUILDING DEPARTMENT MAY BE ABLE TO DUPLICATE THE ORIGINAL. APPROVED PLANS MUST BE SUBMITTED TO FIRE MARSHAL OR THE PROCESS FOR HIGH-PILED STORAGE PLAN SUBMITTAL PROCESS SHALL BE RESTARTED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
744 | A PERMIT SHALL BE OBTAINED PRIOR TO ENGAGING IN ANY ACTIVITIES, OPERATIONS, PRACTICES, OR FUNCTIONS REGULATED BY THIS CODE AND REQUIRING A PERMIT AS LISTED IN SECTION 105.6. IT SHALL BE UNLAWFUL FOR ANY PERSON TO ENGAGE IN ANY ACTIVITIES, OPERATIONS, PRACTICES OR FUNCTIONS WITHOUT HOLDING A CURRENT AND VALID PERMIT.COMPLIANCE: WITHIN 30 CALENDAR DAYS.ISSUED PERMITS SHALL BE KEPT AT FACILITY AT ALL TIMES AND SHALL BE READILY AVAILABLE FOR INSPECTION BY THE FIRE CODE OFFICIAL.APPLY FOR AND OBTAIN A KEY BOX AND HIGH-PILED OPERATIONAL PERMIT FROM THE CITY OF HOUSTON PERMITTING CENTER LOCATED AT 1002 WASHINGTON AVE. (832-394-9000). COMPLIANCE: WITHIN 30 CALENDAR DAYS.
745 | CORRECT ALL VIOLATIONS WIHTIN 30 DAYS TO AVOID BEING ISSUED A REINSPECTION FEE.
746 | HAVE ALL EMERGENCY EXIT LIGHTS REPAIRED OR REPLACED. LIGHTS MUST BE ILLUMINATED AT ALL TIMES.
747 | The standpipe hose valves located on the occupant side of levels 44 and 45 need to comply with the above code and NFPA 14. The Horizontal standpipe system, hose valves and hose valve cabinets need to be approved by HFD plans checking.Compliance in 30 days.
748 | Perform reqired services on all life safety systems and equipment.
749 | NoData
750 | NoData
751 | Have a licensed fire protection company service and tag the fire extinguishers.
752 | Have a licensed fire protection company service and tag the vent hood suppression system. The vent hood requires professional cleaning.
753 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
754 | Repair the emergency illumination on the exit sign located on the rear exit.
755 | Post the occupant load.
756 | NoData
757 | NEED SERVICE 9-10-19 LAST DATE
758 | NoData
759 | IN ORDER TO OPERATE A BOARDING HOME, THE OPERATOR SHALL REGISTER ANNUALLY WITH ADMINISTRATION AND REGULATORY AFFAIRS (ARA) (832)394-8811. COMPLIANCE WITHIN 30 CALENDAR DAYS
760 | COMPLIANCE WITHIN 30 CALENDAR DAYS
761 | COMPLIANCE WITHIN 30 CALENDAR DAYS
762 | COMPLIANCE WITHIN 30 CALENDAR DAYS
763 | COMPLIANCE WITHIN 30 CALENDAR DAYS
764 | NoData
765 | NoData
766 | NEED TO BE SERVICE 9-10-19 LAST DATE
767 | NEED TO BE SERVICE 11-19 LAST DATE
768 | LAST SERVICE DATE 8-2020 ,DUE IN FEBRUARY
769 | Corrected on site
770 | THE CERTIFICATE OF OCCUPANCY SHALL BE POST IN BUILDING I.
771 | THE OWNER / OCCUPANT SHALL BE HELD RESPONSIBLE FOR THE CORRECTION AND ABATEMENT OF ALL VIOLATIONS LISTED IN THIS NOTICE OF VIOLATIONS REPORT. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
772 | NoData
773 | NEED SERVICE. 6-20-19 LAST DATE
774 | NEED SERVICE. 4-19 LAST DATE
775 | NEED SERVICE
776 | NoData
777 | FIRE PANEL NEED SERVICE . HAS A TROUBLE SIGNAL ON. 9-23-19 LAST SERVICE DATE
778 | NEED SERVICE. 3-19 LAST DATE
779 | NoData
780 | NoData
781 | NoData
782 | NoData
783 | Eric ZehnderNO VIOLATIONS FOUND AT THIS TIME
784 | ALL FIRE EXTINGUISHERS NEED A CURRENT INSPECTION TAG AND SHOULD BE INSPECTED ANNUALLY BY A LICENSED FIRE PROTECTION EQUIPMENT COMPANY.
785 | NEED 1 FIRE EXTINGUISHER IN OFFICE, 1 IN WAREHOUSE AND 1 ABOVE OFFICE IN STORAGE AREA. ALL FIRE EXTINGUISHERS MUST BE MOUNTED WITHIN 75 FT FROM ONE ANOTHER.
786 | REMOVE ALL ITEMS LOCATED IN FRONT OF ELECTRICAL PANEL. THERE MUST BE A 36 INCH CLEARANCE IN FRONT OF ELECTRICAL PANEL AT ALL TIMES.
787 | CLEAR ALL ISLES SO THAT THERE IS AT THE LEAST A 36 INCH CLEARANCE.
788 | NoData
789 | NoData
790 | NoData
791 | NoData
792 | NoData
793 | Correct red-tagged fire alarm panel within 72 hours.
794 | Fire alarm panel is red-tagged due to phone line #2 being down. Correct red tag conditions and return fire alarm system to full operational status within 72 hours.
795 | A Fire Department stand-by may be required if red-tagged system is not serviced in a timely manner.
796 | Fire alarm system is red tagged and must be serviced within 72 hours
797 | Failure to service red tagged systems will be subject to citations and re-inspection fees.
798 | NoData
799 | The red tag on the fire alarm panel must be corrected.
800 | NoData
801 | ol check, ol is 99, about 9 persons in club. issued permit renewal notice, p2 requested by G.O. Insp back in feb,2013. reinspect on 11-23-13. current permit expired in dec. 2012
802 | NoData
803 | Must place an exit sign above door.
804 | Identify both restrooms with a sign on the doors.
805 | It is the owner's/occupants responsibility to correct all violations listed in this inspection report.
806 | Replace missing ceiling tiles to maintain smoke and fire integrity.
807 | Place "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED" on the glass door or the door frame.
808 | FIRE EXTINGUISHERS ALL HAVE ANNUAL INSPECTIONS>6YRS OLD. HAVE THEM REPLACED, AS A NEW ANNUAL INSPECTION WOULD REQUIRE A HYDROSTATIC TEST - REPLACING THEM IS CHEAPER IN MOST CASES.
809 | TESTED TWO OF THE EMERGENCY LIGHTING AT THE EXIT SIGNS AND NEITHER WORKED - REPAIR OR REPLACE
810 | FIRE EXINGUISHERS NEED TO BE HUNG ON BRACKETS IN LOCATIONS THAT ARE UNOBSCURED BY STORAGE PER ABOVE CODE.
811 | MAINTAIN A COPY OF APPROVED CONSTRUCTION DOCUMENTS ON SITE PER ABOVE FIRE CODE. ALSO POST CERTIFICATE OF OCCUPANCY.
812 | NoData
813 | NoData
814 | NoData
815 | NoData
816 | NoData
817 | NoData
818 | NoData
819 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
820 | Provide documentation/report for fire damper testing and any necessary repairs.
821 | Repaint Fire Lanes
822 | NoData
823 | NoData
824 | NoData
825 | replace missing circuit breaker cover
826 | Repair sheetrock in unit.
827 | Required every 5 years and must be completed with an approved permit from theBuilding Department. PROVIDE A PNEUMATIC GAS TEST BY A LICENSED PLUMBER REQUIRED ONCE EVERYFIVE YEARS, A PERMIT FROM THE BUILDING DEPT. MUST BE OBTAINED FOR THISTEST
828 | Properties with 3 or more units are required to register with the City of Houston as required by Ordinance No. 2006-1124 (Apartment Security Ordinance).Please contact the City of Houston “Multi-Family Rental Property Registration” at 832-394-8841 or log on to http://www.houstonmultifamily.org/Provide copy of lease agreement with smoke detector and openFlame cooking policy or addendum.Abrego Denny 713 201 9804James E. Bowen 832 541 3796
829 | January 1, 2017 as battery operated single station alarm is replaced, that smoke alarm shall be replaced with tamper-resistant battery-operated single station smoke alarm.
830 | Permit Expired 12/18/2020: The annual renewal is always Dec. 18. The last renewal was paid 6 months late and that is why even though this permit was paid in July 2020 it has expired again.
831 | NoData
832 | NoData
833 | NoData
834 | NoData
835 | NoData
836 | NoData
837 | NoData
838 | NoData
839 | NoData
840 | NoData
841 | NoData
842 | NoData
843 | NoData
844 | NoData
845 | NoData
846 | NoData
847 | NoData
848 | NoData
849 | NoData
850 | NoData
851 | NoData
852 | NoData
853 | Have all Fire Extinguishers serviced, and provide with current service tags.
854 | Have Kitchen Fire Suppression / Ansul System serviced, and provided with a current service tag. System must be serviced every 6 months.
855 | Have Certificate of Occupancy posted near Main Entrance of Business
856 | Have "EXIT" @ Main entrance serviced, ensuring back-up power is available.
857 | NoData
858 | NoData
859 | NoData
860 | Have Kitchen Fire Suppression / Ansul System serviced, and provided with a current service tag, Every 6 months.
861 | Renew Public Assembly PermitCOH-Building Dept1002 Washington Ave.
862 | Have all Fire Extinguishers serviced, and provided with current service tags.
863 | A LP-Gas permit is required for the use of Propane Gas Heaters on the Patio.Apply for Lp-Gas Permit @ COH-Building Dept.1002 Washington Ave. Permit Office.
864 | NoData
865 | NoData
866 | NoData
867 | NoData
868 | NoData
869 | NoData
870 | NoData
871 | NoData
872 | NoData
873 | NoData
874 | NoData
875 | NoData
876 | NoData
877 | NoData
878 | NoData
879 | NoData
880 | NoData
881 | NoData
882 | NoData
883 | NoData
884 | NoData
885 | NoData
886 | NoData
887 | NoData
888 | NoData
889 | NoData
890 | NoData
891 | NoData
892 | NoData
893 | NoData
894 | NoData
895 | NoData
896 | NoData
897 | NoData
898 | NoData
899 | NoData
900 | NoData
901 | NoData
902 | NoData
903 | NoData
904 | NoData
905 | NoData
906 | NoData
907 | NoData
908 | NoData
909 | NoData
910 | NoData
911 | NoData
912 | NoData
913 | NoData
914 | NoData
915 | NoData
916 | NoData
917 | NoData
918 | NoData
919 | NoData
920 | NoData
921 | NoData
922 | NoData
923 | NoData
924 | NoData
925 | 5/5/2018 - OK
926 | Last load bank 10/12/2020 - OK
927 | 6/5/2019 - Blue, OK
928 | Evacuation maps OK
929 | Obstructed drills OK
930 | Drill log OK
931 | 8/1/2019 - OK
932 | Last inspection 1/2019Have all portable fire extinguishers inspected (including Class K in both kitchens)
933 | Correct all violations within 60 calendar days.
934 | Last inspection 8/1/2019Have fire alarm system inspected and have any deficiencies corrected.
935 | Last inspection 8/9/2019 - YellowHave sprinkler system inspected and have all deficiencies corrected.
936 | Have fire pump tested and have any deficiencies corrected.
937 | Have all hose cabinets inspected.
938 | Have ANSUL systems in both kitchens inspected.Have exhaust ducts in 2nd floor kitchen professionally cleaned.
939 | Remove all combustible items stored in mechanical and electrical rooms.
940 | Provide documentation of required annual fire safety training.
941 | Prohibit kitchen staff from blocking ANSUL pull stations.
942 | Provide documentation of gas test performed within the last 5 years. Plumber must obtain appropriate permit from the City of Houston prior to performing test.
943 | Last egress lighting test 8/2/2019.Have 90 minute egress lighting test performed and have any deficiencies corrected.
944 | NoData
945 | Contact a licensed Fire Protection Company to make any repairs necessary to clear the "trouble" signal on the fire alarm control panel.
946 | NoData
947 | NoData
948 | Please have a flow test done on all 6 private hydrants excluding both City of Houston hydrants located on North side complex.
949 | Please remove all debris (sofas, old mattresses, trash) located behind and near dumpsters.
950 | LPG containers not allowed on property.
951 | Please repair all micro switches located inside 911 boxes and place inside a master lock key that opens padlock on manual gates.
952 | Please identify all electrical switches with proper unit numbers.
953 | Please visually inspect all draft stops for solid construction & repair all damaged areas.
954 | Blue reflector is required to identify all 9 hydrant locations on property. 6 - private hydrants3 - city hydrants
955 | please verify all sleeping units are furnished with a working smoke alarm including egress pathway from apartment unit.
956 | Please provide a valid access gate permit for Tradewinds Apts.
957 | Please provide a valid key box permit for Tradewinds Apts.
958 | Please repair all damaged 911 boxes including micro switches and failsafe pull boxes.
959 | NoData
960 | Key box permit ( K1) are expired.Access gates permit (A4) are expired.Hazardous materials permit (H1) are expired.
961 | NoData
962 | NoData
963 | NoData
964 | Key Box (K1) permit is expired.
965 | Exit and entry signs on gates would be helpful.
966 | Make sure all 911 emergency features work on all gates. All gates will be left open until all emergency features work properly.
967 | Mike--Building EngineerNO VIOLATIONS FOUND AT THIS TIME.
968 | NoData
969 | Access Gate (A4) permit is expired.
970 | The following operational permits are expired and must be renewed with the City of Houston. A re-inspection fee will be assessed if the permits are not paid. The fee amount due is$918.98
971 | P2 permit expired
972 | Current audibility test required
973 | NoData
974 | Fire alarm is not operational, red tagged on 6/5/19 and currently no power to unit. 72 hour notice given.
975 | Sprinkler requires annual testing
976 | Missing protective caps.
977 | Permit needs to be pulled by plumber before gas test performed
978 | Current gas test required
979 | F7 permit required for cooking oil storage tanks >60 gal. Pending return call from manufactuer regarding tank size, permit may not be required
980 | Current Sensitivity test required
981 | NoData
982 | Obtain and post Certificate of Occupancy [104.1(9)]
983 | NoData
984 | There must be an emergency lighting test performed on all emergency lights.
985 | All fire extinguishers must be serviced and have a current service tag.
986 | The fire alarm permit must be renewed.
987 | NoData
988 | Correct Red tag on fire alarm system.Provide Inspector with compliance letter once corrections are made.Re-inspection fees and or citations for continued non compliance.
989 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
990 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
991 | Provide documentation/report for fire damper testing and any necessary repairs.
992 | Provide certificate of flame resistance, it shall indicate the color for all decorative materials. 1. new curtains, new certificate or 2. new certificate showing retesting of flame resistance.
993 | Correct Yellow tag on Sprinkler System (FDC); Correct Trouble Alert on Fire Alarm System
994 | NoData
995 | Your fire alarm permit has expired. Renew this permit by going to the City of Houston web site under fire department permits.Compliance by 2-12-2021
996 | Your firefighter access road has faded in the rear of the building. Paint over the lines so that they are visible and maintain a clear path inside these lines.Compliance by 2-12-2021
997 | Secure all argon and propane bottles in one of the ways listed.Compliance by 2-12-2021
998 | Provide an approved cover plate over the open electrical near the chiller room.Compliance by 2-12-2021
999 | Have qualified door company perform annual drop test on all fire doors.Compliance by 2-12-2021
1000 | Have qualified fire extinguisher company place a tagged extinguisher on all forklifts powered by propane or fuel.Compliance by 2-12-2021
1001 | Provide aisles around the warehouse so that making it to exits is not blocked.Aisles between racks shall not be blocked unless restocking is going on. At this time at least half the aisle shall remain clear.Compliance by 2-12-2021
1002 | Provide documentation that all emergency lights have been tested and are working at that time.Compliance by 2-12-2021
1003 | Remove the lock on the exit at the front of the building a maintain that door unlocked while the building is occupied.Immediate compliance required.
1004 | Remove the letters HFD on all doors that don't lead into the high piled area.Compliance by 2-12-2021
1005 | Remove all pallets and other objects blocking the width of your firefighter access road in the rear of the building.Compliance by 2-12-2021
1006 | Remove all objects blocking a clear means of egress to all exits and on the outside of all exits so that a clear path away from the building is provided.Immediate compliance required.
1007 | COVER THE OPEN SPACES IN THE ELECTRICAL PANELS WITH BLANK COVERS. ALL OPEN BREAKER SLOTS SHALL BE COVERED.
1008 | Sammi Tran
1009 | COMPLY WITH ABOUT CODE. STORAGE IN A NON-SPRINKLERED BUILDING SHALL BEEN 24 INCHES.
1010 | comply with the about code in the electrical room
1011 | Obtain a P-2 Assembly permit to operate a place of assembly of over 49 maximum occupancy. APPLY FOR THE PERMIT A THE FIRE PREVENTION PERMIT OFFICE LOCATED AT 1002 WASHINGTON AVE. HOUSTON TX. 77002. PHONE NUMBER 832-394-8811. HOURS OF BUSINESS: 8:00-3:30 MON.-FRI.
1012 | There must be an emergency lighting test performed on all emergency lights.
1013 | All fire extinguishers must be serviced and have a current service tag.
1014 | The fire alarm permit must be renewed.
1015 | NoData
1016 | Renew expired assembly (P2) and keybox (K1) permits.
1017 | The High Piled operational permit is expired and must be renewed. The amount owed is: $503.95. Online options have been made available for your safety and convenience. Please follow the instructions above.
1018 | There must be an emergency lighting test performed on all emergency lights.
1019 | All fire extinguishers must be serviced and have a current service tag.
1020 | The fire alarm permit must be renewed.
1021 | The H1 operational permit has expired for this location and must be renewed if it is still applicable. Online payment options are available for your safety and convenience. See the instructions above. The amount owed is: $385.38
1022 | 2/5/2020 - Blue, OK
1023 | 3/22/2018 - OK
1024 | 2/5/2020 - Blue, OK
1025 | 2/13/2019 - Blue, OK
1026 | Evacuation maps OK
1027 | 3/22/2018 - OK
1028 | 2/2020One extinguisher in upstairs electrical room hasn't been inspected since 2017. Have extinguisher updated during next inspection (Due next month)
1029 | Correct all violations within 60 calendar days
1030 | Remove all items stored in stairwells.
1031 | Remove all combustible items stored in electrical and mechanical rooms.
1032 | Conduct and document required annual fire safety training.
1033 | Cover all missing breaker slots.
1034 | Replace all missing ceiling tiles.
1035 | Conduct and document obstructed fire drills.
1036 | Conduct monthly fire drills and provide log for inspector to review.
1037 | Remove all curtains, drapes, and fabrics that are not of fire-retardant materials.
1038 | Provide sign clearly marking location of the FDC.
1039 | Rotate exit signs and/or change chevrons as necessary to ensure that all signs clearly indicate direction of exit(s).
1040 | Label stairwell doors that lead to roof access ladder.
1041 | Have egress lighting tested and provide documentation that any deficiencies were corrected.
1042 | Please renew your access gate & key box permits.Both expired on 12/22/2020.
1043 | NoData
1044 | Please renew both your access gate (a4) & key box (k1) permits. Permits expired on 12/19/2020.
1045 | 1) Gate right of office needs new falcon lock and conduit needs to be secured to gate. 2) Manual gate on Sabo can be left like it is (unlocked) or secure gate with chain and place key in new 911 box mounted to gate post. 3) Kleckley gate needs failsafe and 911 box installed. 4) Manual gate on Kingspoint needs new 911 box mounted on gate post with new falcon lock and key to gate placed inside 911 box.
1046 | 2/2020 - OK
1047 | Correct all violations within 60 calendar days.
1048 | Panel locked and unable to access. Provide report from last fire alarm inspection.Two missing horn/strobes in office and duct detector in gym does not appear to be working. Have alarm company repair and/or replace.
1049 | Conduct and document required annual fire safety training.
1050 | Replace all missing ceiling tiles.
1051 | Conduct and document obstructed fire drills.
1052 | Conduct and document monthly fire drills.
1053 | Label door that leads to roof access ladder.
1054 | NoData
1055 | NoData
1056 | NoData
1057 | NoData
1058 | Please have a flow test done on all 6 private hydrants excluding both City of Houston hydrants located on North side complex.
1059 | Please remove all debris (sofas, old mattresses, trash) located behind and near dumpsters.
1060 | LPG containers not allowed on property.
1061 | Please repair all micro switches located inside 911 boxes and place inside a master lock key that opens padlock on manual gates.
1062 | Please identify all electrical switches with proper unit numbers.
1063 | Please visually inspect all draft stops for solid construction & repair all damaged areas.
1064 | Blue reflector is required to identify all 9 hydrant locations on property. 6 - private hydrants3 - city hydrants
1065 | please verify all sleeping units are furnished with a working smoke alarm including egress pathway from apartment unit.
1066 | Please provide a valid access gate permit for Tradewinds Apts.
1067 | Please provide a valid key box permit for Tradewinds Apts.
1068 | Please repair all damaged 911 boxes including micro switches and failsafe pull boxes.
1069 | NoData
1070 | NoData
1071 | NoData
1072 | NoData
1073 | NoData
1074 | Please label door for electrical equipment identification
1075 | Please add mandatory signage to front doors
1076 | Failure to comply in timely manner - Initial inspection started 9/2/20
1077 | Forgot to include this specific code in original report. Comments were included in the marking code included in original report.The marking for the extinguisher on the column also needs to be marked with RED (preferably) DOT tape near the top of the column for identification
1078 | CO must be available on site
1079 | Aisles in customer sales area must maintain minimum 36" width. Stock, cardboard, carts ect. must not clutter store restricting access or egress
1080 | The Key Box Permit has expired and the current unpaid amount of $177.87 is due. Online payment options are available for your safety and convenience. See payment options above.
1081 | NoData
1082 | The H1-Hazardous Materials permit has expired and must be renewed. The amount owed is$385.38 and there is a new online payment option for your safety and convenience. Payment must be remitted by 1/18/21 to avoid reinspection fees.
1083 | NoData
1084 | currentsept 2020
1085 | Ensure that tenant aware of this regulation.
1086 | Repair sheetrock in storage room
1087 | Required every 5 years and must be completed with an approved permit from theBuilding Department. PROVIDE A PNEUMATIC GAS TEST BY A LICENSED PLUMBER REQUIRED ONCE EVERYFIVE YEARS, A PERMIT FROM THE BUILDING DEPT. MUST BE OBTAINED FOR THISTEST
1088 | Properties with 3 or more units are required to register with the City of Houston as required by Ordinance No. 2006-1124 (Apartment Security Ordinance).Please contact the City of Houston “Multi-Family Rental Property Registration” at 832-394-8841 or log on to http://www.houstonmultifamily.org/Provide copy of lease agreement with smoke detector and openFlame cooking policy or addendum.James E Bowen 832 541 3796Abrego Denny 713 201 9804
1089 | Label installation date on smoke alarm.
1090 | NoData
1091 | NoData
1092 | NoData
1093 | NoData
1094 | NoData
1095 | NoData
1096 | NoData
1097 | NoData
1098 | NoData
1099 | NoData
1100 | NoData
1101 | NoData
1102 | NoData
1103 | NoData
1104 | NoData
1105 | NoData
1106 | NoData
1107 | NoData
1108 | NoData
1109 | NoData
1110 | NoData
1111 | NoData
1112 | NoData
1113 | NoData
1114 | NoData
1115 | NoData
1116 | NoData
1117 | NoData
1118 | NoData
1119 | NoData
1120 | NoData
1121 | NoData
1122 | NoData
1123 | NoData
1124 | NoData
1125 | NoData
1126 | NoData
1127 | NoData
1128 | NoData
1129 | NoData
1130 | NoData
1131 | NoData
1132 | NoData
1133 | NoData
1134 | NoData
1135 | NoData
1136 | NoData
1137 | NoData
1138 | NoData
1139 | NoData
1140 | NoData
1141 | NoData
1142 | NoData
1143 | NoData
1144 | NoData
1145 | NoData
1146 | NoData
1147 | NoData
1148 | NoData
1149 | NoData
1150 | NoData
1151 | NoData
1152 | NoData
1153 | NoData
1154 | NoData
1155 | NoData
1156 | NoData
1157 | NoData
1158 | NoData
1159 | NoData
1160 | NoData
1161 | NoData
1162 | NoData
1163 | NoData
1164 | NoData
1165 | NoData
1166 | NoData
1167 | NoData
1168 | NoData
1169 | NoData
1170 | NoData
1171 | NoData
1172 | NoData
1173 | NoData
1174 | NoData
1175 | NoData
1176 | NoData
1177 | NoData
1178 | NoData
1179 | NoData
1180 | NoData
1181 | NoData
1182 | NoData
1183 | NoData
1184 | NoData
1185 | NoData
1186 | NoData
1187 | NoData
1188 | NoData
1189 | NoData
1190 | NoData
1191 | NoData
1192 | NoData
1193 | NoData
1194 | NoData
1195 | NoData
1196 | NoData
1197 | NoData
1198 | NoData
1199 | NoData
1200 | NoData
1201 | NoData
1202 | NoData
1203 | NoData
1204 | NoData
1205 | NoData
1206 | NoData
1207 | NoData
1208 | NoData
1209 | NoData
1210 | NoData
1211 | NoData
1212 | NoData
1213 | NoData
1214 | NoData
1215 | NoData
1216 | NoData
1217 | NoData
1218 | NoData
1219 | NoData
1220 | NoData
1221 | NoData
1222 | NoData
1223 | NoData
1224 | NoData
1225 | NoData
1226 | NoData
1227 | NoData
1228 | NoData
1229 | NoData
1230 | NoData
1231 | NoData
1232 | NoData
1233 | NoData
1234 | NoData
1235 | NoData
1236 | NoData
1237 | NoData
1238 | NoData
1239 | NoData
1240 | NoData
1241 | NoData
1242 | NoData
1243 | NoData
1244 | NoData
1245 | NoData
1246 | NoData
1247 | NoData
1248 | NoData
1249 | NoData
1250 | NoData
1251 | NoData
1252 | NoData
1253 | NoData
1254 | NoData
1255 | NoData
1256 | NoData
1257 | NoData
1258 | NoData
1259 | NoData
1260 | NoData
1261 | NoData
1262 | NoData
1263 | NoData
1264 | NoData
1265 | NoData
1266 | NoData
1267 | NoData
1268 | NoData
1269 | NoData
1270 | NoData
1271 | NoData
1272 | NoData
1273 | NoData
1274 | NoData
1275 | NoData
1276 | NoData
1277 | NoData
1278 | NoData
1279 | NoData
1280 | NoData
1281 | NoData
1282 | NoData
1283 | NoData
1284 | NoData
1285 | NoData
1286 | Fire Alarm System red and yellow tagged on 12/8/20. Correct all tags and return system to normal operation.
1287 | NoData
1288 | P2, A4 & K1 PERMIT EXPIRED 9/10/2019
1289 | Report is including 9606, 9616, 9636 & 9680 Mesa
1290 | Correct yellow tagged Fire Sprinkler System dated 1/5/2021
1291 | NoData
1292 | NoData
1293 | NoData
1294 | NoData
1295 | NoData
1296 | NoData
1297 | NoData
1298 | NoData
1299 | NoData
1300 | CORRECTION AND ABATEMENT OF VIOLATIONS OF THIS CODE SHALL BE THE RESPONSIBILITY OF THE OWNER.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1301 | WHERE AN APPROVED ELECTRONIC EXIT EGRESS LOCKING DEVICE IS INSTALLED ON AN EXIT EGRESS DOOR, IN ACCORDANCE WITH THE CONSTRUCTION CODES, THE FIRE ALARM SYSTEM, RELAY DEVICES TO LOCKING DEVICES AND AT THE DOOR SHALL BE TESTED AT LEAST SEMI-ANNUALLY TO ENSURE FAIL-SAFE OPERATION OF THE RELAY AND LOCKING DEVICE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1302 | ALL AUTOMATIC WET-PIPE SPRINKLER SYSTEMS SHALL BE INSPECTED AND TESTED ANNUALLY IN ACCORDANCE WITH NFPA 25 AND STATE REQUIREMENTS, AND SERVICE TAGGED BY A LICENSED AUTOMATIC FIRE SPRINKLER SERVICE COMPANY.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1303 | FDC's SHALL BE INSPECTED QUARTERLY BY BUILDING PERSONNEL IN ACCORDANCE WITH THIS STANDARD AND NFPA 25. INSPECTIONS SHOULD CHECK FOR MISSING PROTECTIVE CAPS.MISSING FDC PROTECTIVE CAPS SHALL BE REPLACED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1304 | A LICENSED SERVICE COMPANY SHALL CONDUCT HYDROSTATIC AND FLOW TESTS OF ALL FIRE DEPARTMENT CONNECTIONS (FDC), PIPING AND CHECK VALVE ASSEMBLIES, NOT LESS THAN EVERY 5 YEARS.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1305 | EACH FIRE AND SMOKE DAMPER ASSEMBLY IN MECHANICAL, ELECTRICAL OR AIR HANDLER ROOMS AND SPACES, AND IN FIREWALLS OR RATED OCCUPANCY SEPERATION WALLS SHALL BE VISUALLY INSPECTED AT LEAST ANNUALLY TO VERIFY THAT THEIR OPERATIONS ARE NOT OBSTRUCTED OR IMPAIRED.A WRITTEN RECORD OF INSPECTIONS SHALL BE MAINTAINED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1306 | AN APPROVED HVAC COMPANY SHALL CONDUCT A FULL-FUNCTION TEST AND MAINTENANCE ON ALL FIRE DAMPERS AT LEAST EVERY 4 YEARS.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1307 | OPEN JUNCTION BOXES AND OPEN-WIRING SPLICES SHALL BE PROHIBITED.PLACE COVER OVER OPEN-WIRING SPLICES.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1308 | FIRE WALLS, FIRE BARRIERS AND FIRE PARTITIONS. REQUIRED FIRE WALLS, FIRE BARRIERS AND FIRE PARTITIONS SHALL BE MAINTAINED TO PREVENT THE PASSAGE OF FIRE.MAINTAIN REQUIRED FIRE PROTECTION IN PIPING GOING THROUGH CEILING.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1309 | ALL FLOOR PLANS SHALL INCLUDE THE PRIMARY EVACUATION ROUTE FROM EACH ROOM AND AN ALTERNATE ROUTE THAT CAN BE USED IF THE PRIMARY ROUTE BECOMES OBSTRUCTED.PRIMARY AND ALTERNATE ROUTES SHALL BE SHOWN IN DIFFERENT COLORS AND A LEGEND SHOWING APPROPRIATE COLOR ASSOCIATED WITH ROUTES.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1310 | FIRE PROTECTION SYSTEMS SHALL BE INSPECTED, TESTED AND MAINTAINED IN ACCORDANCE WITH THE REFERENCED STANDARDS AND IN ACCORDANCE WITH HFD LSB STANDARD NO. 02.FIRE SPRINKLER SYSTEM LAST INSPECTED ON 02 FEBRUARY 2016.FIRE SPRINKLER SYSTEM SHALL BE TESTED ANNUALLY BY A LICENSED COMPANY AND AN ACCEPTABLE TAG SHALL BE AFFIXED TO THE FIRE SPRINKLER RISER.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1311 | WHERE REQUIRED ALL INSTITUTIONAL (I4) OCCUPANCIES SHALL HAVE A TEST OF THE BUILDING'S NATURAL GAS SYSTEM(S), TO CHECK FOR LEAKAGE, AT LEAST EVERY 5 YEARS.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1312 | ALL GAS PRESSURE TESTS REQUIRE PERMITTING BY THE CITY OF HOUSTON CONSTRUCTION CODES."GAS TEST" PERMITS SHALL BE OBTAINED, AND GAS PRESSURE TESTS CONDUCTED, BY A LICENSED PLUMBER OR APPROVED GAS EQUIPMENT SERVICE COMPANY.COPIES OF THE CITY OF HOUSTON "GAS TEST" PERMIT AND FINAL APPROVAL FORM SHALL BE OBTAINED FROM THE PLUMBER OR SERVICE COMPANY AND MAINTAINED ON THE PREMISES.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1313 | THE CODES AND STANDARDS REFERENCED IN THIS CODE SHALL BE THOSE THAT ARE LISTED IN CHAPTER 80, AND SUCH CODES AND STANDARDS SHALL BE CONSIDERED PART OF THE REQUIREMENTS OF THIS CODE TO THE PRESCRIBED EXTENT OF EACH SUCH REFERENCE.NFPA 13 (INSTALLATION OF SPRINKLER SYSTEMS) SECTION 6.2.9.6: ONE SPRINKLER WRENCH AS SPECIFIED BY THE SPRINKLER MANUFACTURER SHALL BE PROVIDED IN THE SPRINKLER CABINET FOR EACH TYPE OF SPRINKLER INSTALLED TO BE USED FOR THE REMOVAL AND INSTALLATION OF SPRINKLERS IN THE SYSTEM.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1314 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit for test.
1315 | A Fire Department stand-by may be required if red-tagged system is not serviced in a timely manner.
1316 | Fire alarm system is red tagged and must be serviced within 72 hours
1317 | Failure to service red tagged systems will be subject to citations and re-inspection fees.
1318 | Access Gate (A4) permit is expired.
1319 | NoData
1320 | NoData
1321 | Anuli Ezumah NO VIOLATIONS FOUND AT THIS TIME.
1322 | NoData
1323 | Access Gate (A4) permit is expired.Keybox (K1) permit is expired.
1324 | Hot works (H3) is expired.
1325 | NoData
1326 | NoData
1327 | NoData
1328 | NoData
1329 | NoData
1330 | Access Gate (A4) permit is expired.
1331 | NoData
1332 | Hotworks (H3) permit is expired.
1333 | NoData
1334 | for informational purpose only
1335 | Corrected all fire code violations pointed out
1336 | NoData
1337 | NoData
1338 | No violations as of this date.
1339 | NoData
1340 | NoData
1341 | NoData
1342 | Perform reqired services on all life safety systems and equipment.
1343 | NoData
1344 | NoData
1345 | NoData
1346 | NoData
1347 | NoData
1348 | NoData
1349 | NoData
1350 | NoData
1351 | NoData
1352 | NoData
1353 | NoData
1354 | NoData
1355 | NoData
1356 | NoData
1357 | NoData
1358 | NoData
1359 | NoData
1360 | See above- per our discussion (through email/ phone) the following MAQ see table for quantities allowed- you have 14 days to get under the amount allowed
1361 | Provide inventory for current material.
1362 | See above.
1363 | See above- per our discussion through email (provided Fire Engineer contact information)
1364 | apply for a flammable and combustible liquids permit type (f-7 )for storage of waste oils stored over the (55) gallon limit in one container
1365 | NoData
1366 | repair all emergency lights or replace them
1367 | remove all metal parts and any other obstructions away from exit door
1368 | have both fire extinguishers inspected and tad
1369 | remove flammable or combustible materials from shop area such as boxes paper .leaves ,plastic containers from the emmediate area that could a fire hazard.
1370 | remove all flammable or combustible materials such as empty plastic bottles, empty boxes, paper ,cloth materials and any other trash from premises that create a fire hazard
1371 | provide metal covers for (5) gallon containers that are filled with waste oils temporary before dispensing into main plastic oil container designed for all waste oils.
1372 | label with the following words restroom ,office,main
1373 | provide and install a small 2/1-2 fire extinguisher at front office
1374 | all doors shall be properly identified in case of an emergency or fire with the following wordage such as restroom, storage room, office electrical room exc.
1375 | remove all waste oil from ground area where located
1376 | apply for a cutting and welding permit or remove the hold rig from premises.
1377 | make application permit for flammable or combustible liquids storage and use class (2) and class 3b over 25 gallons inside of shop or 60 gallons outside type f-7 at 1002 Washington fire marshal's permit section
1378 | repair all emergency lights that are not working
1379 | NoData
1380 | NoData
1381 | NoData
1382 | NoData
1383 | NoData
1384 | NoData
1385 | NoData
1386 | NoData
1387 | NoData
1388 | NoData
1389 | NoData
1390 | NoData
1391 | NoData
1392 | NoData
1393 | NoData
1394 | NoData
1395 | NoData
1396 | NoData
1397 | NoData
1398 | NoData
1399 | NoData
1400 | NoData
1401 | The owner/occupant has the responsibility of correcting or abating all fire code violations or hazards that occur in the business.
1402 | All issued permits shall be kept on the premises and readily available for inspection by all fire code officials.
1403 | Always maintain approved occupancy of a building as stated be the certificate of occupancy. Failure to do so will result with the event being stopped until such conditions are corrected with the possibility of citations being issued.
1404 | Always renew or apply for permits that are required for the business at the City of Houston Fire Permit Office. All be permits are to be obtained prior to engaging in any activities, operations, practices, or functions regulated by this fire code.(any permit that is required for the business)
1405 | NoData
1406 | General cleaning needed.
1407 | Label electrical room.
1408 | Provide.
1409 | Post evacuation maps in each classroom. Make each map room specific.
1410 | Provide forms.
1411 | Mount fire extinguishers every 75ft. in hallway. One in kitchen area.
1412 | NoData
1413 | NoData
1414 | NoData
1415 | NoData
1416 | ol check, ol is 99, about 9 persons in club. issued permit renewal notice, p2 requested by G.O. Insp back in feb,2013. reinspect on 11-23-13. current permit expired in dec. 2012
1417 | NoData
1418 | NoData
1419 | NoData
1420 | NoData
1421 | NoData
1422 | NoData
1423 | NEED SERVICE 6-18 LAST DATE
1424 | NoData
1425 | NoData
1426 | NoData
1427 | NoData
1428 | NoData
1429 | NoData
1430 | JACQELINE WILLIAMS 281 741 3693
1431 | PUT BACK MISSING CEILING TILES IN BOILER ROOM.
1432 | REQUIRED SERVICE OUT OF DATE
1433 | NoData
1434 | Repair ASAP.
1435 | A4-GATE PERMIT EXPIRED 8-12-20K1- 911 KEY BOX PERMIT EXPIRED 8-3-19
1436 | FIRE ALARM PANEL NEEDS ANNUAL TESTING
1437 | LAST FIRE EXTINGUISHER INSPECTION EXPIRED SEPTEMBER 2020
1438 | INFORMATION
1439 | INFORMATION
1440 | POST THE CERTIFICATE OF OCCUPANCY
1441 | NoData
1442 | NoData
1443 | NoData
1444 | expired fire extinguishers 5/1/2019
1445 | NoData
1446 | NoData
1447 | NoData
1448 | INFORMATION ONLY
1449 | INFORMATION ONLY
1450 | NoData
1451 | NoData
1452 | NoData
1453 | Ansul inspection due by end of this month 1-31-21
1454 | NoData
1455 | NoData
1456 | Have a licensed fire protection company inspect/tag the vent hood suppression systems and clean the vent hoods.
1457 | The fire alarm was red tagged on 1/5/2021 for phone lines down. Corrections must be made to bring the alarm back into full operational condition within 72 hrs. This includes restoration of the phone lines as well as inspection and retagging by a certified fire alarm company.
1458 | NoData
1459 | NoData
1460 | NoData
1461 | The fire extinguishers are required to have annual inspection tags.
1462 | Provide filler plates for the openings in the breaker panel.
1463 | NoData
1464 | NoData
1465 | NoData
1466 | NoData
1467 | NoData
1468 | NoData
1469 | NoData
1470 | NoData
1471 | NoData
1472 | NoData
1473 | NoData
1474 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
1475 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
1476 | Provide documentation/report for annual Load testing and any necessary repairs.
1477 | Provide documentation/report for 5 year FDC testing and any necessary repairs.
1478 | Provide documentation/report for fire damper testing and any necessary repairs.
1479 | Repaint Fire Lane
1480 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
1481 | Post the occupant load.
1482 | NoData
1483 | NoData
1484 | NoData
1485 | NoData
1486 | PROVIDE EXIT SIGNS -KITCHEN -D107 STORAGE
1487 | STORAGE SHALL BE SEPARATED FROM HEATERS OR HEATING DEVICES BY DISTANCE OR SHIELDING SO IGNITION CANNOT OCCUR. -STOVE C113
1488 | PROVIDE DOCUMENTATION FOR DETECTOR SENSITIVITY TESTING. VERIFY ALL DETECTOR SENSITIVITY IS IN WORKING CONDITION.
1489 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL OF THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY 3 YEARS. PROVIDE WRITTEN DOCUMENTATION OF AUDIBILITY TESTING AND ANY DOCUMENTATION REGARDING REPAIRS OF ANY FAILURES
1490 | REPAIR EXIT SIGN. -T261 B
1491 | MEANS OF EGRESS (EXIT ACCESSES, EXITS OR EXIT DISCHARGES) SHALL BE CONTINUOUSLY MAINTAINED FREE FROM OBSTRUCTIONS OR IMPEDIMENTS. -BACK OF STAGE
1492 | PROVIDE PORTABLE FIRE EXTINGUISHERS -T202 A,B -T217 A,B -T210 A,B -C113
1493 | CURRENT-UP TO DATE FIRE ALARM SYSTEM ANNUAL INSPECTION DATE: 8/1/2018 ACCEPTABLE BLUE TAG SPRINKLER SYSTEM INSPECTION DATE: N/A ANNUAL FIRE EXTINGUISHER INSPECTION DATE: 7/2018 ANSUL SYSTEM BI-ANNUAL INSPECTION DATE: N/A
1494 | MAINTAIN ADEQUATE CLEARANCE BELOW CEILING AT ALL TIMES. 2 FEET OR MORE IN NONSPRINKLERED AREAS OF BUILDINGS -GYM STORAGE
1495 | MAINTAIN ADEQUATE CLEARANCE TO ALL ELECTRICAL SERVICE EQUIPMENT AT ALL TIMES. MARK THE NECESSARY ELECTRICAL CLEARANCE AND PROVIDE SIGNAGE. -GYM STORAGE
1496 | AN AUTHORIZED GENERATOR SERVICE COMPANY SHALL CONDUCT AN ANNUAL LOAD TEST WITH THE AVAILABLE EPSS LOAD AND SUPPLEMENTAL LOADS. PROVIDE DOCUMENTATION OF TESTING.
1497 | BOILER CERTIFICATE OF OPERATIONS SHALL BE MAINTAINED ON PREMISES. PROVIDE CERTIFICATES
1498 | AN APPROVED LICENSED MASTER ELECTRICIAN OR LICENSED ELECTRICAL SERVICE COMPANY SHALL TEST ALL EMERGENCY LIGHTING SYSTEMS ANNUALLY. PROVIDE WRITTEN DOCUMENTATION OF TESTING AND RESULTS. ANY FAILURES OF THE EMERGENCY LIGHTING SYSTEM SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
1499 | AN APPROVED HVAC COMPANY SHALL CONDUCT A FULL-FUNCTION TEST AND MAINTENANCE ON ALL FIRE DAMPERS AT LEAST EVERY 4 YEARS. PROVIDE DOCUMENTATION FOR TESTING AND ALL NECESSARY REPAIRS.
1500 | A 704 Placard must be installed in the following areas, unobstructed from the view of emergency responders during a spill or fireThe fence leading into the main entranceThe entrance doors into the warehouseThe LPG cageThe degree of severity for placards installed on the fence and doors will reflect that of the commodity with the most severe "health", "flammability", "instability" and "special hazards" in each category on location.The 704 placard for the LPG cage will reflect identifiers only for LPG
1501 | An alarm system must be installed to monitor the extinguishment system as required by code.
1502 | For Reference
1503 | For Reference
1504 | For Reference
1505 | Hazardous materials have been reduced below MAQ and separation for corrosives achieved.
1506 | Hazardous materials have been removed and secondary containment is no longer required.
1507 | The following permits must be obtained from the Permitting office by Tuesday, Aug 1, 2020K1 - Keybox PermitH1 - Tier II Permit for hazardous materialsL1 - LPG
1508 | For Reference
1509 | For Reference
1510 | Citation issued to Lois Tennen for the failure to maintain storage at the proper heights after multiple requests.
1511 | Failure to maintain proper storage height throughout the storage facility. Only 2,500 square feet may be used for High Piled storage. Ordinary combustibles must be stored below 12'. Plastic and high hazard below 6'.
1512 | The proper storage height must be maintain throughout the facility. As defined by code:HIGH-PILED COMBUSTIBLE STORAGE. Storage of combustible materials in closely packed piles or combustible materials on pallets, in racks or on shelves where the top of storage is greater than 12 feet (3658 mm) in height. When required by the fire code official, high-piled combustible storage also includes certain high-hazard commodities. such as rubber tires. Group A plastics. flammable liquids, idle pallets and similar commodities, where the top of storage is greater than 6 feet (1829 mm) in height.HiGH-PILED STORAGE AREA. An area within a building which is designated. intended, proposed or actually used for high-piled combustible storage.An area of 2,500 square feet is allowed to be designated high-piled because the facility is fully sprinklered. Have areas for storage at 12 feet marked so that the allowable heighth is not exceeded.
1513 | For Reference
1514 | NoData
1515 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL OF THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY 3 YEARS. LAST AUDIBILITY TEST DATED: UNKNOWN PROVIDE WRITTEN DOCUMENTATION OF AUDIBILITY TESTING AND ANY DOCUMENTATION REGARDING REPAIRS OF ANY FAILURES
1516 | CURRENT INFORMATION -FPS FIRE ALARM SYSTEM ANNUAL INSPECTION DATE: 2/18/2019 ACCEPTABLE BLUE TAG SPRINKLER SYSTEM INSPECTION DATE: 7/11/2019 BT/YT/SERVICE TAG ANNUAL FIRE EXTINGUISHER INSPECTION DATE: 6/2019, 7/2019 ANSUL SYSTEM BI-ANNUAL INSPECTION DATE:7/2019
1517 | REMINDER: ALL CURTAINS, DRAPERIES, HANGINGS AND OTHER DECORATIVE MATERIALS SHALL MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701 OR BE NONCOMBUSTIBLE. PROVIDE CERTIFICATE OF FLAME RESISTANCE (SEE FIRE CODE BELOW, 807.2) OR REMOVE ALL THAT DO NOT MEET THE CRITERIA.
1518 | AN APPROVED LICENSED MASTER ELECTRICIAN OR LICENSED ELECTRICAL SERVICE COMPANY SHALL TEST ALL EMERGENCY LIGHTING SYSTEMS ANNUALLY. LAST TEST DATE: UNKNOWN PROVIDE WRITTEN DOCUMENTATION OF TESTING AND RESULTS. ANY FAILURES OF THE EMERGENCY LIGHTING SYSTEM SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
1519 | BOILER CERTIFICATE OF OPERATIONS SHALL BE MAINTAINED ON PREMISES. PROVIDE CERTIFICATE FOR #220266
1520 | PROVIDE SIGNAGE "FIRE ALARM PANEL" ON/BY DOOR WHERE THE FIRE ALARM SYSTEM PANEL IS LOCATED. -HEAD END 205B, 205 PROVIDE SIGNAGE "SPRINKLER RISER" ON DOORS WHERE THE SPRINKLER RISER IS LOCATED. -614 MECHANICAL
1521 | PROVIDE REPORT OF TEST RESULTS IF DECORATIVE MATERIALS ARE TO MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701. CERTIFICATE OF FLAME RESISTANCE SHALL INDICATE THE COLOR AND/OR NUMBER FOR ALL DECORATIVE MATERIALS THROUGHOUT SCHOOL. -BLUE CURTAINS ON STAGE -PROVIDE UPDATED CERTIFICATE FOR BLACK CURTAINS ON STAGE
1522 | A LICENSED SERVICE COMPANY SHALL CONDUCT HYDROSTATIC AND FLOW TESTS ON ALL FIRE DEPARTMENT CONNECTIONS EVERY 5 YEARS IN CONJUNCTION WITH THE STANDPIPE SYSTEM 5-YEAR TEST. PROVIDE REPORT FOR THE 5-YEAR TEST ON THE FIRE DEPARTMENT CONNECTION
1523 | AN APPROVED HVAC COMPANY SHALL CONDUCT A FULL-FUNCTION TEST AND MAINTENANCE ON ALL FIRE DAMPERS AT LEAST EVERY 4 YEARS. PROVIDE REPORT FOR THE FIRE DAMPER TEST AND ANY NECESSARY REPAIRS.
1524 | REPAINT THE FIRE LANE THROUGHOUT CAMPUS
1525 | EXTENSION CORDS AND FLEXIBLE CORDS SHALL NOT BE A SUBSTITUTE FOR PERMANENT WIRING. EXTENSION CORDS SHALL BE USED ONLY WITH PORTABLE APPLIANCES. REMOVE EXTENSION CORD HANGING FROM CEILING -1405 BOOKROOM (PROJECTOR)
1526 | REPLACE MISSING/DAMAGED CEILING TILES -1215 -GIRLS LOCKER ROOM -KILN ROOM, A2/A4
1527 | PROVIDE PORTABLE FIRE EXTINGUISHER -STUDIO 1, BY EXIT DOOR, KILN -1425 ICE ROOM
1528 | REPAIR EXIT DOOR -MAIN MECHANICAL ROOM (RIGHT SIDE DOOR) REMOVE PIANO FROM MEANS OF EGRESS -STAGE
1529 | LABEL "ELECTRICAL ROOM" -OUTSIDE DOOR (CUSTODIAL, COURTYARD)
1530 | PROVIDE REPORT OF TEST RESULTS IF DECORATIVE MATERIALS ARE TO MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701. CERTIFICATE OF FLAME RESISTANCE SHALL INDICATE THE COLOR AND/OR NUMBER FOR ALL DECORATIVE MATERIALS THROUGHOUT SCHOOL. PROVIDE CERTIFICATE OF FLAME RESISTANCE -STAGE CURTAINS (BLACK) -FLAGS NORTH AND SOUTH CAFETERIA
1531 | AN APPROVED LICENSED MASTER ELECTRICIAN OR LICENSED ELECTRICAL SERVICE COMPANY SHALL TEST ALL EMERGENCY LIGHTING SYSTEMS ANNUALLY. LAST TEST DATE: UNKNOWN. PROVIDE WRITTEN DOCUMENTATION/REPORT OF TESTING RESULTS AND MAINTAIN ON FILE FOR FIRE CODE OFFICIAL. ANY FAILURES OF THE EMERGENCY LIGHTING SYSTEM SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
1532 | CURRENT INFORMATION -FPS FIRE ALARM SYSTEM ANNUAL INSPECTION DATE: 6/20/2019 ACCEPTABLE BLUE TAG SPRINKLER SYSTEM INSPECTION DATE: N/A ANNUAL FIRE EXTINGUISHER INSPECTION DATE: 7/2019 ANSUL SYSTEM BI-ANNUAL INSPECTION DATE: 7/2019 2
1533 | PROVIDE SIGNAGE "FIRE ALARM PANEL" ON DOOR WHERE THE FIRE ALARM SYSTEM PANEL IS LOCATED. -118C ELECTRICAL
1534 | IDENTIFIED ELECTICAL HAZARDS SHALL BE ABATED. -MECHANICAL 4, ELECTRICAL WIRES HANGING -MECHANICAL ROOM, BRIDGADE HALL, ELECTRICAL WIRES HANGING
1535 | REPAIR TROUBLE ALERT ON FIRE ALARM PANEL
1536 | REMINDER.
1537 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL OF THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY 3 YEARS. LAST AUDIBILITY TEST DATED: UNKNOWN. PROVIDE WRITTEN DOCUMENTATION/REPORT OF AUDIBILITY TEST AND MAINTAIN ON FILE FOR FIRE CODE OFFICIAL. ANY FAILURES OF THE AUDIBILITY TESTING SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
1538 | AN APPROVED HVAC COMPANY SHALL CONDUCT A FULL-FUNCTION TEST AND MAINTENANCE ON ALL FIRE DAMPERS AT LEAST EVERY 4 YEARS. PROVIDE DOCUMENTATION/REPORT OF TESTING RESULTS AND MAINTAIN ON FILE FOR FIRE CODE OFFICIAL. ALL FAILURES OF THE FIRE DAMPER TESTING SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
1539 | REMINDER: ALL CURTAINS, DRAPERIES, HANGINGS AND OTHER DECORATIVE MATERIALS SHALL MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701 OR BE NONCOMBUSTIBLE. PROVIDE CERTIFICATE OF FLAME RESISTANCE (SEE FIRE CODE BELOW, 807.2) OR REMOVE ALL THAT DO NOT MEET THE CRITERIA.
1540 | PROVIDE SMOKE DETECTOR -MAIN MECHANICAL ROOM (LEFT SIDE)
1541 | REPAINT FIRE LANE THROUGHOUT ALL OF THE SCHOOL
1542 | PROVIDE EXIT SIGNS -MAIN MECHANICAL ROOM -STUDIO 1
1543 | CURRENT INFORMATION -FPS FIRE ALARM SYSTEM ANNUAL INSPECTION DATE: 3/25/2019 ACCEPTABLE BLUE TAG SPRINKLER SYSTEM INSPECTION DATE: 3/12/2019 ACCEPTABLE BLUE TAG ANNUAL FIRE EXTINGUISHER INSPECTION DATE: 6/2019 ANSUL SYSTEM BI-ANNUAL INSPECTION DATE:7/2019 (2)
1544 | POST ADDRESS ON BUILDING
1545 | PROVIDE SIGNAGE "FIRE ALARM PANEL" ON/BY DOOR WHERE THE FIRE ALARM SYSTEM PANEL IS LOCATED. -ROOM 505 (LIBRARY)
1546 | PROVIDE PORTABLE FIRE EXTINGUISHER -ROOM 125 (W/D) -ROOM 802 WOMEN'S COACH
1547 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL OF THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY 3 YEARS. LAST AUDIBILITY TEST DATED: UNKNOWN PROVIDE WRITTEN DOCUMENTATION/REPORT OF AUDIBILITY TEST AND MAINTAIN ON FILE FOR FIRE CODE OFFICIAL. ANY FAILURES OF THE AUDIBILITY TESTING SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
1548 | AN APPROVED LICENSED MASTER ELECTRICIAN OR LICENSED ELECTRICAL SERVICE COMPANY SHALL TEST ALL EMERGENCY LIGHTING SYSTEMS ANNUALLY. LAST TEST DATE: UNKNOWN PROVIDE WRITTEN DOCUMENTATION/REPORT OF TESTING RESULTS AND MAINTAIN ON FILE FOR FIRE CODE OFFICIAL. ANY FAILURES OF THE EMERGENCY LIGHTING SYSTEM SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
1549 | REMINDER.
1550 | AN APPROVED HVAC COMPANY SHALL CONDUCT A FULL-FUNCTION TEST AND MAINTENANCE ON ALL FIRE DAMPERS AT LEAST EVERY 4 YEARS. PROVIDE DOCUMENTATION/REPORT OF TESTING RESULTS AND MAINTAIN ON FILE FOR FIRE CODE OFFICIAL. ALL FAILURES OF THE FIRE DAMPER TESTING SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
1551 | PROVIDE REPORT OF TEST RESULTS IF DECORATIVE MATERIALS ARE TO MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701. CERTIFICATE OF FLAME RESISTANCE SHALL INDICATE THE COLOR AND/OR NUMBER FOR ALL DECORATIVE MATERIALS THROUGHOUT SCHOOL. PROVIDE UPDATED CERTIFICATE OF FLAME RESISTANCE -BLACK CURTAINS ON STAGE
1552 | REMINDER: ALL CURTAINS, DRAPERIES, HANGINGS AND OTHER DECORATIVE MATERIALS SHALL MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701 OR BE NONCOMBUSTIBLE. PROVIDE CERTIFICATE OF FLAME RESISTANCE (SEE FIRE CODE BELOW, 807.2) OR REMOVE ALL THAT DO NOT MEET THE CRITERIA.
1553 | THROUGHOUT SCHOOL. ALL TWO WAY COMMUNICATION NOT IN OPERATIVE CONDITION SHALL BE REMOVED.
1554 | REPAINT FIRE LANE THROUGHOUT SCHOOL
1555 | NoData
1556 | NoData
1557 | Repair or replace the emergency illumination on the exit signs.
1558 | The 5 year hydrostatic test must be completed on the sprinkler system.Compliance within 30 days.
1559 | Per NFPA 13, tires are considered high hazard commodities and must not be stored higher than 6 feet from the floor. The tire storage must be reduced to 6 feet in height through out the entire facility.Compliance within 30 days.
1560 | Tires permanently stored on loading dock and not part of the daily distribution operations, must be at least 50 feet from the buildingCompliance within 30 days.
1561 | Replace all missing ceiling tiles in office area.Compliance within 30 days.
1562 | Life safety equipment must be operational at all times. Refer to repairs needed on tag by Digital Alarm Systems and your licensed fire protection vendor's quote.Compliance within 30 days
1563 | Per NFPA 13, tires are considered high hazard commodities and must not be stacked higher than 6 feet.Compliance in 30 days.
1564 | Aisle widths must be maintained at all times to allow access and egress though out the warehouse.Compliance within 30 days.
1565 | Hydraulic design information shall be placed on all risers. NFPA 13 requires a legible Hydraulic information sign.1. Location of the design area or areas.2. Discharge densities over the design area or areas.3. Required flow and residual pressure demand at the base of the riser4. Occupancy classification or commodity classification and maximum permitted storage height and configuration.5. Hose stream allowance included in addition to sprinkler demand.6. The name of the installing contractor.Compliance in 30 days.
1566 | All tires must be removed from all corridors and hallways.Compliance within 30 days
1567 | Have a small extinguisher installed on each forklift with LPG fuel. These extinguishers must be serviced annually.
1568 | Yellow Tag deficiencies on the Suppression system must be corrected and the system maintained in operational readiness condition.
1569 | An L1 permit must be obtained for the LPG on site. This permit is purchased at the Houston Permitting Center 1002 Washington Ave, Houston TX 77002
1570 | NoData
1571 | Your h2 high-piled permit ($496.18) on 1/28/2020. Please make payment as instructed on this form.
1572 | NoData
1573 | NoData
1574 | Have egress lighting test performed, correct any deficiencies, and place report in binder.
1575 | Update expired keybox and fire alarm permits.
1576 | Place "Roof Access" sign on all doors leading to roof ladder (downstairs and upstairs doors in mech room)
1577 | Surge protectors must be plugged directly into wall outlets. Discontinue use of all surge protectors connected to extension cords.
1578 | Stage curtains have FR label sewn on - OK Remove all drapes/curtains/fabric/combustible 3D decorations that do not have FR certificates.
1579 | Do not exceed the maximum allowable wall coverage.
1580 | Last inspection 6/2019 - OK
1581 | Add one extinguisher to gym. Add one extinguisher to cafeteria.
1582 | Last inspection 6/7/19 - Blue, OK WIRES FOR RISER TAMPER SWITCH ARE EXPOSED. CONTACT ALARM COMPANY TO HAVE WIRES PLACED IN CONDUIT MOTION SENSOR FOR MAG LOCK ON FRONT DOOR IS MALFUNCTIONING AND DOES NOT RELEASE PROPERLY. REPAIR IMMEDIATELY AND HAVE MAG LOCKS TESTED EVERY SIX MONTHS
1583 | Obtain sensitivity report from alarm company and place in binder.
1584 | Have audibility test performed.
1585 | Last inspection 6/7/19 - Blue, OK
1586 | Place log in fire marshal binder.
1587 | Last drill 9/12/19. Drills are conducted every month.
1588 | Maintain required ceiling clearance.
1589 | Do not hang/suspend/display anything from ceilings.
1590 | FDC cap missing. Contact sprinkler company and have cap replaced.
1591 | No obstructed drills logged. At least 50% of fire drills must be obstructed.
1592 | Last hydro 7/15/19 - Blue, OK
1593 | Test dampers, correct any deficiencies, and place report in binder.
1594 | Do not decorate doors.
1595 | Training required annually. Keep documentation of training in Fire Marshal Binder
1596 | Inspector recommends that records of all employee safety training be in memo/letter form. The memo/letter should include the date, location, type of training received, whether any employees were absent from training, and the name & signature of the person conducting the training.
1597 | EOP OK
1598 | Compliance required within 60 calendar days.
1599 | Evacuation maps OK
1600 | Test system and place report in binder.
1601 | NoData
1602 | Your k1 Key/Fire Depository Box permit ($177.87) expired on 1/28/2020. Please make payment as instructed on this form.
1603 | Please have deficiencies noted on red tag corrected.
1604 | NoData
1605 | NoData
1606 | NoData
1607 | 4/2020 - OK
1608 | Remove all obstructions around fire extinguishers and prohibit future obstructions.
1609 | Correct all violations within 60 calendar days.
1610 | 4/21/2020 - Blue, OK
1611 | Have audibility test performed and provide documentation that any deficiencies were corrected.4/29/2020 - OK
1612 | 4/21/2020 - Blue, OK
1613 | 7/31/2019 - Blue, OK
1614 | No obstructed drills logged. Conduct and document obstructed fire drills.
1615 | Drill log is incomplete. Some months are missing. Update drill log and conduct drills every month.
1616 | Smart panel/internal sensitivity testing - OK
1617 | Label hallway side of door to room 135 with sign that indicates sprinkler riser room is inside classroom.
1618 | Have 90 minute egress lighting test performed and document correction of deficiencies.New installation 4/2020. Lights will need to be tested beginning 4/2021 and tested annually, thereafter.
1619 | Mag lock on right leaf of exit door near room 204 failed to release. Have mag lock repaired. Have all mag locks tested to ensure proper release (under normal operation and during fire alarm activation).
1620 | Conduct and document required annual fire safety training.
1621 | BUSINESS IS TO REPAIR ILLUMINATION LIGHTS NEAR WOMEN'S RESTROOM AREA
1622 | BUSINESS NEEDS SIGN ON OFFICE DOOR STATING ELECTRICAL ROOM OR PANEL
1623 | REPAIR CEILING TILES IN OFFICE
1624 | BUSINESS NEEDS TO APPLY FOR A CANDLE PERMIT IN ORDER TO CONTINUE USE OF STERNO CANDLES
1625 | BUSINESS IS TO APPLY FOR ASSEMBLY PERMIT IMMEDIATELY
1626 | BUSINESS IS TO APPLY FOR ASSEMBLY PERMIT IMMEDIATELY
1627 | BUSINESS MUST DISCONTINUE USE OF POWER STRIP INTO ANOTHER POWER STRIP
1628 | BUSINESS MUST MOVE SNACK STAND FROM BLOCKING EXTINGUISHER
1629 | MUST MOVE ALL COMBUSTIBLES AWAY FROM ELECTRICAL PANEL IN OFFICE
1630 | NoData
1631 | Have gate co. repair all 911 functions on all gates (automatic, failsafe, and manual gates). HFD needs access to all gates (vehicle and pedestrian). Gates can not be welded shut (HFD must have access). Gates that don't function properly when I return will be opened until repaired.
1632 | NoData
1633 | NoData
1634 | NoData
1635 | Have a licensed fire protection company service and tag the fire extinguishers.
1636 | Mount the fire extinguisher that's located on the ground.
1637 | Replace or repair missing or broken exit signs.
1638 | Exit signs are required to be illuminated and capable of emergency illumination.
1639 | Provide a key for the padlock on the gate.
1640 | Building Engineer: Pablo IbarraNO VIOLATIONS FOUND AT THIS TIME.
1641 | Exits are required to be unlocked while the building is occupied.
1642 | When exiting the front door, I noticed that the door hardware / locking mechanism does not meet code requirements for an "E" occupancy with an occupancy load greater than 50. All exits in an "E" occupancy with an occupancy load greater than 50 must have panic hardware, not require more than one motion to exit, and not require special knowledge. The existing hardware on the front door has an electronic deadbolt and a knob. Any occupant exiting the means of egress must be able to exit freely without having to wait on the electronic deadbolt to be released. Replace the front door hardware with panic bar type hardware. If you would like to keep the premisis secure, an electronic strike-lock mechanism may be used so the front door can remain locked from the outside at all times but occupants can also exit from the inside at all times. A magnetic locking device may also be used, but must be permitted by the City of Houston Electronic Lock Plans Checking Department through plans submittal. Magnetic locks must also be tied into the fire alarm system so that the mag- lock releases when the alarm is activated and require semi-annual testing. I would advise against mag-lock mechanism and would suggest strike-lock type.
1643 | When exiting the front door, I noticed that the door hardware / locking mechanism does not meet code requirements for an "E" occupancy with an occupancy load greater than 50. All exits in an "E" occupancy with an occupancy load greater than 50 must have panic hardware, not require more than one motion to exit, and not require special knowledge. The existing hardware on the front door has an electronic deadbolt and a knob. Any occupant exiting the means of egress must be able to exit freely without having to wait on the electronic deadbolt to be released. Replace the front door hardware with panic bar type hardware. If you would like to keep the premisis secure, an electronic strike-lock mechanism may be used so the front door can remain locked from the outside at all times but occupants can also exit from the inside at all times. A magnetic locking device may also be used, but must be permitted by the City of Houston Electronic Lock Plans Checking Department through plans submittal. Magnetic locks must also be tied into the fire alarm system so that the mag- lock releases when the alarm is activated and require semi-annual testing. I would advise against mag-lock mechanism and would suggest strike-lock type.
1644 | When exiting the front door, I noticed that the door hardware / locking mechanism does not meet code requirements for an "E" occupancy with an occupancy load greater than 50. All exits in an "E" occupancy with an occupancy load greater than 50 must have panic hardware, not require more than one motion to exit, and not require special knowledge. The existing hardware on the front door has an electronic deadbolt and a knob. Any occupant exiting the means of egress must be able to exit freely without having to wait on the electronic deadbolt to be released. Replace the front door hardware with panic bar type hardware. If you would like to keep the premisis secure, an electronic strike-lock mechanism may be used so the front door can remain locked from the outside at all times but occupants can also exit from the inside at all times. A magnetic locking device may also be used, but must be permitted by the City of Houston Electronic Lock Plans Checking Department through plans submittal. Magnetic locks must also be tied into the fire alarm system so that the mag- lock releases when the alarm is activated and require semi-annual testing. I would advise against mag-lock mechanism and would suggest strike-lock type.
1645 | Areas of refuge (including classroom / other when used in a lockdown / intruder situation, fire drill, shelter in place, etc.), must have some form of communication system or device(s) that are working order. Testing of such devices should be done on an annual basis. Such devices may be in the form of cell phones, two-way hand-held radios, an overhead built in intercom system, or hard-wired telephones in every room normally occupied by students. Provide dated documentation on school letterhead stating the type of devices that the school uses for drills of all types, and that all devices have been tested and all are in proper working condition.
1646 | Make all code violation corrections prior to the compliance date noted on page 1 of the report.
1647 | Provide current audibility test documentation within the last 3 years for the fire alarm system. Test documentation must have one of two things to be acceptable. A) Must show each audibility device's ambient decibel level and the decibel level when the device is active. The difference in DB level must fall within NFPA 72's acceptable range for the device to pass the test. OR B) A document from their company on company's letter head that has the following information - 1) Test date 2) Company's ACR# 3) Tester's FAL# 4) A statement that all audibility devices passed the audibility test as required by NFPA 72. Documentation should contain Company's ACR#, Tester's FAL#, and date.
1648 | Provide documentation for a current emergency egress light annual test. An approved licensed master electrician or licensed electrical service company shall test all emergency lighting systems annually. The battery units, whether of the acid or alkali type, shall be tested continuously for a minimum of 90 minutes. Failed devices shall be corrected prior to the re-inspection. Provide dated documentation stating the master electrician and/or company's certification number, and that all devices passed the 90-minute test.
1649 | NoData
1650 | Facility acquired Fire Lane permit and submitted proper documentation. Fire Lane has been approved.
1651 | Facility acquired Fire Lane permit and submitted proper documentation. Fire Lane has been approved.
1652 | NoData
1653 | NoData
1654 | NoData
1655 | Fire Alarm issues noted on tags shall be corrected.
1656 | NoData
1657 | NoData
1658 | 1) Replace missing ceiling tiles: -Parts Area -Server Room -Vestibule2) Correct open wiring through out the facility: -2nd Floor Mechanical room -Shop floor3) Mark Doors: -"Mechanical Room" - 2nd floor mechanical room -"Electrical Room" - sales area4) Ensure swinging fire doors are not blocked open: -Vestibule -Mechanical room door (remove stopper)5) Install 704 Hazard Placards: -Both entrance gates (highest hazard per category for any material on site) -Totes storing product (oil and coolant) -Propane cage -Door to rebuild area (for compressed gases) -Diesel Tank (outside) -Doors leading to Dyno room- diesel6) Replace the faded warning labels on the outside diesel tank: Diesel, No Smoking7) Pipe labeling: -Label the piping conveying diesel from the outside tank to the dyno room: product and flow direction8) Place totes being utilized for distributing product on containment pallets for spill control
1659 | NoData
1660 | NoData
1661 | NoData
1662 | NoData
1663 | NoData
1664 | NoData
1665 | NoData
1666 | NoData
1667 | NoData
1668 | NoData
1669 | NoData
1670 | NoData
1671 | FYI:109.2 Owner/occupant responsibility. Correction and abatement of violations of this code shall be the responsibility of the owner. If an occupant creates, or allows to be created, hazardous conditions in violation of this code, the occupant shall be held responsible for the abatement of such hazardous conditions.
1672 | FYI: 105.3.5 Posting the permit. Issued permits shall be kept on the premises designated therein at all times and shall be readily available for inspection by the fire code official.
1673 | THE ALARM SYSTEM IS RED TAGGED - RED TAG WAS ISSUED 12/31/2020 AND SYSTEM MUST BESERVICED OR REPAIRED IMMEDIATELY
1674 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY
1675 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
1676 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit - (K1) REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMFlammable and Combustible Permit - (F7) REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMFire Alarm Permit -REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMElevator Operating Permit -REQUIRED; TO BE POSTED IN THE ELEVATOR ROOM OR WITHIN 10FT OF THE ELEVATOR CALL BUTTONSBoiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancy -REQUIRED; TO BE POSTEDFire Depository Box Permit - (K1)REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMThese are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30CALENDAR DAYS
1677 | NoData
1678 | NoData
1679 | NoData
1680 | NoData
1681 | NoData
1682 | NoData
1683 | NoData
1684 | NoData
1685 | NoData
1686 | NoData
1687 | NoData
1688 | NoData
1689 | NoData
1690 | NoData
1691 | NoData
1692 | NoData
1693 | NoData
1694 | NoData
1695 | NoData
1696 | NoData
1697 | NoData
1698 | NoData
1699 | NoData
1700 | NoData
1701 | NoData
1702 | NoData
1703 | NoData
1704 | NoData
1705 | NoData
1706 | NoData
1707 | NoData
1708 | NoData
1709 | NoData
1710 | NoData
1711 | NoData
1712 | NoData
1713 | NoData
1714 | NoData
1715 | NoData
1716 | NoData
1717 | NoData
1718 | NoData
1719 | NoData
1720 | NoData
1721 | NoData
1722 | NoData
1723 | NoData
1724 | NoData
1725 | NoData
1726 | NoData
1727 | NoData
1728 | All violations listed in this report must be corrected within 30 DAYS in order to avoid citations and re-inspection fees.
1729 | On 6/12/2020 the fire alarm was yellow tagged for deficiencies. Have a certified fire alarm company correct all deficiencies to bring the system back into full operation with no impairments within 30 DAYS, ensuring that a correction tag is placed once repairs are complete.
1730 | Have the required 2 year gas test performed and retain the approved permit on site, as set forth by state requirements for day cares. (the last gas test was noted as 3/1/2018)
1731 | NoData
1732 | NoData
1733 | NoData
1734 | NoData
1735 | NoData
1736 | NoData
1737 | NoData
1738 | NoData
1739 | NoData
1740 | NoData
1741 | NoData
1742 | NoData
1743 | NoData
1744 | Any where there is on covered wire needs to be covered up properly
1745 | Your fire alarm system needs to have it's annually test done
1746 | All sheet rock that is damage or missing needs to be repaired
1747 | All firestops need to be repaired up to standard no damage and holes allowed
1748 | Marker is required for location of all fire hydrants
1749 | Time to renew your permits
1750 | Need to be hung correctly no wires showing and emergency lights working on all exit signs
1751 | Time to renew your permits
1752 | Where your pedestrian gates are located we need access to the property so each 911 box need to have some type of fob
1753 | Need all permits on location at all times in a book or in a frame on the wall
1754 | It needs to have placement of fire hydrants on it an exit and entrance direction also needs to be seen at night
1755 | I need a technical report for your fire hose and your fire alarm
1756 | NoData
1757 | Fire extinguishers need annual inspection, need to be mounted on the wall, cannot be obstructed.
1758 | Fire extinguishers need annual inspection, need to be mounted on the wall, cannot be obstructed.
1759 | Fire extinguishers need annual inspection, need to be mounted on the wall, cannot be obstructed.
1760 | Repair ASAP.
1761 | NoData
1762 | K1 permit expired 12/26/20
1763 | NoData
1764 | NoData
1765 | NoData
1766 | NoData
1767 | NoData
1768 | Fire extinguishers must have current inspection tags.
1769 | NoData
1770 | NoData
1771 | NoData
1772 | NoData
1773 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
1774 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES PER CODE AND KEEP UPDATED. TRAIN QUARTERLY.
1775 | GET GAS LINE PRESSURE TEST EVERY 5 YEARS.
1776 | provide an extra key from your gate lock entrance on east side location ,so key can be place inside 911 key box in case of fire or other emergencies. Key to be place inside the emergency box with on duty fire marshal inspector
1777 | apply for a flammable or combustible liquid permit (f-7)if your going to store more than (5) gallons of gasoline inside premises. or more than (25) gallons of waste oil inside of garage
1778 | apply for a certificate of occupancy from the building department at 1002 Washington .
1779 | NoData
1780 | remove all L.P. compress gas bottles or apply for a cutting and welding permit at 1002 Washington fire permit section
1781 | NoData
1782 | remove plastic cans for storage of gas and provide an approved metal gas can for storage of (5) gallons with out a permit
1783 | Make application for a certificate of occupancy on line occupancy .inspections@houstontx.gov or call 8323948880 or 8323938880 for application
1784 | NoData
1785 | Fire extinguishers must have current inspection tags.
1786 | Maintain shop clear of combustibles.
1787 | Please renew expired key box permit (12/28/2020)
1788 | Repair ASAP.
1789 | Post the occupant load.
1790 | Remove obstructions in front of the fire extinguisher.
1791 | NoData
1792 | COMPLIANCE DATE 30 CALENDAR DAYS
1793 | INSURE ELEVITOR IS SERVICED AND PERMITS ARE AQUIRED ACCORDING TO THIS CODE.
1794 | NoData
1795 | NoData
1796 | NoData
1797 | Approved, no violations found.
1798 | Provide proof of a natural gas leak test within the last 5 years.
1799 | 1 Boiler Room is missing the certificate.
1800 | NoData
1801 | Have a licensed fire protection company service and tag the ansul system. The vent hood is due for cleaning.
1802 | AISLES WIDTHS STATED ON THE APPROVED PLANS ARE NOT BEING MAINTAINED AND SHALL BE BROUGHT INTO COMPLIANCE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1803 | ENSURE THAT THE TRASH DUMPSTER IS NOT STORED INSIDE THE BUILDING CREATING A FIRE HAZARD.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1804 | PORTABLE FIRE EXTINGUISHERS SHALL BE LOCATED IN CONSPICUOUS LOCATIONS WHERE THEY WILL BE READILY ACCESSIBLE AND IMMEDIATELY AVAILABLE FOR USE. FIRE EXTINGUISHER SHALL BE 75 FEET THROUGHOUT THE WAREHOUSE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1805 | remove metal fence bars in order for water hydrant to properly function in case fires or other usage done by the city of Houston water department and fire fighters able to fully open water pressure with spanner wrench on top of hydrant.
1806 | move metal fence bars obstructing water hydrant
1807 | remove metal bars on fence for water hydrant clearance
1808 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
1809 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
1810 | Provide Documentation/Report and tag for the 5th Year FDC Hydrostatic test
1811 | Inspect and Service tag commercial kitchen hood system. Correct all red tag impairments immediately.
1812 | Correct 6/27/2017 Yellow tag (5 year FDC) on Sprinkler System
1813 | Provide documentation/report for fire damper testing and any necessary repairs.
1814 | Your a4 - Access Gate and k1 - Key/Fire Depository Box permits ($444.66) expired 2/8/2020. Follow the instruction provided in the form above to pay for the renewal.
1815 | NoData
1816 | NoData
1817 | Your h2 - Hi-Pile Storage permit ($) expired 4/2/2020. Follow the instruction provided on the form above to pay for the renewal.
1818 | Amount Due: $379.43
1819 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
1820 | Fire Alarm and Sprinkler System Annual Inspection is out of date.
1821 | Fire Alarm and Sprinkler System Annual Inspection is out of date.
1822 | Entrance Toggle Switch is not working.
1823 | Fire Alarm and Sprinkler Systems have been tagged Impaired. Make all corrections.
1824 | NoData
1825 | NoData
1826 | Last intercom test 8/6/19 - OK These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1827 | Update expired fire alarm permit. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1828 | Do not hang/suspend/display anything from ceilings. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1829 | Do not exceed the maximum allowable wall coverage. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1830 | Last sensitivity 9/11/19 - OK These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1831 | Drills logged monthly - OK These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1832 | Do not obstruct any marked exit doors. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1833 | Remove all curtains/fabric unless the manufacturer or a certified laboratory has provided verification that the material is flame resistant. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1834 | Last inspection 8/2018 Have all extinguishers inspected. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1835 | Last hydro 7/26/19 - Blue, OK These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1836 | Test all dampers, correct any deficiencies, and place report in binder. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1837 | Last egress lighting test 8/3/18 Perform egress lighting test and correct any deficiencies. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1838 | Do not decorate doors. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1839 | Compliance required within 90 calendar days. Within 30 days, provide action plan for items that cannot be completed by compliance date. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1840 | Maintain required ceiling clearance. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1841 | Last gas test 5/21/19 - OK Place documentation in binder. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1842 | Replace/repair missing or damaged ceiling tiles and sheetrock. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1843 | Last inspection 9/2018 Have alarm system inspected. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1844 | Last audibility 12/2017 - OK These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1845 | Last inspection 8/13/19 - Yellow Have yellow tag corrected. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1846 | Last inspection 6/2019 - OK These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1847 | Ensure that FDC sign clearly lists address and system served. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1848 | Place updated log in binder. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1849 | Last training 9/26/19 - OK These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1850 | Emergency plan OK overall but fire drills require modification. The primary exit route for all students should be through the front doors and into the parking lot. Secondary exits will continue to be through rear exit doors and into the parking lot. District is working to improve walking surface and to install gates with panic hardware. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1851 | Place "Roof Access" signs on doors to all mechanical rooms that contain roof access ladders. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1852 | Conduct more obstructed fire drills. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1853 | Ensure that all rooms have evacuation maps and that they are not obscured by classroom decorations. These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1854 | Cover missing breaker slot in Panel L1 These codes shall carry over to new inspection report #313818: 2.7.4 - Damper Test510.1 - Roof Access Signage605.6 - Open Breaker Slot in Panel L1
1855 | Renew public assembly permit.
1856 | Ensure the rear exit is clear of trash and debris.
1857 | Move the obstructed fire extinguisher to a more accessible place.
1858 | Ensure the rear exit is unlocked while the building is occupied.
1859 | The vent hood is due for cleaning.
1860 | Secure the compressed gas cylinders.
1861 | Provide filler plates for the openings in the breaker panel. Replace the missing cover on the breaker panel.
1862 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
1863 | a1 & k4 permits expired 12/11/20
1864 | NoData
1865 | NoData
1866 | h3 permit expired 12/9/20
1867 | Renew the key box permit.
1868 | Renew the key box permit.
1869 | Renew the public assembly permit.
1870 | NoData
1871 | NoData
1872 | NoData
1873 | NoData
1874 | -Red/Yellow Tagged Fire Alarm System-Bad phone lines
1875 | Renew the hot works permit.
1876 | Renew the f7 fuel use and storage permit.
1877 | NoData
1878 | NoData
1879 | NoData
1880 | NoData
1881 | NoData
1882 | NoData
1883 | Repair the "fail safe" on the access gate.
1884 | Install a 911 key box near the key pad that will open the access gate.
1885 | MISSING (10:B/C) FIRE EXTINGUISHER(S) ON THE FORKLIFT(S) SHALL BE REPLACED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.FIRE EXTINGUISHER (S) ARE REQUIRED EVERY 75 FEET IN THE WAREHOUSE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1886 | THE EXIT PATHWAYS AND EXIT STAIRWAYS LEADING AWAY FROM THE WAREHOUSE SHALL HAVE A CLEAR PATH TO AN AREA OF SAFE REFUGE.COMPLIANCE: WITHIN 7 CALENDAR DAYS.
1887 | APPLY FOR AND OBTAIN A ACEES GATE PERMIT AND 911 KEY BOX PERMIT FROM THE CITY OF HOUSTON PERMITTING CENTER LOCATED AT 1002 WASHINGTON AVE. (832-394-9000). COMPLIANCE: WITHIN 30 CALENDAR DAYS.
1888 | An approved automatic extinguishing system is required on the spray booth.
1889 | NoData
1890 | NoData
1891 | Plans are required to be submitted to the building department.
1892 | Submit plans to the building department.
1893 | Submit plans to the building department.
1894 | NoData
1895 | Permit Expired 8/9/2020; Unpaid $385.38
1896 | Clear area by circuit boxes of all combustible materials.
1897 | Because your facility is unsprinkled, your only allowed 500 sq ft of high pile storage. Lack of a sprinkler system and a high-pile permit, all of your storage must be under 12 feet high. Mattresses maximum height is 6 feet.
1898 | Employees should be able to egress the facility
1899 | Storage shall be orderly and stacks shall be stable
1900 | Must have 2 feet clearance from the ceiling or storage at 12 feet of height because of no sprinkler system.
1901 | No extension cords used for permanent use
1902 | An automatic sprinkler system must be provided throughout all buildings containing a Group S-1 occupancy used for storage of upholstered furniture or mattresses exceeding 2,500 square feet.
1903 | All fire extinguishers must be mounted
1904 | Must have clear path exiting the building
1905 | Aisle clearance must maintained throughout the facility.
1906 | NoData
1907 | Make all code violation corrections prior to the reinspection date noted on page 1 of the Inspection Report.
1908 | Provide current audibility test documentation within the last 3 years for the fire alarm system.Test documentation must have one of two things to be acceptable. A) Must show each audibility device’s ambient decibel level and the decibel level when the device is active. The difference in DB level must fall within NFPA 72’s acceptable range for the device to pass the test. OR B) A document from their company on company’s letter head that has the following information – 1) Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all audibility devices passed the audibility test as required by NFPA 72. The Documentation should also contain the Company’s ACR#, the Tester’s certification #, and the date the test was performed.
1909 | Provide documentation for a current emergency egress light annual test.An approved licensed master electrician or licensed electrical service company shall test all emergency lighting systems annually. The battery units, whether of the acid or alkali type, shall be tested continuously for a minimum of 90 minutes.Failed devices shall be repaired or replaces as soon as possible. Provide dated documentation stating the master electrician and/or company's certification number, and that all devices passed the 90-minute test.
1910 | Provide documentation for a current damper test that is performed every 4 years.
1911 | Cover missing breaker slot in Panel L1.
1912 | Place "Roof Access" signs on doors to all mechanical rooms that contain roof access ladders.
1913 | NoData
1914 | NoData
1915 | NoData
1916 | NoData
1917 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY CODE VIOLATIONS AT ALL TIMES.
1918 | NoData
1919 | NoData
1920 | NoData
1921 | NoData
1922 | NoData
1923 | David Knighten 713 691 5453
1924 | NoData
1925 | NoData
1926 | NoData
1927 | NoData
1928 | Fire alarm permitCOcurrent
1929 | NoData
1930 | NoData
1931 | EMERGENCY EXIT ANDEGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOSTRECENT TEST EXIT SIGNS WERE FOUNDOUT/NOT ILLUMINATED ON THE FRONT DOOR AND IN THE HALLWAY -REPAIR OR REPLACE THEM IMMEDIATELY
1932 | EMERGENCY EXIT ANDEGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY - PROVIDE EVIDENCE OF MOSTRECENT TEST BOTH EXIT SIGNS WERE FOUNDOUT/NOT ILLUMINATED -REPAIR OR REPLACE THEM IMMEDIATELY
1933 | THE BACK EXIT DOOR MUST BE IDENTIFIEDAND LABELED ON THE EXTERIOR SIDE WITH THE BUSINESS NAME AND/OR ADDRESS
1934 | ENSURE THAT A SMOKEDETECTOR IS PROVIDED IN THE HALLWAY WHERE THE MASSAGE ROOMS ARE LOCATED
1935 | PROVIDE A SMOKE DETECTOR IN THE HALLWAY
1936 | CONTACT A CERTIFIEDPLUMBER TO CONDUCT A GAS TEST IF GAS TEST WAS CONDUCTED MORE THAN FIVE YEARSAGO
1937 | A PERMITAND A LICENSED PLUMBER MUST BE OBTAINED PRIOR TO CONDUCTING A GAS TEST -CONTACT THE HOUSTON PERMITTING CENTER 832.394.8811 FOR MORE INFORMATION
1938 | CONTACT A CERTIFIEDPLUMBER TO CONDUCT A GAS TEST IF GAS TEST WAS CONDUCTED MORE THAN FIVE YEARSAGO PROVIDE EVIDENCE OFLAST GAS TEST AND KEEP DOCUMENTS/PROOF OF TESTING ON SITE AND READY FORINSPECTION AT ALL TIMES A PERMITAND A LICENSED PLUMBER MUST BE OBTAINED PRIOR TO CONDUCTING A GAS TEST -CONTACT THE HOUSTON PERMITTING CENTER 832.394.8811 FOR MORE INFORMATION
1939 | PROVIDE AN EXIT SIGNON THE ROOM WHICH LEADS TO THE REAR EXIT AND ANOTHER ONE ON THE ACTUAL EXIT DOOR
1940 | PROVIDE AN EXIT SIGNON THE ROOM WHICH LEADS TO THE REAR EXIT AND ON THE REAR EXIT DOOR
1941 | THE CERTIFICATE OF OCCUPANCY AND ALLREQUIRED PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES
1942 | OBTAIN CERTIFICATE OFOCCUPANCY FROM THE HOUSTON PERMITTING CENTER THE CERTIFICATE OF OCCUPANCY AND ALLREQUIRED PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES
1943 | NoData
1944 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THEPROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THEPREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEALALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURINGSUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIREDPRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THEFIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THATARE AN IMMEDIATE LIFE SAFETY HAZARD
1945 | A SIGN OR ADHESIVE STATING "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING ISOCCUPIED" MUST BE POSTED ON OR NEAR THE FRONT ENTRANCE DOOR AND THE ROOM TO THE REAR EXIT DOOR AND THE REAR EXIR DOOR ALL SECURITY GRILLSAND SECURITY GRILL DOORS SHALL REMAIN OPEN (AND SECURED AND LOCKED IN THE OPENPOSITION) WHILE THE BUSINESS IS OCCUPIED, OPEN AND OPERATING
1946 | A SIGNOR ADHESIVE STATING "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED" MUST BEPOSTED ON OR NEAR THE FRONT ENTRANCE DOOR AND THE BACK EXIT DOOR THE SECURITY GATE ON THE EXTERIOR REAR EXIT MUST REMAIN UNLOCKED DURING BUSINESS HOURS
1947 | replace missing spacer
1948 | Label sprinkler room
1949 | Repair missing sheetroom
1950 | Service yellow tag
1951 | NoData
1952 | NoData
1953 | NoData
1954 | NoData
1955 | #NAME?
1956 | - PROVIDE INTERCOM TEST - REQUIRED EVERY 2 YEARS
1957 | NoData
1958 | EXPIRED P2 PERMIT
1959 | NoData
1960 | EXPIRED K1 PERMIT
1961 | EXPIRED K1 PERMIT
1962 | EXPIRED K1 PERMIT
1963 | NoData
1964 | NEED SERVICE 8-19 LAST DATE
1965 | NEED SERVICE 3-19 LAST DATE IN ALL BUILDINGS
1966 | NEED SERVICE 3-19 LAST DATE
1967 | NoData
1968 | NoData
1969 | NoData
1970 | P2-PUBLIC ASSEMBLY PERMIT EXPIRED 12-13-20
1971 | LAST EMERGENCY LIGHT TEST 1-22-18BRING UP TO CODE
1972 | LAST INSPECTION ON SPRINKLER RISEROCTOBER 2018. BRING UP TO CODE.
1973 | LAST INSPECTION ON FIRE EXTINGUISHERS 9-2019BRING UP TO CODE
1974 | LAST ANSUL INSPECTION APRIL 2020. SEMI-ANNUAL INSPECTION. BRING UP TO CODE
1975 | AS PER CODE
1976 | INFORMATION
1977 | ELEVATOR PERMIT EXPIRED 3RD QUARTER OF 2020
1978 | Do not hang or display anything from ceilings.
1979 | Last audibility test 8/10/18 - OK
1980 | Last intercom test 11/5/19 - OK
1981 | Last gas test 3/12/19 - OK
1982 | Remove extension cord that is being used as permanent wiring in attic of school building.
1983 | Profide certificate of flame resistance for carpet that covers walls. Remove all curtains, drapes, fabrics, and 3D decorations that do not have FR certificates.
1984 | Do not exceed the maximum allowable wall coverage
1985 | Last inspection 3/2019 - OK
1986 | Add one dry chemical (2A:10BC) extinguisher to office hallway. Add one dry chemical (2A:10BC) extinguisher to front office. Add one dry chemical (2A:10BC) extinguisher to gym (near main entrance doors). Add one dry chemical (2A:10BC) extinguisher to choir loft in chapel.
1987 | Last inspection 8/16/19 - Blue, OK
1988 | Last damper test 4/19/16 - OK
1989 | No obstructed drills conducted yet this year. Conduct and log obstructed fire drills.
1990 | Do not decorate doors.
1991 | Slide bolts are prohibited. Remove deadbolt from gym entrance doors. If locking of doors is required, install approved panic hardware.
1992 | P2, A4, K1, and Fire Alarm permits current. Two P2 permits active for property. Inspector will cancel P2 permit for Bldg. C.
1993 | Compliance required within 60 calendar days
1994 | Inspector recommends that training records be kept in memo form.
1995 | Repair/replace missing and/or damaged ceiling tiles in gym storage room.
1996 | Prohibit the use of door stops on all fire rated doors.
1997 | Provide instructions for fire alarm and intercom systems
1998 | Last sensitivity 8/16/19 - OK
1999 | Last inspection 9/23/19 - OK
2000 | Current water heating appliances are classified as boilers, per Texas Boiler Law. Apply for State of Texas and City of Houston boiler permits. Apply for City of Houston boiler operator permit.
2001 | Maintain required celing clearance
2002 | Annual training required. Document training and place in binder.
2003 | Emergency plan OK
2004 | Last egress lighting test 8/20/19 - OK
2005 | Remove slide bolts and peep holes from fire rated doors. Repair door and door frame penetrations in accordance with NFPA 80.
2006 | Evacuation maps OK
2007 | Have all private hydrants inspected and tested. Correct any deficiencies, and place report in binder.
2008 | Replace all missing outlet covers. Repair hanging light fixture in school building attic. Remove high voltage wiring and conduit that once powered water heater in school building attic.
2009 | Last fire drill 11/19/19 - OK Monthly drills conducted.
2010 | NoData
2011 | NoData
2012 | 3/2020 - OK
2013 | Correct all violations within 60 calendar days.
2014 | Last inspection 8/10/2020 - Blue, OK
2015 | 8/10/2018 - OK
2016 | Last inspection 4/19/2016Have dampers inspected and provide documentation that any deficiencies were corrected.Inspected and serviced 1/29/2021 - OK
2017 | 9/2020 - OK
2018 | 3/12/2019 - OK
2019 | Conduct and document obstructed fire drills.
2020 | Monthly drills conducted and logged. No December drill due to campus shutdown (COVID). - OK
2021 | 8/16/2019 - OK
2022 | 8/10/2020 - OK
2023 | Conduct and document required annual fire safety training.NLN. No employees assigned to firefighting duties.
2024 | NoData
2025 | NoData
2026 | NoData
2027 | NoData
2028 | NoData
2029 | P2 permit is expired. Expired on 8/26/2020. Amount owed for permit 385.38 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
2030 | NoData
2031 | 10/2020 - OK
2032 | 10/12/2020 - Blue, OK
2033 | Last gas test 5/12/2017 - OK
2034 | Correct all violations within 60 calendar days.
2035 | Have audibility test performed and provide documentation that deficiencies were corrected.
2036 | Conduct and document required annual fire safety training.
2037 | Cover all open junction boxes and empty breaker slots.
2038 | Conduct and document obstructed fire drills (50%).
2039 | Conduct and document monthly fire drills.
2040 | Fire alarm panel is showing trouble. Have a licensed fire alarm company correct trouble condition(s).
2041 | Have detector sensitivity test performed and provided documentation that deficiencies were corrected.
2042 | Have 90 minute egress lighting test performed by a licensed electrician and provide documentation that deficiencies were corrected.
2043 | Ali Samani
2044 | Per the alarm company (Mrs. Ross) Firetron the 5 yr hydro is needed.
2045 | NoData
2046 | Provide Spacer inside 4th floor Electrical Room Panel.
2047 | NoData
2048 | NoData
2049 | Fire Hose, Fire Extinguishers and Fire Sprinkler System.
2050 | Provide Current Tags for Fire Hose, Fire Sprinkler System and Fire Extinguishers.
2051 | Provide for Fire Hose, Fire Extinguishers and Fire Sprinkler System.
2052 | Fire Command Room.
2053 | Provide 5-inch contrasting address numbers (11777 - B) within 3-feet of front entrance doors.
2054 | Provide Fire Depository Box Binder.
2055 | Replace Ceiling Tile at Stair "B" ground floor Exit. Repair Sheetrock Hole in 1st floor Janitor Room.
2056 | Replace Emergency Stair Signage inside Stair "A" 4th floor.
2057 | Throughout Property.
2058 | 7/2020 - OK
2059 | 11/25/2020 - Blue, OK
2060 | 7/25/2018 - OK
2061 | 12/21/2020 - Blue, OK
2062 | 2/20/2017 - YellowCorrected 1/1/2018 - OK
2063 | 1/2021 - OK
2064 | 7/30/2019 - OK
2065 | Monthly drills conducted and logged - OK
2066 | FR certs 2/27/2013 and 8/23/2002 - OK
2067 | 12/28/2017 - OK
2068 | Correct all violations within 60 calendar days.
2069 | Conduct and document required annual fire safety training.
2070 | Conduct and document obstructed fire drills.
2071 | Have 90 minute egress lighting test performed and provide documentation that deficiencies were corrected.
2072 | NoData
2073 | When supplies are dropped off, ensure the exit isn't blocked by the supplies.
2074 | Provide filler plates for the openings in the breaker panel.
2075 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
2076 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABTE AND CORRECT ALL LIFE SAFETY AND CODE VILATIONS AT ALL TIMES.
2077 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AND UPDATED AT ALL TIMES. TRAIN QUARTERLY.
2078 | OBTAIN CERTIFICATE OF OCCUPANCY.
2079 | NoData
2080 | NoData
2081 | NoData
2082 | Provide Current Annual Service Tags for the Fire Hose, Fire Extinguishers an Fire Sprinkler System.
2083 | Provide for 1) Fire Sprinkler System, 2) Fire Hose, and 3) Fire Extinguishers. Provide Fire Pump Weekly Test Log.
2084 | Provide Current Annual Inspection Tag.
2085 | Throughout Property.
2086 | Throughout Property.
2087 | Discontinue Storage inside Stair "A" ground floor Stairwell.
2088 | Fire Command Room.
2089 | Replace current "N" on address to the letter "B."
2090 | Provide Fire Depository Box Binder.
2091 | 1) Repair Sheetrock Holes on wall inside Fire Command Room. 2) Repair Sheetrock Hole on wall inside 3rd Floor Janitor Room.
2092 | Throughout Property.
2093 | NoData
2094 | NoData
2095 | NoData
2096 | Approved, no violations found.
2097 | emergency gates are allowed as long as you provide emergency 911 access to both sides of gate.
2098 | Please have a flow test done on all 5 private fire hydrants found on property.
2099 | please make sure all trash/debris is placed inside dumpster for removal.
2100 | fail safe" boxes are in need of repair. No pull cord is attached to chain for manual operation
2101 | Please identify all electrical cutoff with proper unit number.
2102 | visually inspect all draft stops for solid construction. Please repair any damaged draft stops.
2103 | 18" x 18" HFD 4 Sign is required at main gate.
2104 | Please place a blue reflector on driveway marking fire hydrant location.
2105 | working smoke alarms/notification devices located inside all sleeping units.
2106 | gas test was done on 3/2020 for all buildings.
2107 | Access Gate (A4) permit is expired.
2108 | All fire extinguishers must have current inspection tags.
2109 | NoData
2110 | NoData
2111 | A4,K1 permits are expired. Expired on 12/21/2020. Amount owed for permits 355.72Please pay for permits within 10 days of this notice. If more information is needed about permits contact the Fire Prevention Permit Office.
2112 | Have a licensed fire protection company correct the red tagged fire alarm panel.
2113 | Provide address numbers for the exterior of the business.
2114 | Remove the exit sign above the black door located next to the bathrooms.
2115 | Test all emergency illumination and replace or repair any inoperable emergency lighting.
2116 | Clear and maintain space in front of the breaker panels located in the closet.
2117 | Renew the C1 (open flame) permit before it expires on 12/23/20.
2118 | Have a licensed fire protection company perform an annual fire sprinkler inspection and correct any deficiencies.
2119 | Have a licensed fire protection company perform a 5 year FDC test and correct any deficiencies.
2120 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
2121 | NoData
2122 | Keybox Permit (K1) is expired.Access Gate Permit (A4) is expired.
2123 | NoData
2124 | NoData
2125 | NoData
2126 | NoData
2127 | Keybox Permit (K1) is expired. Access Gate Permit (A4) is expired.
2128 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT AL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
2129 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES AND UPDATED.TRAIN QUARTERLY.
2130 | Need annual test done
2131 | Have sprinkler system tested
2132 | Need to be inspected
2133 | Fire depositary box required mid rise apartment
2134 | All emergency lights must work
2135 | Repair all holes in sheet rock
2136 | Must be on entrance gates
2137 | Place at your location
2138 | Must have permit on location
2139 | Need all permits on location
2140 | All doors must have a sign stating what is behind each door.
2141 | Place all permits in a binder or frame
2142 | Must be in lights for night vision and place fire hydrant location on map
2143 | Required for residential occupancies
2144 | Failure to provide a corrective action plan in the time given after multiple extensions.
2145 | The 5 year hydrostatic test must be completed on the sprinkler system.Compliance within 30 days.
2146 | Per NFPA 13, tires are considered high hazard commodities and must not be stored higher than 6 feet from the floor. The tire storage must be reduced to 6 feet in height through out the entire facility.Compliance within 30 days.
2147 | Tires permanently stored on loading dock and not part of the daily distribution operations, must be at least 50 feet from the buildingCompliance within 30 days.
2148 | Replace all missing ceiling tiles in office area.Compliance within 30 days.
2149 | Life safety equipment must be operational at all times. Refer to repairs needed on tag by Digital Alarm Systems and your licensed fire protection vendor's quote.Compliance within 30 days
2150 | Per NFPA 13, tires are considered high hazard commodities and must not be stacked higher than 6 feet.Compliance in 30 days.
2151 | Aisle widths must be maintained at all times to allow access and egress though out the warehouse.Compliance within 30 days.
2152 | Hydraulic design information shall be placed on all risers. NFPA 13 requires a legible Hydraulic information sign.1. Location of the design area or areas.2. Discharge densities over the design area or areas.3. Required flow and residual pressure demand at the base of the riser4. Occupancy classification or commodity classification and maximum permitted storage height and configuration.5. Hose stream allowance included in addition to sprinkler demand.6. The name of the installing contractor.Compliance in 30 days.
2153 | All tires must be removed from all corridors and hallways.Compliance within 30 days
2154 | NoData
2155 | NoData
2156 | The owner/occupant is responsible for obtaining all permits and correcting all fire code violations.
2157 | Must place used oily rags in the metal container with the self closing lid.
2158 | Must place an exit sign above the exit door in the office.
2159 | Must obtain a hot works permit for the cutting/welding rigs.
2160 | Must have the exit sign and emergency lights repaired or replaced as needed to operate normally.
2161 | Must obtain the H3(Hot Works) and the F7(Flammable/Combustible Storage and Use) permits from the Houston Permitting Center located at 1002 Washington Avenue. Fire Permits are located on the second floor.
2162 | Must obtain a F7 permit for the storage of waste oil tanks located on the business property.
2163 | Must place "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED" on the rear exit door and the door must remain unlocked.
2164 | NoData
2165 | Assembly permit has expired and requires renewing.
2166 | NoData
2167 | NoData
2168 | NoData
2169 | M3 Fuel Dispense Permit Amount due: $385.38
2170 | NoData
2171 | NoData
2172 | NoData
2173 | NoData
2174 | NoData
2175 | NoData
2176 | NoData
2177 | NoData
2178 | NoData
2179 | NoData
2180 | NoData
2181 | k1 permit expired 12/16/20
2182 | NoData
2183 | A Fire Department stand-by may be required if red-tagged system is not serviced in a timely manner.
2184 | Fire alarm system is red tagged and must be serviced within 72 hours
2185 | Failure to service red tagged systems will be subject to citations and re-inspection fees.
2186 | Have egress lighting test performed.
2187 | Apply for combustible dust (D2) permit. Keybox permit #18081908 - approved on 11/19/19 Assembly (P2) permit #18081908 - approved on 11/19/19
2188 | Remove dead vines from classroom.
2189 | Last gas test 7/18/17 - OK
2190 | Discontinue use of power taps that do not have internal surge protection.
2191 | Do not exceed the maximum allowable wall coverage Remove all curtains, drapes, fabrics, and 3D decorations that do not have FR certificates.
2192 | Provide instructions for voice evacuation system.
2193 | NoData
2194 | Evacuation maps OK
2195 | Do not decorate doors.
2196 | Compliance required within 60 calendar days
2197 | Dispose of sawdust daily.
2198 | Do not hang or display anything from ceilings.
2199 | Provide detector sensitivity report.
2200 | Last inspection 1/3/19 - Blue Panel currently shows trouble. Have troule conditions corrected.
2201 | Provide emergency evacuation plan.
2202 | Classrooms exit directly outside. Obstructed drills not possible.
2203 | Maintain required celing clearance
2204 | For reference.
2205 | Last safety training 8/20/19 - OK
2206 | Drill log OK
2207 | Last audibility 7/31/17 - OK
2208 | NoData
2209 | NoData
2210 | P2 REQUIRED
2211 | P2 REQUIRED
2212 | P2 REQUIRED
2213 | P2 REQUIRED
2214 | EXPIRED PERMIT RENEWAL REQUIREDP2
2215 | NoData
2216 | NoData
2217 | NoData
2218 | NoData
2219 | NoData
2220 | NoData
2221 | MEMBERS OF THE FIRESAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR
2222 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR
2223 | Concerningfire drills during COVID-19, a link can be found by going to the "Resources" andthen clicking on "Notices"https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/
2224 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL
2225 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS
2226 | Take the Fire Warden Certification class online through the following link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottom to click onHigh-rise Fire Warden Certification Class.Print out the certificate of completion and keep it in a safe place where it can be accessed upon demand. REGISTER FOR FIRE WARDEN TRAINING AThttps://houstontx.gov/fire/HFMO/highrisecert.htmlAny Building Manager in need of High-Riseor Mid-Rise Atruim Certification Training may send attendees to the followingmonthly seminars at no cost. Monthly seminars are available for managementemployees and tenant fire wardens of high-rise buildings who need to becertified. Certificates shall be valid for a period of five years from the dateof training.There is no charge for attending theseseminars. The only cost incurred may be parking fees, if applicable. Manybuildings will have different fire safety features. The building managementfrom each building represented is required to inform its employees and FireWardens of their specific fire safety features to complete the certification. Please note this training is not valid forMid Rise Evacuation Training. For information on mid rise training please visitthe HFD Mid Rise Fire Certication Webpage.Additional training availability information:The Houston Fire Department has set up and implemented a list of all high-risebuildings for Fire Safety Plan approvals. This list was set up to ensure thatpriority is given to buildings that have the greatest need while also providingeach building an equal opportunity. The list of buildings is separated into twogroups based on whether the building is an occupancy where people sleep, suchas hotel, apartments, and condominiums or those buildings where people do notsleep, such as office buildings. Buildings are then sub-grouped by no sprinklersystem, partial sprinkler system, or complete sprinkler systems before sortingby building height. The highest priority building is the residential buildingthat is non-sprinklered, and the tallest in height. Our goal is to provide theneeded services to approve each building within a two-year cycle. Buildingsdesiring to expedite the process also have three additional options. 1. The monthly openhigh-rise certification seminar is for buildings that have requested to send alimited number of fire wardens and building management employees to a classthat is open to all high-rise buildings. The class information is not specificto any particular building and requires building management to supplement thetraining with their building specifics.2. An inspector/instructorin the Life Safety Bureau, Public Education Section - High-rise Fire SafetyPlan Approvals, may be obtained to provide training outside his regular workhours on an overtime basis. This may be done by contacting Diana Cardenas bye-mail at:diana.cardenas@houstontx.gov. This should be done prior to payment of arequired permit fee so that an instructor can be assigned to made contact withthe requesting party, to assist the requesting party with information on theapplication for over-time training and payment of the permit fees, and toschedule a mutually convenient training date.A City of Houston permit fee is required to schedule an inspector/instructor.The permit fee is $326.89 plus an admin fee of $29.18 (as of January 2019).3. Having a City of HoustonFire Marshal approved consultant perform the training. The process to receivean approved Fire Safety Plan consist of the three following essential trainingelements conducted by persons, institutions or companies approved by the FireMarshal according to regulations established by the Fire Marshal: aconsultation with building management, an approved certification training forFire Wardens and building employees, and a fire drill supervised by persons,institutions or companies approved by the Fire Marshal.
2227 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERAL ALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1
2228 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE
2229 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN
2230 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIREPROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY ORNON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEMIS RESTORED TO NORMAL OPERATIONAL STATUS
2231 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY
2232 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE
2233 | EVIDENCE OF INCOMPLETE OR NON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONING SYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRE CODE
2234 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED
2235 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIREDIF THE HIGH-RISE DOES NOT HAVE ANY OF THESESYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED)DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30 CALENDAR DAYS
2236 | NoData
2237 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
2238 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30 CALENDARDAYS
2239 | CITATIONS WILL BE WRITTEN AFTER 2REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT METWITHIN 90 DAYS CITATIONS WILL BE ISSUED IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 30 DAYS
2240 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
2241 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES AND KEEP UPDATED.TRAIN QUARTERLY.
2242 | NoData
2243 | Secure the compressed gas cylinders.
2244 | Have a licensed fire protection company perform a 5 year FDC test and correct any deficiencies.
2245 | NoData
2246 | Have a licensed fire protection company correct the deficiencies on the yellow tagged sprinkler system.
2247 | Have a licensed fire protection company perform an annual fire alarm inspection before the end of 01/2021.
2248 | Ensure the side exit is unlocked and free from obstructions while the building is occupied.
2249 | NoData
2250 | NoData
2251 | NoData
2252 | NoData
2253 | NoData
2254 | NoData
2255 | NoData
2256 | NoData
2257 | NoData
2258 | NoData
2259 | NoData
2260 | NoData
2261 | NoData
2262 | NoData
2263 | NoData
2264 | NoData
2265 | NoData
2266 | NoData
2267 | NoData
2268 | NoData
2269 | NoData
2270 | NoData
2271 | NoData
2272 | NoData
2273 | NoData
2274 | NoData
2275 | NoData
2276 | Correct all violations within 30 calendar days.Provide action plan for violations that cannot be corrected by reinspection date listed on Page 1.
2277 | Document extinguisher and fire code training.... 9/8/2020OK_.
2278 | Update and extend fire lane to T-buildings.
2279 | Remove all multi-outlet extension cords that do not have built-in surge protection, including those supplying power to Promethean boards.Working action plan. Funds to begin replacement will be available in July.
2280 | Update EOP for 20-21 school year.
2281 | District working action plan to relocate FDC. Construction completion date 10/15/2020, per action plan.
2282 | Install FDC sign after FDC is relocated.
2283 | 9/2019 - Have fire extinguishers inspected.
2284 | Correct all violations within 30 calendar days.Provide action plan for violations that cannot be corrected by reinspection date listed on Page 1.
2285 | Remove all multi-outlet extension cords that do not have built-in surge protection, including those supplying power to Promethean boards.Working action plan. Funds will be available in July.
2286 | Pay reinspection fee.
2287 | Provide documentation of extinguisher and fire code training.
2288 | Update EOP for 20-21 school year.
2289 | COMPLIANCE DATE: 15 CALENDAR DAYS
2290 | (D1) fire prevention permit is expired at this time.
2291 | Obtain a HFD Assembly permit.
2292 | P2 permit is expired. Expired on 12/17/2020. Amount owed 385.38 Please pay for permit within 10 days of this notice. If more information is needed about permit, contact the Fire Prevention Permit Office.
2293 | NoData
2294 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES
2295 | FDC MUST BE PRESSURE TESTED EVERY 5 YEARS AND TAGGED.
2296 | FILL SPACES IN THE ELECTRICAL PANEL TO PREVENT ELECTRICAL HAZARD.
2297 | Correct all violations within 30 calendar days.Provide action plan for violations that cannot be corrected by reinspection date listed on Page 1.
2298 | Document extinguisher and fire code training.
2299 | Add roof access sign to band hall custodial room.
2300 | Remove all multi-outlet extension cords that do not have built-in surge protection, including those supplying power to Promethean boards.Working action plan. Funds will be available in July.
2301 | Remove door stops from fire rated doors in kitchen.
2302 | Evacuation map in room 407 not updated. Ensure that all rooms have current evacuation maps.
2303 | Remove all 3D decorations from walls (Room 407, and any others)
2304 | NoData
2305 | Repair all red tag issues by 1/12/2021.
2306 | NoData
2307 | NoData
2308 | NoData
2309 | Permit Expired 11/7/2020; Unpaid Fees $266.80
2310 | Have all annex extinguishers inspected.
2311 | Correct all violations within 30 calendar days.Provide action plan for violations that cannot be corrected by reinspection date listed on Page 1.
2312 | Document extinguisher and fire code training.
2313 | Remove all multi-outlet extension cords that do not have built-in surge protection, including those supplying power to Promethean boards.Working action plan. Funds will be available July 2021.
2314 | Fire extinguishers must have current inspection tags.
2315 | NoData
2316 | NoData
2317 | NoData
2318 | NoData
2319 | NoData
2320 | NoData
2321 | NoData
2322 | NoData
2323 | NoData
2324 | NoData
2325 | NoData
2326 | NoData
2327 | NoData
2328 | NoData
2329 | NoData
2330 | NoData
2331 | NoData
2332 | NoData
2333 | Annual testing of Fire Alarm System required
2334 | Storage building has 2 exits that open up to a 6 ft drop off and road. Should these exits be considered exits?
2335 | Fire permits shall be renewed from the options sent back in August of 2020.Compliance by 2-19-2021
2336 | Your magnetic locks have never been approved through the City of Houston. Contact the building department using the information given to get your locks approved.Compliance by 2-19-2021
2337 | Your plastic bottles are considered high hazard commodities and maximum storage height for those products is 6 ft. unless approved for high piled storage. Lower all bottles and other plastic products to 6 ft and maintain that height unless approval occurs.Compliance by 2-19-2021
2338 | All buildings with designated letters per your Certificate of Occupancies shall be posted on the matching buildings.Compliance by 2-19-2021
2339 | Provide 2 Falcon Locks or Knox Boxes to replace the locks that no longer open on your front gates.Compliance by 2-19-2021
2340 | Secure all compressed gas bottles from the options listed above.Compliance by 2-19-2021
2341 | Have qualified door company perform annual drop test on all fire doors in your facility.Compliance by 2-19-2021
2342 | Have qualified sprinkler and alarm company perform annual testing on these systems.Compliance by 2-19-2021
2343 | All forklifts powered by propane or fuel shall have a tagged fire extinguisher mounted on the lift.Compliance by 2-19-2021
2344 | All fire extinguishers shall be mounted to a fixed object and not on floors.Compliance by 2-19-2021
2345 | Repair or replace all emergency lighting throughout your facility and provide documentation that all lights were working at that time.Compliance by 2-19-2021
2346 | Provide at least a 3 ft. clearance around all electrical boxes.Compliance by 2-19-2021
2347 | All exits lights shall be illuminated.Compliance by 2-19-2021
2348 | Remove all objects blocking the direct path to exits in the locations listed.Immediate compliance required.
2349 | Verify the Fire Alarm company submits plans and obtains permit.
2350 | Have the Fire Alarm Company provide plans to Plan Checking regarding new fire alarm system devices and relocated devices.
2351 | The Fire Alarm Company shall obtain installation permit regarding new fire alarm system devices and relocated devices.
2352 | Per our conversation- mount the extinguishers- see above for details
2353 | Per our conversation- mark the extinguishers- see above for details.
2354 | Per our discussion- provide a 2A 10BC extinguisher - see above for details
2355 | Trey Meyers
2356 | Per our discussion- maintain all exits free of obstructions and material
2357 | If the H3 permit is acquired- see above for the fire extinguisher needed
2358 | Apply for the F7 permit and the H3 permit if you decide to keep the welding equipment on site.
2359 | Per our conversation, this should be the first thing to apply for -certificate of occupancy.
2360 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRESUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALSAND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ONSITE FOR FIRE MARSHAL INSPECTION
2361 | WHERE LOCAL FIRE MARSHAL APPROVALS AREREQUIRED BY REGULATORY AGENCIES, APPROVED FIRE SAFETY AND EVACUATION PLANSSHALL BE PREPARED, MAINTAINED AND POSTED IN GROUP E OCCUPANCIES
2362 | NoData
2363 | INFORMATION TO BE INCLUDED IN FIRE EVACUATIONPLANS
2364 | POST ADDRESS CONSPICUOUSLY - THE LOCATION MUST HAVE A NUMERICAL ADDRESS WHICH IS CLEARLY VISIBLE FROM THE STREET
2365 | THE CERTIFICATE OF OCCUPANCY AND ALLREQUIRED PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES
2366 | MISSING ILLUMINATED EMERGENCY EXIT SIGNS MUST BE INSTALLED AND TESTED
2367 | INFORMATION TO BE INCLUDED IN FIRE SAFETYPLANS
2368 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
2369 | OBTAIN A CERTIFICATE OF OCCUPANCY AND ANY OTHER PERMITS REQUIRED PER THE CODE
2370 | NoData
2371 | REMOVE DEADBOLT (PLAYGROUND EXIT) AND LOCKING DOOR HANDLE (FRONT ENTRY/EXIT) WHICH ARE BEING USED IN CONJUNCTION WITH PANIC HARDWARE
2372 | NoData
2373 | NoData
2374 | NoData
2375 | NoData
2376 | NoData
2377 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
2378 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES AND KEEP UPDATED PER CODE. TRAIN QUARTERLY.
2379 | NoData
2380 | NoData
2381 | NoData
2382 | LSB2020.8.7.1 Emergency Fire Exit PlanEvery Foster Home shall have a diagrammed “Fire Emergency Exit Plan” indicating the exits of the residence. Discussions of what to do in case of fire and review of the fire emergency exit plan shall be gone over with each child and each member of the family, including a meeting place outside of the house to provide accountably of everyone, and the notification of the Fire Department by calling “9-1-1” from a safe location. This discussion and review shall take place monthly.Compliance: 30 calendar days.
2383 | NoData
2384 | NoData
2385 | EMERGENCY EXIT AND EGRESS LIGHTS MUST BE TESTED, AND INSPECTED ANNUALLY -PROVIDE EVIDENCE OF MOST RECENT TEST AND ENSURE ALL EXIT LIGHTS AND EMERGENCY LIGHTS/EYEBALLS ARE ILLUMINATING/FUNCTIONING - THE EXIT LIGHT AT THE FRONT ENTRANCE IS NOT ILLUMINATING
2386 | ALL HOODVENTS AND HOOD SUPPRESSION SYSTEMS MUST BE INSPECTED AND SERVICED AT LEASTEVERY 6 MONTHS - PROVIDE PROOF OF LAST INSPECTION AND CLEANING
2387 | THE CERTIFICATE OFOCCUPANCY AND FIRE ALARM PERMIT MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES - POST THE MOST RECENT FIRE PERMIT
2388 | FIRE ALARM PANEL IS BLUE TAGGED 10FEB20 AND LAST SENSITIVITY TEST CONDUCTED 1JUN26FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - AUG2020 EMERGENCY ESCAPE MAPS ARE ALL POSTED IN PLACE IN EACH CLASSROOM ALL FIRE DRILLS CONDUCTED MONTHLYANSUL SYSTEM IS BLUE TAGGED AUG2020
2389 | NoData
2390 | NoData
2391 | NoData
2392 | NoData
2393 | COMPLIANCE DATE: 48 HRS
2394 | SERVICE FIRE ALARM PANEL IMMEDIATELY.
2395 | SERVICE FIRE ALARM PANEL IMMEDIATELY.
2396 | SERVICE FIRE ALARM PANEL IMMEDIATELY.
2397 | Repair wall outlet.
2398 | Test emergency lighting at front door.
2399 | Remove extension cords used as permanent power.
2400 | Emergency lighting must be in working order.
2401 | NoData
2402 | NoData
2403 | NoData
2404 | NoData
2405 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL
2406 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - RECIEVED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - RECIEVED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - RECIEVED " Electronic Locks -Semi Annual - RECIEVED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - RECIEVED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - RECIEVED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - RECIEVED " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - RECIEVED " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS
2407 | CABINETS CONTAINING FIRE FIGHTING EQUIPMENT MUST INDICATE THE EQUIPMENT CONTAINED THEREIN - "FIRE HOSE" AND/OR "FIRE EXTINGUISHER" - CORRECTLY IDENTIFY CONTENTS OF CABINET ON THE 3RD FLOOR
2408 | RECEIVED; NO FURTHER ACTION NECESSARY
2409 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
2410 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
2411 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
2412 | THE MOBILITY IMPAIRED LIST MUST BE UPDATED EVERY 6 MONTHS
2413 | PROVIDE 2 ELEVATOR INDEPENDANT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX
2414 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS
2415 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
2416 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
2417 | THE EXIT DOOR ON THE 14TH FLOOR STAIR B DOES NOT LATCH CLOSED
2418 | ALL ELECTRICAL ROOMS, HVAC ROOMS, MECHANICAL ROOMS, IT ROOMS, ELEVATOR ROOMS, FIRE SPRINKLER RISER ROOMS, FIRE ALARM ROOMS AND TRANSFORMER ROOMS MUST BE LABELED AS SUCH FOR READY IDENTIFICATION - ID THE "PIT" AND ELEVATOR ROOM ON THE 10TH FLOOR, ID THE MECHANICAL ROOM ON THE 3RD FLOOR, ID THE MECHANICAL ROOM ALSO AS "DRY PIPE" ON THE 3RD FLOOR AND ACCESS TO THE GARAGE ELEVATORS THROUGH SUITE 620
2419 | PROVIDE DOCUMENTATION OR LETTER TO ENSURE ALL FIREPHONES AND JACKS (IN THE BUILDING ON ALL FLOORS) HAVE BEEN TESTED BY AN APPROVED, CERTIFIED FIRE PROTECTION COMPANY AND FUNCTIONING PROPERLY FIREFIGHTER PHONES AND ALL JACKS IN THE BUILDING MUST BE TESTED ANNUALLY
2420 | ADD FOBS FOR ENTRY TO ALL 5 SETS OF KEYS IN THE FDB WRITE CODE FOR ENTRY TO PUMP ROOM ON KEY TAG TO PUMP ROOM (ON ALL 5 SETS) READ AND REVIEW LSB STANDARD 6; FULL COMPLIANCE OF PROVIDING A PROPERLY SUPPLIED FIRE DEPOSITORY BOX IS REQUIRED IMMEDIATELY
2421 | PERTAINING TO PLACEMENT AND DISTANCE OF FIRE EXTINGUISHERS NEEDED THROUGHOUT THE PARKING GARAGE ENSURE THAT ENOUGH FIRE EXTINGUISHERS ARE SUPPLIED, OBVIOUS AND ACCESSIBLE IN THE PARKING GARAGE (AN S-2) NO FIRE EXTINGUISHERS WERE FOUND IN THE PARKING GARAGE - SUPPLY FIRE EXTINGUISHERS ON ALL LEVELS IN DISTANCES PRESCRIBED BY THE FIRE CODE
2422 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS
2423 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
2424 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
2425 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
2426 | DOOR CLOSER FOUND ON THE 14TH FLOOR (STAIR B) IS NOT WORKING PROPERLY - ENSURE DOORS ARE LATCHING SHUT ON ALL EXIT STAIRWELL DOORS
2427 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
2428 | PROVIDE SIGN ON THE DOOR OF THE PRESSURE WASHING CAGE IN THE GARAGE TO INDICATE THE PRESENCE OF DIESEL
2429 | THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH - IDENTIFY ACCESS TO THE ELECTRICAL ROOM THROUGH SUITE 350
2430 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
2431 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE
2432 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE
2433 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION
2434 | OBTAIN ALL REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER - F7 (FLAMMABLE LIQUIDS PERMIT) AND K1 (KEY BOX PERMIT) ARE DUE THE ALARM PERMIT COULD NOT BE LOCATED IN OUR SYSTEM VIA MY SEARCH - PLEASE VISIT THE HOUSTON PERMITTING CENTER AND OBTAIN THE FIRE ALARM PERMIT
2435 | THE EXIT DOOR ON THE 14TH FLOOR STAIR B IS STICKING - ENSURE ALL EXIT DOORS ARE CAPABLE OF OPENING WITH EASE
2436 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE ELEVATOR ROOM ON THE GROUND FLOOR IN JOE'S OFFICE & THE ELCTRICAL ROOM, ON THE 6TH FLOOR, MECHANICAL ROOMS ON THE 12TH & 13TH FLOORS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR
2437 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE)
2438 | ENSURE THE EMERGENCY "RE-ENTRY" BUTTON ON THE FIRE ALARM PANEL IS HIGHLIGHTED OR CONSPICUOUSLY LABELED
2439 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY
2440 | NoData
2441 | THE BACK EXIT DOOR AND ABOVE ACCESS GATE CONTROL TO SUITE 700 SHOULD BE LABELED "SUITE 700 ACCESS GATE CONTROL"
2442 | PROVIDE A COVER PLATE FOR EXPOSED ELECTRICAL OUTLET BEHIND THE UPS BOX ON THE GROUND FLOOR
2443 | ALL FIRE DETECTION AND FIRE SUPPRESSION ELEMENTS MUST BE FULLY FUNCTIONAL AND BLUE TAGGED
2444 | INSPECT ALL FIRE DETECTION AND FIRE SUPPRESSION EQUIPMENT TO ENSURE FUNCTIONALITY
2445 | THE FIRE ALARM IS RED TAGGED DUE TO A SPRINKLER ACCIDENT ON THE 2ND FLOOR; ENSURE ALL FIRE DETECTION EQUIPMENT (WIRING, CONNECTIONS, DETECTORS, PANELS, ETC) WHICH WAS EXPOSED TO WATER IS NOT DAMAGED OR REPLACED IF DAMAGED.
2446 | NOTIFICATIONMUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OFSERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT OR SERVICE TO THEOWNER/OCCUPANT AND TO THE JURISDICTION – BY PHONE 713.884.3143 AND EMAIL AT HFD.DISPATCH3@houstontx.govTHE FIREDEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMALOPERATIONAL STATUS
2447 | POST CERTIFICATE OF OCCUPANCY CONSPICUOUSLY ON SITE
2448 | NoData
2449 | NoData
2450 | NoData
2451 | NoData
2452 | THE ALARM SYSTEM IS RED TAGGED - RED TAG WAS ISSUED 12/31/2020 AND SYSTEM MUST BESERVICED OR REPAIRED IMMEDIATELY
2453 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY
2454 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
2455 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit - (K1) REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMFlammable and Combustible Permit - (F7) REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMFire Alarm Permit -REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMElevator Operating Permit -REQUIRED; TO BE POSTED IN THE ELEVATOR ROOM OR WITHIN 10FT OF THE ELEVATOR CALL BUTTONSBoiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancy -REQUIRED; TO BE POSTEDFire Depository Box Permit - (K1)REQUIRED; TO BE POSTED IN THE FIRE ALARM ROOMThese are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 30CALENDAR DAYS
2456 | NoData
2457 | NoData
2458 | NoData
2459 | NoData
2460 | NoData
2461 | install 2A:10BC fire extinguisher in corridor.
2462 | fire extinguisher with classification of 2a:10bc and higher required annual inspection.
2463 | as per code
2464 | install key box for main gate, provide keys for gates and main entrance.
2465 | follow Section 312
2466 | NoData
2467 | January 1, 2017 as battery operated single station alarm is replaced, that smoke alarm shall be replaced with tamper-resistant battery-operated single station smoke alarm.
2468 | Required every 5 years and must be completed with an approved permit from theBuilding Department
2469 | provide pedestrian gate.
2470 | repair entrance of 1301 and pedestrian door
2471 | keith Godfrey 832 693 9734
2472 | Post shall comply with section 312
2473 | NoData
2474 | NoData
2475 | NoData
2476 | NoData
2477 | NoData
2478 | NoData
2479 | LSB2020.8.7.1 Emergency Fire Exit PlanEvery Foster Home shall have a diagrammed “Fire Emergency Exit Plan” indicating the exits of the residence. Discussions of what to do in case of fire and review of the fire emergency exit plan shall be gone over with each child and each member of the family, including a meeting place outside of the house to provide accountably of everyone, and the notification of the Fire Department by calling “9-1-1” from a safe location. This discussion and review shall take place monthly.Compliance: 30 calendar days.
2480 | NoData
2481 | NoData
2482 | NoData
2483 | NoData
2484 | NoData
2485 | NoData
2486 | NoData
2487 | NoData
2488 | NoData
2489 | NoData
2490 | NoData
2491 | NoData
2492 | NoData
2493 | NoData
2494 | NoData
2495 | NoData
2496 | NoData
2497 | NoData
2498 | NoData
2499 | NoData
2500 | NoData
2501 | NoData
2502 | NoData
2503 | NoData
2504 | NoData
2505 | NoData
2506 | NoData
2507 | NoData
2508 | NoData
2509 | NoData
2510 | NoData
2511 | NoData
2512 | NoData
2513 | NoData
2514 | NoData
2515 | NoData
2516 | NoData
2517 | NoData
2518 | NoData
2519 | NoData
2520 | NoData
2521 | NoData
2522 | NoData
2523 | NoData
2524 | NoData
2525 | NoData
2526 | NoData
2527 | NoData
2528 | NoData
2529 | NoData
2530 | NoData
2531 | NoData
2532 | NoData
2533 | NoData
2534 | FIRE EXTINGUISHERS GOOD. DATED 10-1-21.
2535 | FIRE DRILL CONDUCTED WHILE ON SCENE.
2536 | FIRE ALARM PANEL UP TO DATE. DATED 1-23-21
2537 | INSTALL AN ABC PORTABLE FIRE EXTINGUISHER INSIDE THE STORE NEAR THE MAIN ENTRANCE/EXIT DOOR
2538 | MAKE SURE BOTH THE LEFT AND RIGHT SIDE EXIT DOORS REMAIN UNLOCKED DURING BUSINESS HOURS
2539 | REPLACE ALL MISSING CEILING TILES
2540 | APPLY FOR THE M3(FUEL DISPENSER PERMIT) AT 1002 WASHINGTON AVE. 832-394-8811
2541 | NoData
2542 | NoData
2543 | NoData
2544 | NoData
2545 | NoData
2546 | NoData
2547 | NoData
2548 | NoData
2549 | NoData
2550 | NoData
2551 | NoData
2552 | NoData
2553 | NoData
2554 | NoData
2555 | NoData
2556 | NoData
2557 | NoData
2558 | NoData
2559 | NoData
2560 | NoData
2561 | NoData
2562 | NoData
2563 | NoData
2564 | NoData
2565 | NoData
2566 | NoData
2567 | NoData
2568 | NoData
2569 | NoData
2570 | NoData
2571 | NoData
2572 | NoData
2573 | NoData
2574 | NoData
2575 | NoData
2576 | NoData
2577 | NoData
2578 | NoData
2579 | NoData
2580 | NoData
2581 | NoData
2582 | NoData
2583 | NoData
2584 | NoData
2585 | NoData
2586 | NoData
2587 | NoData
2588 | NoData
2589 | NoData
2590 | A citation has been written for having a locked exit and for obstructing/blocking an exit.
2591 | FOR REFERENCE
2592 | HOOKAH INSIDE THE BUILDINGPer the City of Houston NO SMOKING ORDINANCE there is to be NO SMOKING inside the building.(Ord. No. 2006-1054, § 2, adopted Oct. 18, 2006, amended Ch. 21, Art. IX, in its entirety, to read as herein set out)"Smoking" is defined as: Smoking means inhaling, exhaling, burning, or carrying any lighted cigar, cigarette, pipe, or any other lighted tobacco product, plant material, or other combustible substance.(Ord. No. 02-800, § 1, 8-28-02; Ord. No. 06-1054, § 2, 10-18-06; Ord. No. 2014-894, § 5, 10-1-2014) Sec. 21-245. - Enforcement.(a) The department, in addition to any authority having jurisdiction to enforce city ordinances, shall have authority to enforce the provisions of this article.(b) Any citizen who desires to register a complaint under this article may initiate enforcement with the department.(c) The health officer and the fire marshal shall, while an establishment is undergoing otherwise mandated inspections, inspect for compliance with this article.(d) The health officer, after proper identification, shall be permitted to enter any public place and place of employment at any reasonable time, for the purpose of making inspections and examining applicable records of the establishment to determine compliance with this article.
2593 | After several attempts were made by the crowd to push themselves into the gate and enter the facility, the head of security, Shay, stated "I can't control this anymore". At this point the Houston Police Department were requested for crowd control and assistance in maintaining control of the entrances.Per LSB2020.22.13.2: It is the responsibility of the owner, agent or lessee to provide trained crowd manager as required by code.
2594 | All aisles, passageways and means of egress throughout the main floor are obstructed due to overcrowding in the facility.
2595 | This facility is found to be a threat to human life and the public welfare due to improper occupancy, overcrowding and inadequate means of egress.Becuase there is no formal count for the number of patrons within the facility, we must remove all patrons and recount them upon re-entry. It is imperative that a consistent and accurate count be maintained.
2596 | FOR REFERENCE -The approved Certificate of Occupancy has an occupant load of 858 for 4290 SF of "dance floor/standing space" - This space has been remodeled with seating and must be updated with the building department and an accurate occupancy load needs to be calculated. An occupant load of 1199, as indicated on the Certificate of Occupancy issued 05-SEP-2017 now poses a threat to life safety within the facility because of the change of use in this space.
2597 | The occupant load on the Certificate of Occupancy must be revised to include the fixed seating that has been installed per code.All fixed seating is to have one person per 18" of bench space. Patrons are not allowed to crowd bench seating or use the backrest for additional seating. This was observed throughout all fixed seating throughout the main open floor.
2598 | The mezzanine balcony on the second floor has a max occupancy load of 48 on the certificate of occupancy. By over crowding and exceeding this number tonight, there was insufficient means of egress as required by code for the safety of all patrons on the second floor. The occupant load of 48 MUST be maintained at all times. A designated member of the staff must ensure there is an accurate count at all times, as there is only one central exit available.
2599 | NoData
2600 | NoData
2601 | NoData
2602 | NoData
2603 | MAKE SURE ALL PORTABLE FIRE EXTINGUISHERS HAVE A CURRENT INSPECTION TAG ON THEM
2604 | MAKE SURE BOTH THE LEFT AND RIGHT SIDE MAIN EXIT DOORS REMAIN UNLOCKED DURING BUSINESS HOURS
2605 | REPLACE MISSING CEILING TILES IN THE BACK ROOM
2606 | LABEL THE DOOR WITH THE ELECTRICAL PANEL BOX IN IT "ELECTRICAL PANEL INSIDE"
2607 | APPLY FOR THE M3(FUEL DISPENSER) PERMIT AT 1002 WASHINGTON AVE. 832-394-8811
2608 | APPLY FOR AND POST THE ORIGINAL CERTIFICATE OF OCCUPANCY. APPLY AT 1002 WAHSINGTON AVE. 832-394-8811
2609 | NoData
2610 | NoData
2611 | NoData
2612 | NoData
2613 | NoData
2614 | NoData
2615 | NoData
2616 | NoData
2617 | NoData
2618 | NoData
2619 | NoData
2620 | NoData
2621 | NoData
2622 | NoData
2623 | NoData
2624 | NoData
2625 | NoData
2626 | NoData
2627 | NoData
2628 | NoData
2629 | NoData
2630 | NoData
2631 | NoData
2632 | NoData
2633 | NoData
2634 | NoData
2635 | NoData
2636 | NoData
2637 | NoData
2638 | NoData
2639 | NoData
2640 | NoData
2641 | NoData
2642 | NoData
2643 | NoData
2644 | NoData
2645 | NoData
2646 | NoData
2647 | NoData
2648 | NoData
2649 | NoData
2650 | NoData
2651 | NoData
2652 | NoData
2653 | NoData
2654 | NoData
2655 | NoData
2656 | NoData
2657 | NoData
2658 | NoData
2659 | NoData
2660 | NoData
2661 | NoData
2662 | NoData
2663 | NoData
2664 | NoData
2665 | NoData
2666 | NoData
2667 | NoData
2668 | NoData
2669 | Required to have an annual gas testMust become compliant within 30 days.
2670 | NoData
2671 | NoData
2672 | NoData
2673 | NoData
2674 | NoData
2675 | NoData
2676 | NoData
2677 | NoData
2678 | COMPLIANCE DATE: 48HRS (48HR NOTICE)
2679 | SERVICE FIRE ALARM PANEL IMMEDIATELY.
2680 | NoData
2681 | NoData
2682 | NoData
2683 | NoData
2684 | NoData
2685 | NoData
2686 | NoData
2687 | NoData
2688 | NoData
2689 | NoData
2690 | NoData
2691 | NoData
2692 | NoData
2693 | NoData
2694 | NoData
2695 | NoData
2696 | NoData
2697 | NoData
2698 | Correct yellow tagged Fire Sprinkler System dated 1/5/2021
2699 | NoData
2700 | NoData
2701 | Must cover the exposed lights in these locations with appropriate covers.
2702 | Provide 3 new 2-A, 10-B:C portable fire extinguishers and 1 new 2-A, 20-B:C portable fire extinguisher. Make sure the fire extinguishers are mounted according to specs and not blocked in any way. Make sure the fire extinguishers are mounted in a well traveled area. Must remove all other fire extinguishers that are not brand new or have a current inspection tag.
2703 | Provide 3 new 2-A, 10-B:C portable fire extinguishers and 1 new 2-A, 20-B:C portable fire extinguisher. Make sure the fire extinguishers are mounted according to specs and not blocked in any way. Make sure the fire extinguishers are mounted in a well traveled area. Must remove all other fire extinguishers that are not brand new or have a current inspection tag.
2704 | It is the owner/occupants responsibility to correct all fire code violations listed in this report.
2705 | Shall use a metal container for discarded oily rags with a metal lid. Place all oily rags throughout business into the metal container with the lid shut.
2706 | Shall remove all combustible materials such as paper, plastics, wood, rubber, Styrofoam, from around the business. These materials pose a fire hazard and remove all trash and rubbish inside and outside the business.
2707 | Must secure all loose compressed gas containers and make sure the lids are on the containers.
2708 | All multi plug adapters shall have current protection.
2709 | All power strips shall be plugged into a permanent receptacle. You cannot plug one power strip into another.
2710 | Extension cords shall not be used as permanent wiring. Extension cords can only be used to power one temporary small radio, fan, or power tool.
2711 | Replace the ceiling tiles.
2712 | Provide 3 new 2-A, 10-B:C portable fire extinguishers and 1 new 2-A, 20-B:C portable fire extinguisher. Make sure the fire extinguishers are mounted according to specs and not blocked in any way. Make sure the fire extinguishers are mounted in a well traveled area. Must remove all other fire extinguishers that are not brand new or have a current inspection tag.
2713 | Provide 3 new 2-A, 10-B:C portable fire extinguishers and 1 new 2-A, 20-B:C portable fire extinguisher. Make sure the fire extinguishers are mounted according to specs and not blocked in any way. Make sure the fire extinguishers are mounted in a well traveled area. Must remove all other fire extinguishers that are not brand new or have a current inspection tag.
2714 | Shall purchase a hot works permit if any welding, cutting, or heating with a torch is taking place.
2715 | Must acquire operational permits from the City of Houston Permitting Center located at 1002 Washington Avenue, 2nd floor.
2716 | Must obtain a F7/Flammable-Combustible liquid permit for the 700 gallon container or remove the container and use a container less than 60 gallons.
2717 | NoData
2718 | NoData
2719 | NoData
2720 | Repair ASAP.
2721 | Amount Due: $385.38
2722 | NoData
2723 | NoData
2724 | NoData
2725 | K1 permit is expired. Expired on 12/10/2020. Amount owed for permit 177.87 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
2726 | Fire Depository Box not complete. Please review LSB 6.
2727 | Binder missing.
2728 | Legend card missing
2729 | Elevator keys needed.
2730 | Fire phones not working properly.
2731 | NoData
2732 | NoData
2733 | fire extinguishers expired last inspected Feb 2019
2734 | NoData
2735 | NoData
2736 | NoData
2737 | Keybox Permit (K1) is expired.
2738 | NoData
2739 | Provide Current Annual Inspection for all Fire Protection Equipment on Property.
2740 | Provide Current Annual Inspection for all Fire Protection Equipment on Property.
2741 | Provide Current Annual Inspection for all Fire Protection Equipment on Property.
2742 | Provide Current Annual Inspection for all Fire Protection Equipment on Property.
2743 | NoData
2744 | NoData
2745 | NoData
2746 | Fire alarm, sprinkler systems and pump need to be tested as soon as possible by certified companies.
2747 | Fire alarm system needs to be tested on an annual basis.
2748 | Fire pumps and sprinkler systems need to be tested on an annual basis.
2749 | The proper storage height must be maintain throughout the facility. As defined by code:HIGH-PILED COMBUSTIBLE STORAGE. Storage of combustible materials in closely packed piles or combustible materials on pallets, in racks or on shelves where the top of storage is greater than 12 feet (3658 mm) in height. When required by the fire code official, high-piled combustible storage also includes certain high-hazard commodities. such as rubber tires. Group A plastics. flammable liquids, idle pallets and similar commodities, where the top of storage is greater than 6 feet (1829 mm) in height.HiGH-PILED STORAGE AREA. An area within a building which is designated. intended, proposed or actually used for high-piled combustible storage.An area of 2,500 square feet is allowed to be designated high-piled because the facility is fully sprinklered. Have areas for storage at 12 feet marked so that the allowable heighth is not exceeded.
2750 | For Reference
2751 | Extinguishers inspected in October of 2020.
2752 | Your business location is not permitted to perform spray painting without a spray booth and a spraying/dipping permit. Cease all spray painting at this time.
2753 | Need to have a metal trash can with a metal lid for oily rags.
2754 | Need to remove the trash and clutter around the business, inside and out. Rubber, plastics, wood, garbage, and fabrics.
2755 | Bring all fire exstiguishers up to current standard compliance.
2756 | Comply with IFC 2012 506.3 Install an Fire Depository Box
2757 | Provide documentation of a gas test within the last 5 years or have a gas test done.
2758 | NoData
2759 | NoData
2760 | NoData
2761 | NoData
2762 | NoData
2763 | Repair ASAP.
2764 | NoData
2765 | NoData
2766 | See above- the current "K" extinguisher is in compliance (12-2020) maintain the extinguisher
2767 | See above- the current fire extinguishers are in compliance (maintain them) 12-2020
2768 | See above- all extinguishers need to be "marked" with signage
2769 | V.K.PBP Wings LLC.Manager on Duty- Heather
2770 | See above- maintain the emergency exit lighting (test it and repair if necessary)
2771 | See above- the current system is in compliance (12-2020) maintain the system
2772 | See above- Provide the physical address #'s on the building.
2773 | See above- per our conversation relocate the extinguisher in the front of the facility to a more visible location.
2774 | See above- per our conversation, obtain the F7 permit for (storage of flammable/combustible liquids)
2775 | See above- per our conversation, provide documentation of the certificate of occupancy.
2776 | Complete Natural Gas Test Prior to the Date of Re-Inspection.
2777 | NoData
2778 | A Fire Department stand-by may be required if red-tagged system is not serviced in a timely manner.
2779 | Fire alarm system is red tagged and must be serviced within 72 hours
2780 | Failure to service red tagged systems will be subject to citations and re-inspection fees.
2781 | NoData
2782 | LAST INTERCOM INSPECTION REPORT 12-5-2017BRING UP TO CODE
2783 | FIRE ALARM PANEL RED TAGGED 72 HRS. TO BRING UP TO CODE
2784 | LAST EMERGENCY LIGHTING TEST IN FIRE MARSHAL BINDER WAS 10-23-2019
2785 | LAST ANSUL INSPECTION MAY 2020PAST DUE, BRING UP TO CODE
2786 | INFORMATION
2787 | INFORMATION
2788 | AS PER CODE
2789 | LAST ELEVATOR PERMIT EXPIRED 2ND QUARTER 2020
2790 | LAST INTERCOM INSPECTION REPORT 12-5-2017BRING UP TO CODE
2791 | FIRE ALARM PANEL RED TAGGED 72 HRS. TO BRING UP TO CODE
2792 | LAST EMERGENCY LIGHTING TEST IN FIRE MARSHAL BINDER WAS 10-23-2019
2793 | LAST ANSUL INSPECTION MAY 2020PAST DUE, BRING UP TO CODE
2794 | INFORMATION
2795 | INFORMATION
2796 | AS PER CODE
2797 | LAST ELEVATOR PERMIT EXPIRED 2ND QUARTER 2020
2798 | NoData
2799 | All automatic wet-pipe sprinkler systems shall be inspected and tested annually in accordance with NFPA 25 and state requirements, and service tagged by a licensed automatic fire sprinkler service company.
2800 | Fire extinguishers shall be inspected and service tagged annually by a licensed fire protection equipment service company.
2801 | Inspect all Fire Doors and ensure they are operating as intended.
2802 | Label all unit breakers as to which unit it controls.
2803 | FA: Sept. 17 FS: March 16 FEX: June 17 GAS: None
2804 | Make all corrections to deficiencies of the Fire Alarm, Fire Sprinklers immediately.
2805 | Provide a list of all Fire Alarm and Fire Sprinkler deficiencies.
2806 | Replace missing fire extinguishers at the BBQ areas.
2807 | ANSUL SYSTEM FOR THE COMMERICIAL KITCHEN HOOD SYSTEM HAS A RED TAG ISSUED ON 11/5/18. MUST BE CORRECTED AS SOON AS POSSIBLE. INFORMED OF THIS RED TAG THROUGH A COMPLAINT. FIRE MARSHAL WAS NOT NOTIFIED OF THIS RED TAG
2808 | ALSO REPORTED IN THE COMPLAINT WAS A YELLOW TAGGED FIRE ALARM SYSTEM. DEFICIENCIES REGARDING THE YELLOW TAG MUST BE CORRECTED WITHIN 30 DAYS.
2809 | Replace missing outlet face plate.
2810 | Renew fire alarm permit.
2811 | Fire hydrant being blocked by steel cable from telephone pole.
2812 | NoData
2813 | Building B has a Fire Sprinkler Valve that has not been had the annual inspection. Perform the inspection and make any corrections required.
2814 | All fire extinguishers must be serviced and have a current service tag placed on them.
2815 | An emergency lighting test must be performed on the fire alarm system.
2816 | The boiler permit and the fire alarm permit must be renewed.
2817 | NoData
2818 | NoData
2819 | Have all fire extinguishers inspected annually.
2820 | Fire alarm panel must be inspected annually.
2821 | Sprinkler due for 5yr test.
2822 | Replace missing spacers in electrical panel.
2823 | Exit light in shop must illuminate.
2824 | NoData
2825 | Renew fire alarm permit.
2826 | Access Gate Permit (A4) is expired.
2827 | NoData
2828 | NoData
2829 | Restaurant due for 5 year gas test.
2830 | Gas test permit required prior to gas test.
2831 | NoData
2832 | NoData
2833 | NoData
2834 | NoData
2835 | NoData
2836 | NoData
2837 | NoData
2838 | ANSUL SYSTEM FOR THE COMMERICIAL KITCHEN HOOD SYSTEM HAS A RED TAG
2839 | NoData
2840 | NoData
2841 | NoData
2842 | NoData
2843 | NoData
2844 | NoData
2845 | NoData
2846 | NoData
2847 | NoData
2848 | PLEASE REPAIR KEYBOX AT FRONT DOOR, AND LUBE HINGES AND FALCON LOCKS AT OTHER KEYBOX LOCATIONS
2849 | ONLY PANIC HARDWARE OR SIMILIAR SINGLE OPERATION TO OPEN/UNLOCK LOCKING DEVICES ALLOWED ON THESE DOORS. REMOVE ALL OTHER LOCKING DEVICES.
2850 | NoData
2851 | NoData
2852 | NoData
2853 | Provide New Installation tag and Blue ITM Tag on new Sprinkler System by New Gym from original Sprinkler company.
2854 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
2855 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
2856 | Provide documentation/report for annual 'Load Test' and any necessary repairs.
2857 | Provide documentation/report for fire damper testing and any necessary repairs.
2858 | Repaint Fire Lane
2859 | Provide Boiler permits, 250355, 192429, 192430.
2860 | Provide elevator permits(2).
2861 | NoData
2862 | NoData
2863 | NoData
2864 | NoData
2865 | NoData
2866 | NoData
2867 | Teddy
2868 | CORRECT RED TAG SYSTEM WITHIN 72 HOURS OF THIS NOTICE.
2869 | ANSUL FIRE SUPPERSION SYSTEM IS RED TAG. CORRECT RED TAG ANSUL SYSTEM WITHIN 72 HOURS OF THIS NOTICE.
2870 | ANSUL FIRE SUPPRESSION SYSTEM IS RED TAG. CORRECT RED TAG WITHIN 72 HOURS OF THIS NOTICE.
2871 | ANSUL FIRE SUPPRESSION SYSTEM SHALL BE MAINTAINED IN AN OPERATIVE CONDITION AT ALL TIMES AND SHALL BE REPLACED OR REPAIRED WHERE DEFECTIVE.
2872 | NoData
2873 | NoData
2874 | PROTECTED GAS METERS
2875 | REPAIR ALL WALL PENETRATION WITH APPROVED FIRE RATED CAULKING
2876 | Required every 5 years and must be completed with an approved permit from the Building Department.
2877 | JENNIFER TELEPSEN 713 899 9422 Provide copy of lease agreement with smoke detector, fire extinguisher and open Flame cooking policy or addendum.
2878 | Provide letter that states "All tenants have acknowledged and signed the outdoor cooking policy within the lease agreement or the cooking addendum."
2879 | SERVICE OUT OF DATE FIRE EXTINGUISHER REPLACE FIRE EXTINGUISHER IN SHOP AND OFFICE WITH MINIMUM RATING OF 2A:10BC
2880 | LABEL MAINTENANCE SHOP
2881 | REQUIRED ON MAIN GATE ENTRANCE
2882 | Provide letter that states "All units have been supplied with smoke alarms in sleeping areas" January 1, 2017 as battery operated single station alarm is replaced, that smoke alarm shall be replaced with tamper-resistant battery-operated single station smoke alarm. MOUNTED SMOKE ALARM NO MORE THEN 12" INCH FROM CEILING OR PER MANUFACTURING INSTRUCTION
2883 | FIRE ALARM PERMIT CURRENT KEY BOX PERMIT CURRENT
2884 | REMOVE UNAPPROVED GAS CONTAINER
2885 | AFS tested fire alarm system on 1/07/21 and placed a red tag violation on System. Please have all issues corrected within 72 hours.
2886 | NoData
2887 | NoData
2888 | NoData
2889 | NoData
2890 | NoData
2891 | NoData
2892 | NoData
2893 | NoData
2894 | NoData
2895 | GET CORRECT SIZE FIRE EXSTINGUISHER AND GET INSPECTED ANNUALLY.
2896 | WINDOWS IN EACH BED ROOM SHOULD BE OPERATIONAL FOR A SECONDARY EGRESS.
2897 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
2898 | REMOVE ALL DEAD BOLTS FROM EGRESS EXIT DOORS.
2899 | NoData
2900 | NoData
2901 | NoData
2902 | NoData
2903 | Renew p2 (assembly) permit at Houston Permitting Office, 1002 Washington.
2904 | Renew your Public Assembly Permit within 10 Business Days
2905 | NoData
2906 | NoData
2907 | No violations found upon inspection. Classic Protection Systems is scheduled to perform inspection on the entire facility on January 26, 2021.
2908 | NoData
2909 | NoData
2910 | NoData
2911 | NoData
2912 | NoData
2913 | NoData
2914 | NoData
2915 | NoData
2916 | NoData
2917 | NoData
2918 | NoData
2919 | NoData
2920 | NoData
2921 | NO VIOLATIONS FOUND
2922 | NoData
2923 | NoData
2924 | NoData
2925 | NoData
2926 | NoData
2927 | NoData
2928 | NoData
2929 | NoData
2930 | NoData
2931 | NoData
2932 | NoData
2933 | NoData
2934 | NoData
2935 | Please have American Fire System repair/correct red tag issues within 72 hours.
2936 | NoData
2937 | NoData
2938 | NoData
2939 | NoData
2940 | Inspect and Service tag commercial kitchen hood system. Correct all red tag impairments immediately.
2941 | NoData
2942 | NoData
2943 | NoData
2944 | NoData
2945 | Repair ASAP.
2946 | Repair ASAP.
2947 | NoData
2948 | NoData
2949 | NoData
2950 | NoData
2951 | ONLY USING ONE UPSTAIRS CLASSROOM IN BLD 4 AND THE GYM .
2952 | NEED SERVICE TO FIX THE YELLOW TAG. 2-12-20 LAST DATE
2953 | ADD 2 MORE FIRE EXSTINGUISHERS INSIDE OF THE GYM
2954 | NoData
2955 | NoData
2956 | NoData
2957 | NoData
2958 | Extinguishers must be tested and tagged by licensed company
2959 | Have exit lights tested and functional
2960 | Extinguishers must be tested and tagged by licensed company
2961 | Discontinue use of extension cord as a permanent source of electricity
2962 | Close open wires in kitchen
2963 | NoData
2964 | The High Piled and Key Box permit are expired. $770.75 is due at this time. Please remit payment with the instructions listed above.
2965 | NoData
2966 | NoData
2967 | Correct Yellow Tagged Fire Alarm
2968 | Inspect all fire doors.
2969 | NoData
2970 | NoData
2971 | NoData
2972 | NoData
2973 | NoData
2974 | NoData
2975 | ALL VIOLATIONS SHALL BE CORRECTED BY OWNER AND/OR PERSONS IN CHARGE
2976 | REMOVE ALL DEBRIS IN FRONT OF FDC IMMEDIATELY. ALL DEBRIS REMOVED AS OF 3/29/19 TIME: 1535
2977 | NoData
2978 | NoData
2979 | NoData
2980 | NoData
2981 | NoData
2982 | NoData
2983 | An emergency lighting test must be performed on the fire alarm system.
2984 | The kitchen ansul system must be inspected and have current service tag placed on it.
2985 | The boiler and key box permits must be renewed.
2986 | Replace missing Fire Extinguishers in laundry rooms.
2987 | Boiler Permits are out of date.
2988 | Toggle Switch is inoperable.
2989 | The manual gate 911 lock is rusted shut.
2990 | NoData
2991 | NoData
2992 | NoData
2993 | Have all Fire Doors inspected to NFPA 80 standard by a certified company. An approved service company shall perform any required repairs of fire doors or assemblies.
2994 | NoData
2995 | Correct red-tagged fire alarm panel within 72 hours.
2996 | Fire alarm panel is red-tagged due to phone line #2 being down. Correct red tag conditions and return fire alarm system to full operational status within 72 hours.Red tag corrected 11/12/2021 - OK
2997 | NoData
2998 | Fire Alarm Inspections are out of date.
2999 | NoData
3000 | NoData
3001 | NoData
3002 | NoData
3003 | NoData
3004 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
3005 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
3006 | Provide Documentation/Report and tag for the 5th Year FDC Hydrostatic test.
3007 | Provide documentation/report for fire damper testing and any necessary repairs.
3008 | Provide Certificate of Flame Resistance for new blue curtains. (Date)
3009 | Provide Boiler Certificates- 163930, 202120, 239334
3010 | keep all access gates in a working condition including the "fail safe" operations.
3011 | Fire Alarm annual test expires on 06/21
3012 | Sprinkler system annual test expires 06/21
3013 | NoData
3014 | annual test required on all 3 private hydrants 06/21
3015 | maintain both emergency 911 box including toggle switch and fail safe equipment in a working condition.
3016 | NoData
3017 | 109.2 Owner/occupant responsibility. Correction and abatement of violations of this code shall be the responsibility of the owner. If an occupant creates, or allows to be created, hazardous conditions in violation of this code, the occupant shall be held responsible for the abatement of such hazardous conditions.
3018 | 3201.3 Construction documents. At the time of building permit application for new structures designed to accommodate high-piled storage or for requesting a change of occupancy/use, and at the time of application for a storage permit, plans and specifications shall be submitted for review and approval. In addition to the information required by the International Building Code, the storage permit submittal shall include the information specified in this section. Following approval of the plans, a copy of the approved plans shall be maintained on the premises in an approved location.Compliance: 30 calendar days.
3019 | 506.1 Where required. Where access to or within a structure or an area is restricted because of secured openings or where immediate access is necessary for life-saving or fire-fighting purposes, the fire code official is authorized to require a key box or a fire depository box to be installed in an approved location. The key box shall be of an approved type listed in accordance with UL 1037, and shall contain keys to gain necessary access as required by the fire code official. Key boxes shall be provided in accordance with Houston Fire Department LSB Standard No. 05, “Key Boxes.”
3020 | 901.6 Inspection, testing and maintenance. Fire detection, alarm, and extinguishing systems, mechanical smoke exhaust systems, and smoke and heat vents shall be maintained in an operative condition at all times, and shall be replaced or repaired where defective. Nonrequired fire protection systems and equipment shall be inspected, tested and maintained or removed.Compliance: 30 calendar days.
3021 | 1006.3 Emergency power for illumination. The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1. Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2. Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3. Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4. Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. Compliance: 30 calendar days.
3022 | NoData
3023 | Amount Due: $496.18
3024 | NoData
3025 | NoData
3026 | PROVIDE SIGN ON THE DOOR OF THE PRESSURE WASHING CAGE IN THE GARAGE TO INDICATE THE PRESENCE OF DIESEL
3027 | ADD FOBS FOR ENTRY TO ALL 5 SETS OF KEYS IN THE FDB WRITE CODE FOR ENTRY TO PUMP ROOM ON KEY TAG TO PUMP ROOM (ON ALL 5 SETS) READ AND REVIEW LSB STANDARD 6; FULL COMPLIANCE OF PROVIDING A PROPERLY SUPPLIED FIRE DEPOSITORY BOX IS REQUIRED IMMEDIATELY
3028 | THE ELECTRICAL ROOM MUST BE IDENTIFIED AND LABELED AS SUCH - IDENTIFY ACCESS TO THE ELECTRICAL ROOM THROUGH SUITE 350
3029 | THE EXIT DOOR ON THE 14TH FLOOR STAIR B DOES NOT LATCH CLOSED
3030 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THE FOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATE INSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THE SYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THE INSPECTION REPORT. PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFE SAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WAS COMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOW TAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). " Certificate of Occupancy: Core of Building C of O only - REQUIRED " Active Fire Permits: Up to date and Paid - REQUIRED " Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation - RECIEVED " Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards - RECIEVED " Fire Alarm Permit - Annual - REQUIRED " Sprinkler Percentage Letter and Form (included in report) - RECIEVED " Electronic Locks -Semi Annual - RECIEVED " Sprinkler System - Annual - REQUIRED " Fire Alarm System Test - Annual - REQUIRED " Fire Extinguishers - Annual - REQUIRED " Fire Hoses - Annual - REQUIRED " Fire Pumps Flow Test - Annual - RECIEVED " Emergency Power & Lighting - Annual - REQUIRED " Generator Test (ATS) - Annual - REQUIRED " Fire Alarm Audibility Test - 3 Year - REQUIRED " Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - RECIEVED " Fire Alarm Sensitivity - 2 Year - REQUIRED " FDC Test (Bldg. & Garage) - 5 Year - REQUIRED " PRV / PRD Test - 5 Year - REQUIRED " Stair pressurization Test - 5 Year - REQUIRED " Standpipe System - 5 Year - REQUIRED " Water Supply Tank Inspection - 5 Year - REQUIRED " Boiler Permit - RECIEVED " Elevator Permit - Annual - REQUIRED " Dry Partial or Full Trip Test - REQUIRED " Gas Test - 5 Year - RECIEVED " FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED IF THE HIGH-RISE DOES NOT HAVE ANY OF THESE SYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED) DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 60 CALENDAR DAYS
3031 | RECEIVED; NO FURTHER ACTION NECESSARY
3032 | PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS; PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE
3033 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
3034 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
3035 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
3036 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
3037 | NoData
3038 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS
3039 | PROVIDE 2 ELEVATOR INDEPENDANT SERVICE KEYS (LABELED WITH BLACK TAGS) - THESE KEYS ARE TO BE PLACED OUTSIDE OF THE FIRE DEPOSITORY BOX
3040 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
3041 | CABINETS CONTAINING FIRE FIGHTING EQUIPMENT MUST INDICATE THE EQUIPMENT CONTAINED THEREIN - "FIRE HOSE" AND/OR "FIRE EXTINGUISHER" - CORRECTLY IDENTIFY CONTENTS OF CABINET ON THE 3RD FLOOR
3042 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
3043 | ALL ELECTRICAL ROOMS, HVAC ROOMS, MECHANICAL ROOMS, IT ROOMS, ELEVATOR ROOMS, FIRE SPRINKLER RISER ROOMS, FIRE ALARM ROOMS AND TRANSFORMER ROOMS MUST BE LABELED AS SUCH FOR READY IDENTIFICATION - ID THE "PIT" AND ELEVATOR ROOM ON THE 10TH FLOOR, ID THE MECHANICAL ROOM ON THE 3RD FLOOR, ID THE MECHANICAL ROOM ALSO AS "DRY PIPE" ON THE 3RD FLOOR AND ACCESS TO THE GARAGE ELEVATORS THROUGH SUITE 620
3044 | PROVIDE DOCUMENTATION OR LETTER TO ENSURE ALL FIREPHONES AND JACKS (IN THE BUILDING ON ALL FLOORS) HAVE BEEN TESTED BY AN APPROVED, CERTIFIED FIRE PROTECTION COMPANY AND FUNCTIONING PROPERLY FIREFIGHTER PHONES AND ALL JACKS IN THE BUILDING MUST BE TESTED ANNUALLY
3045 | PERTAINING TO PLACEMENT AND DISTANCE OF FIRE EXTINGUISHERS NEEDED THROUGHOUT THE PARKING GARAGE ENSURE THAT ENOUGH FIRE EXTINGUISHERS ARE SUPPLIED, OBVIOUS AND ACCESSIBLE IN THE PARKING GARAGE (AN S-2) NO FIRE EXTINGUISHERS WERE FOUND IN THE PARKING GARAGE - SUPPLY FIRE EXTINGUISHERS ON ALL LEVELS IN DISTANCES PRESCRIBED BY THE FIRE CODE
3046 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTION FEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90 DAYS
3047 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
3048 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
3049 | DOOR CLOSER FOUND ON THE 14TH FLOOR (STAIR B) IS NOT WORKING PROPERLY - ENSURE DOORS ARE LATCHING SHUT ON ALL EXIT STAIRWELL DOORS
3050 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
3051 | THE STANDARD AND PROCEDURES ARE BEING REVISED; PLEASE CONTINUE TO CONDUCT FIRE DRILLS AND KEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WE REVIEW AND DISCUSS IN THE NEAR FUTURE
3052 | THE MOBILITY IMPAIRED LIST MUST BE UPDATED EVERY 6 MONTHS
3053 | FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE
3054 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS AND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITE FOR FIRE MARSHAL INSPECTION
3055 | OBTAIN ALL REQUIRED PERMITS FROM THE HOUSTON PERMITTING CENTER - F7 (FLAMMABLE LIQUIDS PERMIT) AND K1 (KEY BOX PERMIT) ARE DUE THE ALARM PERMIT COULD NOT BE LOCATED IN OUR SYSTEM VIA MY SEARCH - PLEASE VISIT THE HOUSTON PERMITTING CENTER AND OBTAIN THE FIRE ALARM PERMIT
3056 | THE EXIT DOOR ON THE 14TH FLOOR STAIR B IS STICKING - ENSURE ALL EXIT DOORS ARE CAPABLE OF OPENING WITH EASE
3057 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN THE ELEVATOR ROOM ON THE GROUND FLOOR IN JOE'S OFFICE & THE ELCTRICAL ROOM, ON THE 6TH FLOOR, MECHANICAL ROOMS ON THE 12TH & 13TH FLOORS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR
3058 | A REINSPECTION FEE WILL ONLY ACCRUE IF TOTAL COMPLIANCE IS NOT MET ON THE DATE INDICATED (HIGHLIGHTED DATE IN THE TOP RIGHT HAND CORNER UNDERNEATH THE REPORT DATE)
3059 | ENSURE THE EMERGENCY "RE-ENTRY" BUTTON ON THE FIRE ALARM PANEL IS HIGHLIGHTED OR CONSPICUOUSLY LABELED
3060 | WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY
3061 | NoData
3062 | PERTAINING TO THE CHARACTERISTICS OF SIGN TO INDICATE PRESENCE OF DIESEL
3063 | THE BACK EXIT DOOR AND ABOVE ACCESS GATE CONTROL TO SUITE 700 SHOULD BE LABELED "SUITE 700 ACCESS GATE CONTROL"
3064 | PROVIDE A COVER PLATE FOR EXPOSED ELECTRICAL OUTLET BEHIND THE UPS BOX ON THE GROUND FLOOR
3065 | NoData
3066 | Repair ASAP.
3067 | NoData
3068 | NoData
3069 | NoData
3070 | NoData
3071 | Expired 12/6/2020; Unpaid Fees $385.38
3072 | NoData
3073 | NoData
3074 | NoData
3075 | NoData
3076 | K1 - Keybox permit is expired and must be renewed. Please remit payment in person, by mail or online as described above.
3077 | NoData
3078 | NoData
3079 | The Falcon Lock on the 911 key box has rusted in the closed position. The lock must be removed with bolt cutters and replaced - OR - a new 911 key box with the hinged lid protecting the key lock may be used. Should you decide to use the key box with the hinged lid (which will not require a falcon lock being replaced periodically), the existing key box must be removed.
3080 | NoData
3081 | NoData
3082 | NoData
3083 | NoData
3084 | NoData
3085 | NoData
3086 | NoData
3087 | NoData
3088 | NoData
3089 | NoData
3090 | Failure to renew the Assembly (p2) permit will render a Re-inspection Fee of $386.44. Houston Permitting Center is located at 1002 Washington.
3091 | Michael BrownNO VIOLATIONS FOUND AT THIS TIME.
3092 | Provide documentation/report showing repair of emergency lights.
3093 | Provide Fire Alarm Permit
3094 | Make all violation corrections prior to the reinspection date noted on the front page of the report.
3095 | Repair the life safety emergency egress light near the lunch room exit.
3096 | Exit sign illumination intensity level must be at least 5 foot-candles (54 lux).
3097 | Emergency Exit signs must stay illuminated at all times and during a loss of power. Repair all exit signs that are not lit.
3098 | Renew the fire alarm permitHFD18032748
3099 | NoData
3100 | NoData
3101 | NoData
3102 | NoData
3103 | NoData
3104 | NoData
3105 | NoData
3106 | NoData
3107 | NoData
3108 | NoData
3109 | NoData
3110 | NoData
3111 | Amount Due: $770.76
3112 | INFORMATION
3113 | INFORMATION
3114 | INFORMATION
3115 | INFORMATION
3116 | NoData
3117 | Information only.
3118 | Information only.
3119 | Gas test required every 5 years. Call your plumber and have gas test performed. Plumber must obtain permits from city. FYI: Last test was on 8/30/2013 project #13087409.
3120 | Information only.
3121 | Label boiler room doors.
3122 | NoData
3123 | NoData
3124 | NoData
3125 | NoData
3126 | NoData
3127 | Remove rolling carts that block extinguishers in cafeteria.
3128 | Correct all violations within 30 calendar days.Provide action plan for violations that cannot be corrected by reinspection date listed on Page 1.
3129 | Working action plan for dampers. Provide documentation when impaired dampers are replaced.
3130 | 7/2020, but upstairs culinary hood still dirty. Have vent hood cleaned.
3131 | Document fire code training.Extinguisher training OK
3132 | Remove all multi-outlet extension cords that do not have built-in surge protection, including those supplying power to Promethean boards.Working action plan. Funding will be available July 2021.
3133 | Remove extension cord that passes through culinary ceiling.
3134 | Add cover plates to junction boxes in ceiling of upstairs culinary class.
3135 | Remove door stops from fire rated doors in kitchen.
3136 | Map update in progress. Complete and post updated maps.
3137 | One expired boiler permit. Update and place in binder.
3138 | Repair ASAP.
3139 | NoData
3140 | NoData
3141 | P2-Public Assembly permit past dueF7-Flammable comb. storage permit past dueH3-Hot Works permit past due
3142 | INFORMATION
3143 | INFORMATION
3144 | Need sign on door FIRE ALARM PANEL
3145 | INFORMATION
3146 | Library exits down stairs and up stairs, bring up to code
3147 | NoData
3148 | NoData
3149 | NoData
3150 | INFORMATION
3151 | INFORMATION
3152 | Need sign on door FIRE ALARM PANEL
3153 | INFORMATION
3154 | Library exits down stairs and up stairs, bring up to code
3155 | See above for the Fire extinguishers (all of the current extinguishers are out of date) 2-2016
3156 | Carlos Mejea
3157 | See above for the storage of tires.
3158 | Apply for the (F7) permit with the permitting office.
3159 | NoData
3160 | 6/2019 - Have all extinguishers inspected.9/2020 - OK
3161 | Correct all violations within 30 calendar days.Provide action plan for violations that cannot be corrected by reinspection date listed on Page 1.
3162 | Document fire code training.9/2/2020 - OKExtinguisher training documentation OK.
3163 | Remove all multi-outlet extension cords that do not have built-in surge protection, including those supplying power to Promethean boards.Working action plan. Funding available July 2021.
3164 | NoData
3165 | NoData
3166 | NoData
3167 | NO VIOLATIONS FOUND AT THIS TIME.
3168 | PER NFPA 55 7.1.8.4.2At cylinder-filling plants, authorized cylinder requalifier's facilities, and distributors' warehouses,the nesting of cylinders shall be permitted as a means to secure cylinders.There is no need for straps, chains or cables whiles cylinders are being stored in an appropriatemanner per the code.IN COMPLIANCE AT THIS TIME
3169 | NoData
3170 | NoData
3171 | Correct all violations within 30 calendar days.Provide action plan for violations that cannot be corrected by reinspection date listed on Page 1.
3172 | Document fire code training.Extinguisher training OK
3173 | Update maps. Do not use red and green for route colors.
3174 | Correct all violations within 30 calendar days.Provide action plan for violations that cannot be corrected by reinspection date listed on Page 1.
3175 | Remove all multi-outlet extension cords that do not have built-in surge protection, including those supplying power to Promethean boards.Working action plan. Funding available 7/2021
3176 | Expired 7/17/2020. Update expired boiler permit.
3177 | Correct all violations within 30 calendar days.Provide action plan for violations that cannot be corrected by reinspection date listed on Page 1.
3178 | Document extinguisher and fire code training.
3179 | Remove all multi-outlet extension cords that do not have built-in surge protection, including those supplying power to Promethean boards.Working action plan. Funds available 7/2021.
3180 | One boiler expired 3/6/2020. Update boiler permit.
3181 | Amount Due: $533.60
3182 | NoData
3183 | K1 permit is expired at this time.
3184 | COMPLIANCE DATE: 15 CALENDAR DAYS
3185 | NoData
3186 | NoData
3187 | NoData
3188 | Correct all violations within 30 calendar days.Provide action plan for violations that cannot be corrected by reinspection date listed on Page 1.
3189 | Document extinguisher and fire code training.9/8/2020- OK
3190 | Remove all multi-outlet extension cords that do not have built-in surge protection, including those supplying power to Promethean boards.Action plan. Funds available 7/2021
3191 | One boiler expired 3/6/2020. Have boiler inspected and update permit.
3192 | NoData
3193 | COMPLIANCE DATE: 15 CALENDAR DAYS
3194 | K1 and A4 fire prevention permit is expired at this time.
3195 | Fire extinguishers must be inspected annually.
3196 | Mount all fire extinguishers.
3197 | Emergency exit lights must be tested.
3198 | Remove combustibles around electrical panel.
3199 | Exit lights must illuminate.
3200 | 3/2019 - Have all extinguishers inspected9/2020 - OK
3201 | Correct all violations within 30 calendar days.Provide action plan for violations that cannot be corrected by reinspection date listed on Page 1.
3202 | Remove all multi-outlet extension cords that do not have built-in surge protection, including those supplying power to Promethean boards.Action plan. Funds available 7/2021
3203 | NoData
3204 | NoData
3205 | 7/2019 - Have all extinguishers inspected.9/2020 - OK
3206 | Correct all violations within 30 calendar days.Provide action plan for violations that cannot be corrected by reinspection date listed on Page 1.
3207 | Remove all multi-outlet extension cords that do not have built-in surge protection, including those supplying power to Promethean boards.Action plan. Funds available 7/2021
3208 | Boiler expired. Update permit and place in binder.Boiler removed and replaced with water heater.
3209 | NoData
3210 | NoData
3211 | NoData
3212 | NEED SERVICE. FIX YELLOW TAG. 6-2-20 LAST DATE
3213 | NEED SERVICE. 8-19 LAST DATE
3214 | NoData
3215 | NoData
3216 | NO VIOLATIONS FOUND AT THIS TIME REMINDER TO POST FIRE DRILL ACTIVITY LOG AND HAVE AVAILABLE AT ALL TIMES
3217 | PLACE SIGNAGE ON EACH ACCESS GATE LEADING INTO PROPERTY
3218 | NoData
3219 | Remove combustible material stored in 16th floor mechanical room per code.
3220 | Add electronic lock override switch to FCC per code.
3221 | Trim bushes that are obstructing the FDC.
3222 | Add cover to junction box on level 5 near stair A per code.
3223 | Return the fire rating to its designed fire resistance rating per code.Go through mechanical, electrical and IT rooms and make additional corrections as needed.
3224 | Ensure all stairwell doors close and latch from the open position per code.
3225 | Remove chevron so exit sign points to the exit per code.
3226 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriateinspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualFire Extinguishers- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
3227 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. • Present Permits that apply to facility Address listed • on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS.
3228 | NoData
3229 | NoData
3230 | NoData
3231 | NoData
3232 | NoData
3233 | NoData
3234 | keep all access gates in a working condition including the "fail safe" operations.
3235 | Fire Alarm annual test expires on 06/21
3236 | Sprinkler system annual test expires 06/21
3237 | NoData
3238 | annual test required on all 3 private hydrants 06/21
3239 | maintain both emergency 911 box including toggle switch and fail safe equipment in a working condition.
3240 | NoData
3241 | Test sprinkler system
3242 | NoData
3243 | NoData
3244 | NoData
3245 | NoData
3246 | Fire Alarm System needs annual, audibility and sensitivity test done.
3247 | Provide documentation for sprinkler system annual and 5 year hydrostatic test. All components of system should have a compliance tag attached.
3248 | Remove items (bicycles) blocking means of egress.
3249 | Remove combustible storage from all equipment rooms.
3250 | Fire Depository Box is required for all midrise buildings.
3251 | Identify fire hydrants with square blue reflectors.
3252 | Upon follow up inspection performed by Inspector Hopkins, a red tag was placed on the sprinkler system dated 1/15/2021 by the fire protection service company. I initiated a 72 hours notice to have the sprinkler system repaired to compliant status. I also notify management to start a in house fire watch until the sprinkler system is returned to compliant status.
3253 | Fire extinguishers are required in the courtyard near the cooking appliances.
3254 | Provide signs for pump room and elevator control room (shutoff).
3255 | 911 Keyboxes are required at all stairwell discharge doors.
3256 | Provide signage for rainwater pit under parking garage.Provide documentation and signage for Permeable Grass required for fire access road.Provide signage identifying the number of hydrants inside of complex.Provide signage for FDC according to LSB # 2.5.4.3
3257 | Provide clearance from electrical panels.
3258 | NoData
3259 | NoData
3260 | P2 permit is expired. Expired on 2/13/2018. Amount owed for permit 1135.41 Please pay for permit within 10 days of this notice. If permit is not paid for within 10 days a reinspection fee will be applied. If more information is needed about permit contact the Fire Prevention Permit Office.
3261 | NoData
3262 | NoData
3263 | NoData
3264 | NoData
3265 | NoData
3266 | NoData
3267 | NoData
3268 | Emergency lights must be tested yearly. Documentation must be added into the FMB of last test date.
3269 | It's the owner/management to maintain all required inspections and permits up to date.
3270 | Fire alarm audibility testing must be done every 3 yrs. and alarm panel tagged showing last date. Copy of results entered into FMB
3271 | All emergency lights need to be tested once a yr and results entered into the FMB.
3272 | Damper testing must be done every 4 yrs. and placed into the FMB
3273 | All fire extinguisher must be tested once a yr. and tagged with current date.
3274 | An access gate key box must be install for apparatus access.
3275 | All fire rated exit doors must open and return to the closed position without any assistance. Proper swing arms need to be installed and if necessary doors adjusted.
3276 | All class rooms need updated evacuation routes per example given.
3277 | Smoke detector testing must be done and results placed into the FMB and Alarm Panel tagged.
3278 | Access Gate permit needed.
3279 | Exterior gates in play ground/court yard must open in the direction of travel and never to be lock or chained. Access to public way must be maintain and made available for the occupancy of the building.
3280 | At no time can exit doors leading to public way be chained and pad locked.
3281 | Exit signs with emergency lights must be installed above all emergency exit doors.
3282 | K-1 permit needed.
3283 | All class room emergency exit doors must have panic hardware UL approved.In addition all exterior gates to the public way and leading to the public way must open in the direction of travel and have panic hardware installed. UL approved.
3284 | All updated permits and certificate of occupancy must be placed inside binder.
3285 | Large tree needs to be removed or maintained so that the exit door opens the required clear width.
3286 | All exterior doors exit pathway of egress, must be kept clear of obstruction and hazards. All debris obstructing the path of travel to the public way must be removed.Example. falling broken fence, wood pickets, grocery cart and any other large obstacles along the path.
3287 | NoData
3288 | NoData
3289 | NoData
3290 | All fire extinguishers must be serviced and have a current service tag placed on them.
3291 | An emergency lighting test must be performed on the fire alarm system.
3292 | The sprinkler system must be inspected and have a current service tag placed on it.
3293 | The ansul system in the kitchen must be inspected and have a current service tag placed on it.
3294 | The assembly and fire alarm permits must be renewed.
3295 | Remove combustible storage.
3296 | Provide updated certificate of flame resistance for black and tan curtains. Pic included in email. The certificate shall indicate the color of the curtains (retesting of the flame resistance). New curtains on site. Pending: need Certificates of Flame Resistance (2)
3297 | Provide service tag showing 10/15/2019 HITEK Yellow Tag on fire alarm panel. FYI, copy of report shows blue tagged only. Pic included in email. The Fire Alarm system is now expired. Correct 10/26/2020 AST Yellow tag on Fire Alarm System (pic emailed)
3298 | Retag fire extinguisher in electrical/ mechanical room.
3299 | Install fail-safe on access gate.
3300 | Install knox-box on gates.
3301 | Replace cover on junction box.
3302 | Cover opening in electrical room with fire resistant caulking.
3303 | Place knox box on access gates.
3304 | NoData
3305 | NoData
3306 | NoData
3307 | NoData
3308 | NoData
3309 | NoData
3310 | -Red/Yellow Tagged Fire Alarm System-Bad phone lines
3311 | NoData
3312 | NoData
3313 | NoData
3314 | Required to have an annual gas testMust become compliant within 30 days.
3315 | Permit Expired 11/21/2020; Unpaid Fees $385.38
3316 | See above, per our conversation you need to maintain the extinguishers on a annual basis ( the current extinguisher has no tag and we need a receipt to prove the date)
3317 | See above-provide the following for welding.
3318 | See above, per our conversation, when spraying parts.
3319 | See above, maintain the safety of exits (free from obstructions)
3320 | See above, per our conversation, apply for the F7( storage of flammable/combustible liquid) and the H3 permit (welding)
3321 | NoData
3322 | NoData
3323 | NoData
3324 | NoData
3325 | NoData
3326 | All generator, electrical rooms, mechanical rooms and boiler rooms must have a fire extinguisher placed inside of it.
3327 | The tags on the sprinkler standpipe must be replaced.
3328 | NoData
3329 | NoData
3330 | Provide signage, "Electrical Room", on or above the door where the Electrical Panels are located.
3331 | Provide (2) additional, size 2A:10BC Fire Extinguishers, with service tags for the Patio areas.
3332 | Have all Fire Extinguishers serviced, and provided with current service tags, annually.
3333 | Provide proper work space clearance around the Electrical Panel.
3334 | NoData
3335 | NoData
3336 | NoData
3337 | NoData
3338 | NoData
3339 | Exit Sign needed above doors.
3340 | NoData
3341 | Need to be tested and results placed into FMB.
3342 | Needs updated service tags.
3343 | Dampers Tested every 4 yrs.
3344 | Remove any obstruction during cooking service. Pull station shall not be block during cooking times.
3345 | Heavy accumulation of clutter must be removed and brought back to the approved load. Excess boxes and material shall be moved to a storage area away from the school.
3346 | General fuel shall not be stored inside storage area including used burned wood that is used for camp fire.
3347 | Remove any combustible material from electrical room.
3348 | All exit doors need to open and close and latch on it's own without any assistants.
3349 | Permits required
3350 | Access Gates Permit required.
3351 | IFC2012.B1027.5, Describes the requirement for installation of panic hardware to the public way. If your area does not meet the requirements then you will have to install panic hardware on those gates.
3352 | Heavy accumulation of clutter must be removed and brought back to the approved load. Excess boxes and material shall be moved to a storage area away from the school.
3353 | Exit gate to public way.
3354 | Exit Gates to the public way need to have panic hardware install and shall never be chained or pad locked.
3355 | Any blinds installed on exit doors need to be removed.
3356 | All pathways leading to emergency exit doors shall never be obstructed by tables or book shelfs.
3357 | NoData
3358 | NoData
3359 | Per Ed Cope Technical Report provided in 2007 and plans submitted for approval, this building MUST have an action plan with compliance to code as referenced in reports. The action plan must be adhered to and the approved project completed. This building is a combustible dust building. (Complinace to submit Action Plan 2019: by 12/31/2019)
3360 | NoData
3361 | (FOR REFERENCE)
3362 | THE APPROVED HIGH PILED PLANS MUST BE KEPT ON SITE AN ACCESSIBLE FOR INSPECTION. THESE PLANS MUST BE APPROVED AND STAMPED BY THE CITY OF HOUSTON. (COMPLIANCE DATE: NOV 7, 2019)
3363 | AN APPLICATION MUST BE FILED WITH THE CITY OF HOUSTON FOR THE CERTIFICATE OF OCCUPANY TO BE ISSUED FOR BUILDING 3-925. THE APPLICATION FOR THIS MUST BE FILED IN 15 CALENDAR DAYS (COMPLIANCE DATE: OCT 24, 2019)
3364 | (FOR REFERENCE)
3365 | HAVE THE ANNUAL LOAD TEST PERFORMED ON THE BACK UP GENERATOR FOR THIS BUILDING (COMPLIANCE DATE: NOV 7, 2019)
3366 | NoData
3367 | NFPA 13 6.2.9.6 REQUIRES THAT A WRENCH AND EXTRA REPLACEMENT SPRINKLER HEADS BE PLACED IN A SECURED BOX. HAVE THIS EQUIPMENT INSTALLED BY THE RISER IN BUILDING 3-960 (COMPLIANCE DATE: NOV 7, 2019)
3368 | NoData
3369 | 911 KEY BOX AND A KEY TO ACCESS THE BUILDING NEED TO BE INSTALLED AT THE FRONT DOOR. ONCE THE KEY BOX IS IN PLACE, CALL TO HAVE THE LOCK OPENED AND THE ACCESS KEY PLACED INSIDE. (COMPLIANCE DATE: NOV, 7 2019)
3370 | NoData
3371 | NoData
3372 | The 5 year hydrostatic flow test is due must be completed if there is not a tag or report indicating it has passed in the last 5 years. Any deficiencies found must be repaired/replaced.
3373 | Because your facility is protected in accordance with NFPA 13 -12.12.1.2 (4), they may be stored indoors as described below "pallets arestored no higher than 6 ft (1.8 m) and each pile of no more than four stacksshall be separated from other pallet piles by at least 8 ft (1.4 m) of clearspace or 25 ft (7.6 m) of commodity". Ensure pallets are arrangedaccordingly.Storage of idle pallets shall comply with NFPA 13NFPA 13 – 2010 Storage of idle wood pallets12.12 Protection of Idle Pallets.12.12.1 Wood Pallets.12.12.1.1Wood pallets shall bepermitted to be stored in the following arrangements:(1) Stored outside(2) Stored in adetached structure(3) Stored indoorswhere arranged and protected in accordance with 12.12.1.212.12.1.2Wood pallets, wherestored indoors, shall be protected in accordance with one of the following:(1) Control modedensity/area sprinkler protection as specified in Table 12.12.1.2(a).(2) CMSA sprinklerprotection in accordance with Table 12.12.1.2(b).(3) ESFR sprinklerprotection in accordance with Table 12.12.1.2(c).(4) Control modedensity/area sprinkler protection in accordance with the OH2 curve of Figure13.2.1 existing with a hose stream demand of at least 250 gpm (946 L/min) for aduration of at least 60 minutes when pallets are stored no higher than 6 ft(1.8 m) and each pile of no more than four stacks shall be separated from otherpallet piles by at least 8 ft (1.4 m) of clear space or 25 ft (7.6 m) ofcommodity. The maximum clearance of 20 ft (6.1 m) specified in 12.1.3.4 shallnot apply to arrangement 12.12.1.2(4).12.12.1.3Idle wood palletsshall not be stored in racks unless they are protected in accordance with theappropriate requirements of Table 12.12.1.2(a) or Table 12.12.1.2(c).(SeeSection C.7.)
3374 | Several rack structures are found to be damaged at the footing where protections were not installed. These racks must be repaired or replaced and maintained to manufacturer standards as specified by approved plans. Should repairs be made, a letter must be signed and stamped by an engineer ensuring all standards have been met.The following locations were noted on inspection: B16-A1, B17-A4, D06-A1, D08-A1, E02-A1, F07-A1, J07-A1, K20-A1, K14-A1, K02-A1, K02-A2Please ensure all damaged footings not listed above are included
3375 | NoData
3376 | NoData
3377 | NoData
3378 | NoData
3379 | NoData
3380 | NoData
3381 | NoData
3382 | The fire alarm control unit was found to have a yellow tag attached. Contact a licensed fire protection to correct the violations and ensure a current service tag reflecting the corrections made is attached.
3383 | NoData
3384 | NoData
3385 | NoData
3386 | NoData
3387 | Cover all electrical wires over the access doors by doors 19, 20 and throughout the warehouse.Compliance by 1-29-2021
3388 | Remove the locks on the exit near the breakroom. You should be able to exit out of this door while the building is occupied.Immediate compliance required.
3389 | Place electrical covers over all open electrical outlets in the breakroom.Compliance by 1-29-2021
3390 | Remove all objects blocking a clear path to the fire extinguisher by doors 18 and 19.Compliance by 1-29-2021
3391 | Move all large dumpsters a minimum of 10 feet away from the building.Compliance by 1-29-2021
3392 | Provide documentation that all emergency lighting has been tested and is working of the time of the test.Compliance by 1-29-2021
3393 | The knox box at the front entrance will not open. Try to spray the locking mechanism with lubricant so that we have access to the box.Compliance by 1-29-2021
3394 | Provide the key to the lock on the gate and a access door key so that it can be placed inside the knox box on the rear gate heading to the side of the building near the 610 Loop. Also, the access gate heading to the side of the building shall be cleared so that access to all sides of the building is possible (dumpster).Compliance by 1-29-2021
3395 | Your fire alarm permit expired in 2018. Renew your fire alarm permit by going to permits.houstontx.gov then HFD contact us.Compliance by 1-29-2021
3396 | All exit signs shall be illuminated.Compliance by 1-29-2021
3397 | Provide documentation that all private fire hydrants on your property have been inspected in accordance to NFPA 25.Compliance by 1-29-2021
3398 | Have Atlas Fire correct all red tag issues on your fire pump and bring system back into service.A self fire watch shall be in place following the guidelines provided until the pump and sprinkler system have been replaced and tagged acceptable by qualified sprinkler company. Fire watch shall start no later than1-28-2021 and is a 24 hour watch.Also submit a detailed action plan of the work being done with estimated time frames to completion.
3399 | All fire extinguishers shall be inspected and tagged in the warehouse and on all forklifts powered by propane.Sprinkler riser by door 14 needs a inspection tag.Compliance by 1-29-2021
3400 | All fire extinguishers shall be mounted on a fixed object and off the floor by C2.Compliance by 1-29-2021
3401 | Provide a new FDC sign on the wall on the side of the building facing the 610 Loop.Compliance by 1-29-2021
3402 | Have qualified sprinkler company address the lack of sprinkler coverage in the Medegen Office.Compliance by 1-29-2021
3403 | NoData
3404 | NoData
3405 | NoData
3406 | ALL EXTINGUISHERS MUST BE TESTED AND TAGGED BY LICENSE COMPANY
3407 | RED TAG MUST BE ADDRESSED AND CORRECTED IN ACCEPTANCE STATUS BY A LICENSE ALARM CO.
3408 | SPRINKLER SYSTEM YELLOW TAGGED. IMPAIRMENTS MUST BE ADDRESSED BY LICENSE SPRINKLER COMPANY
3409 | NEW INSTALL TAG MUST ATTACHED TO PANEL BY THE ALARM COMPANY
3410 | DRYER VENT HOSE DISCONNECTED. MUST REATTACHED AND LINT BUILDUP REMOVED
3411 | NoData
3412 | NoData
3413 | Repaint fire lane.
3414 | Remove surge protector coming through ceiling tile.
3415 | Reminder. Remove all from ceiling.
3416 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
3417 | Both sprinkler systems. Provide Tags.
3418 | 3 Hydrants, Provide Documentation.
3419 | Correct 4/27/2020 & 1/5/2021 Yellow tags on Sprinkler System, provide service tag showing correction. ----- Correct trouble alert on fire alarm system. Correct 1/7/2021 Red Tag on Fire Alarm Panel
3420 | Compliance required within 60 calendar days.
3421 | Remove combustibles from mechanical rooms.
3422 | Training required annually. Keep documentation of training in Fire Marshal Binder
3423 | Place log in fire marshal binder.
3424 | Assembly and fire alarm permits current.
3425 | Maintain required ceiling clearance.
3426 | Do not exceed the maximum allowable wall coverage.
3427 | Mount one additional extinguisher on stage.
3428 | Drill log OK.
3429 | Last egress test 2/18/19. Report states all devices passed, but one exit light is not illuminated under normal building power. Repair exit sign.
3430 | Place report in binder.
3431 | Inspector recommends that records of all employee safety training be in memo/letter form. The memo/letter should include the date, location, type of training received, whether any employees were absent from training, and the name & signature of the person conducting the training.
3432 | Replace all missing/damaged ceiling tiles.
3433 | Have sensitivity test performed, or provide documentation of a passing sensitivity test.
3434 | Last inspection 7/2019 - OK
3435 | Last inspection 1/21/19 - Blue, OK
3436 | Last audibility 1/21/19 At least 30 failures noted with no documentation of correction. Have all failures corrected.
3437 | Curtain certs issued 9/2014 and 2/2007 - OK
3438 | Do not hang/suspend/display anything from ceilings.
3439 | Provide instructions for fire alarm and intercom operation. Instructions must be located at the respective systems.
3440 | Obstructed drills OK.
3441 | Do not decorate doors.
3442 | NoData
3443 | INFORMATION
3444 | INFORMATION
3445 | AS PER CODE
3446 | UPDATE FIRE ALARM PERMIT
3447 | NEED PUBLIC ASSEMBLY P2 PERMIT
3448 | NEED ANNUAL FIRE SPRINKLER TEST
3449 | AS PER CODE
3450 | DOORS NEED TO BE FIRE RATED, SHOW CERTIFICATE TO VERIFY IF THE DOORS ARE FIRE RATED
3451 | AS PER CODE
3452 | NoData
3453 | NoData
3454 | NoData
3455 | NoData
3456 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES. PER THE CITY OF HOUSTON CODE A SAFETY INSPECTION (FIRE MARSHALL APPROVAL) MUST BE PERFORMED ANNUALLY. APPLY FOR THE SAFETY PERMIT BY MONDAY 01-25-2021 OR A CITIATION WILL BE ISSUED AND THE STATE WILL BE NOTIFIED.
3457 | It is the owner/occupants responsibility to correct all violations listed below:-Contact a licensed fire protection company to have the fire alarm system serviced and ensure a blue acceptable annual service tag is attached. Ensure that an audibility test has been performed within the past 3 years, and a sensitivity test has been performed within the past 2-5 years. Repair or replace damaged smoke detector in the custodial closet.-Wet chemical extinguishing systems in commercial kitchens are required to be serviced every 6 months. Contact a licensed fire protection company to service the ANSUL system and ensure a current service tag is attached.-Commercial kitchen hoods in low-volume cooking operations such as places of religious worshipare required to beinspected and serviced as necessary every 12 months. Contact a licensed professionalto have the vent hood inspected. Ensure a service tag is attached following the completion of the service.-Have all exit signs inspected to ensure they are properly illuminated under regular service power and battery back up power.-Ensure all ceiling tiles that were found to be missing are put back into place and are properly seated. (second floor classroom and custodial closet)-Remove the white tape being used tocover the open space in the breaker boxin the electrical closet in the school roomand replace with a breaker box filler plate.Side NotesGas test performed and finaled on 09/02/20Fire drill logs inspected and found to be complete
3458 | NoData
3459 | NoData
3460 | NoData
3461 | NoData
3462 | NoData
3463 | NoData
3464 | NoData
3465 | NoData
3466 | NoData
3467 | NoData
3468 | NoData
3469 | NoData
3470 | Teddy
3471 | CORRECT RED TAG SYSTEM WITHIN 72 HOURS OF THIS NOTICE.
3472 | ANSUL FIRE SUPPERSION SYSTEM IS RED TAG. CORRECT RED TAG ANSUL SYSTEM WITHIN 72 HOURS OF THIS NOTICE.
3473 | ANSUL FIRE SUPPRESSION SYSTEM IS RED TAG. CORRECT RED TAG WITHIN 72 HOURS OF THIS NOTICE.
3474 | ANSUL FIRE SUPPRESSION SYSTEM SHALL BE MAINTAINED IN AN OPERATIVE CONDITION AT ALL TIMES AND SHALL BE REPLACED OR REPAIRED WHERE DEFECTIVE.
3475 | NoData
3476 | NO VIOLATIONS FOUND
3477 | NoData
3478 | NoData
3479 | NoData
3480 | Repaint Fire Lane
3481 | NoData
3482 | Provide documentation for annual emergency lights testing.
3483 | Sprinkler system is expired, 11/9/2017.
3484 | Provide Certificate of Flame Resistance for Green curtains. Note: nothing should be pinned, stapled or glued on stage curtains.New Curtains added to Stage, provide Certificate of Flame Resistance for both colors.
3485 | Correct 11/9/2017 Yellow Tag on Sprinkler System
3486 | Provide Sprinkler Signage on outside door
3487 | NoData
3488 | NoData
3489 | -It is the owner/occupants responsibility to correct all violations found.-Reinspection fees will be issued if the violations are not corrected prior to the follow up date.-Citations will be issued if compliance is not obtained.-All exit doors must be able to be opened from the egress side without the use of a key. Replace the double keyed cylinder locks on each door.-Once power is restored to the building, ensure all exits signs are illuminated under regular power and battery backup power.-Replace the missing extinguisher near the exit dooron thewestern end of the building. Mounting a second extinguisher is the kitchen is acceptable and encouraged. Minimum size - 2:A 10:BC-Ensure all extinguishers have been serviced by a licensed fire protection company and have a service tag attached.-At least one fire extinguisher with a minimum rating of 2:A 10:BC is required to the tagged and mounted in the ambulance service shop while being used as a service area.-Ensure all electrical wires are secured and junction boxes/breaker boxeshave appropriate covers.-Install breaker box filler plates in the small breaker box in the office.-Properly secure all compress gas cylinders-Apply for a "Hot Works" permit or remove the cutting torch from the premises.Disable the chain from the access gate. If the decision is made in the future to use the access gate, ensure the Houston Fire Department Life Safety Bureau Standard #4 is followed.Ensure the sensor for the mag lock on the front door is not covered.It appears Acute Medical Services does not have a Certificate of Occupancy on file. Please contact the Houston Permitting Center Occupancy Division. (832)394-8880
3490 | NoData
3491 | NoData
3492 | NoData
3493 | NoData
3494 | NoData
3495 | NoData
3496 | NoData
3497 | NoData
3498 | NoData
3499 | NoData
3500 | Permit Expired 12/4/2020; Unpaid $385.38
3501 | NoData
3502 | NoData
3503 | NoData
3504 | NoData
3505 | NoData
3506 | NoData
3507 | NoData
3508 | Fire Alarm needs annual inspection. Last noted inspection was in 2019.
3509 | All fire extinguishers are due for their annual inspection. Last noted inspection was in 2019.
3510 | NoData
3511 | NoData
3512 | PLACE SING SHOWING THAT FIRE EXTINGUISHER IS INSIDE THAT ROOM.COMPLIANCE WITHIN 30 DAYS
3513 | ROMOVE ALLCOMBUSTIBLE MATERIALS FROM ELECTRICAL ROOM AND OR RISER ROOMCOMPLIANCE WITHIN 30 DAYS
3514 | NoData
3515 | NoData
3516 | Location and placement of the fire extinguisher shall be placed in accordance with the manufactures guidelines or Section 1.3.8, near the kitchen entryway, accessible and no closer than 5 feet from the cooking appliance.The extinguisher shall be placed so that the top of the extinguisher is not more than five feet above floor and the clearance between the bottom of the extinguisher and the floor is not less than 4 inches
3517 | Ann Marie Pedraza 832 607 6461 Properties with 3 or more units are required to register with the City of Houston as required by Ordinance No. 2006-1124 (Apartment Security Ordinance).Please contact the City of Houston “Multi-Family Rental Property Registration” at 832-394-8841 or log on to http://www.houstonmultifamily.org/Provide copy of lease agreement with smoke detector, fire extinguisher and openFlame cooking policy or addendum.
3518 | Label Water Heater Room
3519 | Minimum of 2A:10bc fire extinguisher is needed in water heater room.
3520 | Required every 5 years and must be completed with an approved permit from the building department.
3521 | NoData
3522 | NoData
3523 | NoData
3524 | NoData
3525 | NoData
3526 | NoData
3527 | NoData
3528 | HAVE EXIT DOOR IN THE BAY AREA ADJUSTED TO THE RIGHT POUNDAGE OF FORCE TO ALLOW IT TO BE OPEN WITH LESS THAN 15 POUNDS PF PRESSURE.COMPLIANCE WITHIN 30 DAYS.
3529 | HAND-HELD PORTABLE FIRE EXTINGUISHERS SHALL BE INSTALLED ON THE HANGERS OR BRACKETS SUPPLIEDCOMPLIANCE WITHIN 30 DAYS.
3530 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL PERFORM A TEST OF ALL THEFIRE ALARM SYSTEM ANNUNCIATION DEVICES NOT LESS THAN EVERY 3 YEARSCOMPLIANCE WITHIN 30 DAYS
3531 | ROMOVE ALLCOMBUSTIBLE MATERIALS FROM ELECTRICAL ROOM AND OR RISER ROOMCOMPLIANCE WITHIN 30 DAYS
3532 | EXTENSION CORDS SHALL NOT BE USED FOR A PERMITSOURCE OF POWER IN FACILITY.COMPLIANCEWITHIN 30 DAYS
3533 | NoData
3534 | NoData
3535 | Place on entrance gates
3536 | Fail safe needs to be put on gates and work
3537 | Need to have all fire wall and draft stops check for damages . Must pull permit to do this work
3538 | Need all fire blocking walls check for damage in every building
3539 | Need to be placed on entrance gates
3540 | Make sure you have the 10 year Lithium battery warranty .
3541 | Need to get Access gate permit
3542 | And apartment can not be use as a business office without the change of use Certificate of Occupancy have the Building department approve of use
3543 | C Of Occupancy do not match your buildings need building department to verify called 311 # 449-7276
3544 | Need to get Key box permit
3545 | Need 911 locks for 911 boxes paint tow away lines a different color need flammable cabinets paint 911 and fail safe red with 911 in white
3546 | Your permits must be on location and posted in a binder or on wall in a frame
3547 | Need a Site map at the entrance gate
3548 | Need to place a site map at each entrance gate.
3549 | Must be operational do not chain or weld gates
3550 | NoData
3551 | NoData
3552 | NoData
3553 | NoData
3554 | NoData
3555 | NoData
3556 | NoData
3557 | NoData
3558 | NoData
3559 | NoData
3560 | NoData
3561 | NoData
3562 | NoData
3563 | NoData
3564 | NoData
3565 | NoData
3566 | NoData
3567 | NoData
3568 | NoData
3569 | NoData
3570 | NoData
3571 | NoData
3572 | NoData
3573 | NoData
3574 | NoData
3575 | NoData
3576 | NoData
3577 | NoData
3578 | NoData
3579 | NoData
3580 | NoData
3581 | NoData
3582 | NoData
3583 | NoData
3584 | NoData
3585 | NoData
3586 | NoData
3587 | NoData
3588 | NoData
3589 | NoData
3590 | NoData
3591 | Repair all fail-safes on automatic gates. Battery back-ups are not considered fail-safes. Keys for locks to fail-safes need to be placed in 911 box.
3592 | When draft stops have been altered, damaged, breached or penetrated have a responsible party inspect all draft stops in the complex and itemize repairs made for each building and include a statement on their letterhead that all draft stops have been inspected and have been repaired or replaced to the required fire-resistance-rated construction required in accordance with the Houston Fire and Building Codes. See Owner's Statement of Compliance
3593 | See Owner's Statement of Compliance After January 1, 2017, as a battery-operated single-station alarm is replaced, that smoke alarm shall be replaced with a tamper-resistant battery-operated single-station smoke alarm. Provided, however, nothing in this section shall require an owner to replace an operational battery- operated single-station smoke alarm. For the purposes of this provision, a tamper-resistant battery-operated single-station smoke alarm shall mean a sealed, single-station smoke alarm with a long-life lithium or similar battery.
3594 | See Owner's Statement of Compliance
3595 | Reflective signs missing for 3 hydrants on property.
3596 | See Owner's Statement of Compliance
3597 | Sprinkler systems are yellow tagged and issues must be repaired.
3598 | MAKE SURE BOTH THE LEFT AND RIGHT SIDE EXIT DOORS REMAIN UNLOCKED DURING BUSINESS HOURS
3599 | REMOVE THE NEWSPAPER RACKE FROM IN FRONT OF THE EXIT DOOR
3600 | LABEL THE DOOR WITH THE ELECTRICAL PANELS IN IT "ELECTRICAL PANELS INSIDE"
3601 | REPLACE ALL MISSING OR DAMAGED CEILING TILES IN THE STORE
3602 | RENEW THE EXPIRED M3(FUEL DISPENSER) PERMIT AT 1002 WASHINGTON AVE. 832-394-8811 APPLY FOR AND POST THE L1(LPG STORAGE) PERMIT AT 1002 WASHINGTON AVE. 832-394-8811
3603 | INSTALL EMERGENCY EGRESS LIGHTS IN CASE OF POWER OUTAGE OR POWER FAILURE
3604 | NoData
3605 | NoData
3606 | NoData
3607 | NoData
3608 | NoData
3609 | NoData
3610 | NoData
3611 | NoData
3612 | NoData
3613 | NoData
3614 | NoData
3615 | NoData
3616 | NoData
3617 | NoData
3618 | NoData
3619 | NoData
3620 | NoData
3621 | NoData
3622 | NoData
3623 | NoData
3624 | NoData
3625 | NoData
3626 | NoData
3627 | NoData
3628 | NoData
3629 | NoData
3630 | NoData
3631 | NoData
3632 | NoData
3633 | NoData
3634 | NoData
3635 | NoData
3636 | NoData
3637 | NoData
3638 | NoData
3639 | NoData
3640 | NoData
3641 | NoData
3642 | NoData
3643 | NoData
3644 | NoData
3645 | NoData
3646 | NoData
3647 | NoData
3648 | NoData
3649 | NoData
3650 | NoData
3651 | NoData
3652 | NoData
3653 | NoData
3654 | NoData
3655 | NoData
3656 | NoData
3657 | NoData
3658 | NoData
3659 | NoData
3660 | NoData
3661 | NoData
3662 | NoData
3663 | NoData
3664 | NoData
3665 | NoData
3666 | NoData
3667 | NoData
3668 | NoData
3669 | NoData
3670 | NoData
3671 | NoData
3672 | NoData
3673 | NoData
3674 | NoData
3675 | NoData
3676 | NoData
3677 | NoData
3678 | NoData
3679 | NoData
3680 | NoData
3681 | NoData
3682 | NoData
3683 | NoData
3684 | NoData
3685 | NoData
3686 | NoData
3687 | NoData
3688 | NoData
3689 | NoData
3690 | NoData
3691 | NoData
3692 | NoData
3693 | NoData
3694 | NoData
3695 | NoData
3696 | NoData
3697 | NoData
3698 | NoData
3699 | NoData
3700 | NoData
3701 | Micro switch malfunction, repair or replace.
3702 | k1 permit expired 10/22/2020
3703 | NoData
3704 | NoData
3705 | NoData
3706 | NoData
3707 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
3708 | Renewal of the assembly permit is required.
3709 | NoData
3710 | NoData
3711 | NoData
3712 | Repair or replace the inoperable emergency lighting on the exit signs.
3713 | Ensure all exits are operational.
3714 | Provide NFPA 704 compliant signs for the diesel fuel on the outside of the fire pump room and near the generator.
3715 | Replace damaged or missing ceiling tiles.
3716 | NoData
3717 | NoData
3718 | Provide fire extinguishers in appropriate locations throughout the business.
3719 | Have a licensed fire protection company perform an annual fire alarm inspection and correct any deficiencies.
3720 | Keep a record of weekly fire pump test.
3721 | Provide address numbers on the front of the business.
3722 | Label electrical room doors, "Electrical".
3723 | Label the following: sprinkler riser room door "Sprinkler Riser", fire pump room door, "Fire Pump", and fire alarm room door "Fire Alarm".
3724 | Obtain a Certificate of Occupancy with the current business name.
3725 | Obtain a flammable liquids permit (F7) from the Houston Permitting Center for storage of diesel fuel (fire pump and generator have tanks).
3726 | NoData
3727 | NoData
3728 | NoData
3729 | NoData
3730 | NoData
3731 | NoData
3732 | NoData
3733 | NoData
3734 | NoData
3735 | NoData
3736 | NoData
3737 | NoData
3738 | NoData
3739 | NoData
3740 | Continue the process of obtaining your Certificate of Occupancy.
3741 | Provide and illuminated exit sign above the exit door in the warehouse. Remove the exit signs not leading to an exit.
3742 | Provide guards for the for the door opening drop-off on the 2nd floor in the office area.
3743 | Required spacing.
3744 | NoData
3745 | NoData
3746 | NoData
3747 | MAQ for outdoor storage is 1100 gallons. Minimum distance to lot line is 50 ft.. Minimum distance to street is 10 ft..
3748 | Class 1A liquid containers are required to be less than a 5.3 gallon capacity for gravity dispensing.
3749 | Provide a "fail safe" for the access gate.
3750 | Remove obstructions in front of the exit in the warehouse.
3751 | Required height.
3752 | A key box is required near the keypad that will open the access gate.
3753 | Obtain a key box and access gate permit from the Houston Permitting Center.
3754 | Required to increase MAQ.
3755 | NoData
3756 | NoData
3757 | NoData
3758 | The MAQ for 1B and 1C liquids is 120 gallons (MAQ can increase to 240 gallons if stored in approved storage cabinets).The MAQ for class 2 liquids is 240 gallons (MAQ can increase to 480 if stored in approved storage cabinets). Amounts greater than the MAQ are to be removed from the building and stored accordingly.
3759 | NoData
3760 | Outdoor storage for flammable liquids.
3761 | Required for outdoor storage.
3762 | Required for outdoor storage.
3763 | Required for outdoor storage.
3764 | Required for outdoor storage.
3765 | Have SDS forms readily available on site.
3766 | Obtain a flammable combustible liquids permit from the Houston Permitting Center.
3767 | NoData
3768 | NoData
3769 | NoData
3770 | NoData
3771 | NoData
3772 | NoData
3773 | Provide proof of test
3774 | Have all Fire Doors Inspected by a Certified Door Company to the NFPA 80 standard.
3775 | Have all Fire Doors Inspected by a Certified Door Company to the NFPA 80 standard.
3776 | Correct Yellow Tagged Fire AlarmCorrected
3777 | Inspect all fire doors.
3778 | NoData
3779 | NEED TO BE SERVICE TO FIX TAGS. 1-8-20 LAST DATE
3780 | NEED TO BE SERVICE IN NOVEMBER. 5-2020
3781 | Clean around electrical panels
3782 | NoData
3783 | 10-2019. Need to be service in October
3784 | THIS IS JUST INFORMATION
3785 | NoData
3786 | THIS IS JUST INFORMATION .LAST INSPECTION 4-17-2020 - PANEL IS GOOD
3787 | THIS IS JUST INFORMATION . LAST DATE 4-2020,GOOD
3788 | THIS IS JUST INFORMATION
3789 | Fire extinguishers for communal use must be inspected annually.
3790 | LPG tanks cannot be stored on property or used within 10 ft. of a bldg.
3791 | Ensure each electrical meter is mark with the appropriate unit number. Replace any missing dead man covers inside boxes covering breakers.
3792 | Ensure each unit has a smoke detector inside each bedroom and hallways leading to the bedroom.
3793 | Gas test needed for this property or proof that one has been performed.
3794 | NoData
3795 | Directory map needed for this property.
3796 | NoData
3797 | NoData
3798 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
3799 | Post the occupant load.
3800 | Fire alarm system is yellow tagged. Initiated a 72 Hrs. Notice of Violations and a Fire Watch Assignment Agreement.
3801 | NoData
3802 | Micro-switch in west gate needs to be repaired and returned to working order.
3803 | Gas leak test required every 5 years. MAKE SURE A PERMIT WITH THE CITY IS PULLED!
3804 | NoData
3805 | VEHICLE MUST CONFORM TO CODE NOTED ABOVE
3806 | VEHICLE MUST CONFORM TO CODE NOTED ABOVE
3807 | VEHICLE MUST CONFORM TO CODE NOTED ABOVE
3808 | NoData
3809 | NoData
3810 | NoData
3811 | NoData
3812 | NoData
3813 | Dionne McLaughlin NO VIOLATIONS FOUND AT THIS TIME.
3814 | Have a licensed fire protection company service and tag the fire extinguishers.
3815 | Mount the fire extinguisher that's been placed on the ground.
3816 | Ensure the swinging door isn't propped open blocking the fire extinguisher. Move the fire extinguisher if necessary.
3817 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
3818 | Clear and maintain space in front of the breaker panels.
3819 | Post the occupant load.
3820 | Remove locking bars from exits while the building is occupied. Repair door hardware if necessary.
3821 | NoData
3822 | NoData
3823 | NoData
3824 | last annual Fire Sprinkler System Test 1/8/2018
3825 | Correct the Yellow tagged Fire Alarm Panel
3826 | All fire extinguishers should be serviced and have a current service tag placed on them.
3827 | The fire alarm system must have an emergency lighting test performed on it.
3828 | The sprinkler system must have an annual inspection performed on it.
3829 | The ansul system in the kitchen has a red tag that needs to be corrected. The ansul system must be inspected and have a current service tag placed on it.
3830 | The gate code must be put inside of the key box for the gate leading to building B.
3831 | The assembly permit and the fire alarm permit must be renewed and placed inside of the Fire Marshal's Binder. The access gate and key box permits must be printed out and placed inside of the Fire Marshal's Binder.
3832 | NoData
3833 | ALL EMERGENCY EQUIPMENT IS INSPECTED PER ESTABLISHED INTERVALSAND DOCUMENTED - ALL DOCUMENTATION IS POSTED OR ORGANIZED AND KEPT ONSITE FOR FIRE MARSHAL INSPECTION
3834 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
3835 | NO VIOLATIONS FOUND CERTIFICATE OF OCCUPANCY POSTED (45 OCCUPANTS) ALL EMERGENCY LIGHTS AND EXIT LIGHTS INSPECTED AND PASSED FEBRUARY 2020 ALL FIRE EXTINGUISHERS TAGGED JANUARY 2021
3836 | Correct the deficiencies on the yellow tagged fire alarm panel and fire sprinkler system.
3837 | No violations found
3838 | NoData
3839 | NoData
3840 | ENSURE COMPLIANCE WITH CODE.
3841 | ENSURE ALL COMPONENTS OF EGRESS ARE MAINTAINED FREE FROM OBSTRUCTION
3842 | Obtain and post a gate permit (A4) and a key box permit (K1).
3843 | NoData
3844 | NoData
3845 | NoData
3846 | NoData
3847 | NoData
3848 | NoData
3849 | Have vent hood professionally inspected and cleaned. Ensure inspection sticker is placed on the hood.
3850 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit prior to test.
3851 | Clear and maintain clearance in front of the breaker panels.
3852 | NoData
3853 | NoData
3854 | NoData
3855 | NoData
3856 | Post the occupant load. Maximum occupancy is 66.
3857 | Yellow tagged due to 5year test. Letter of intent is needed for the testing of the sprinkler system with dates of start and completion.
3858 | Proof of flow testing is needed for hydrants on property.
3859 | Replace covers to alarm boxes inside sprinkler rooms.
3860 | repairs holes in ceilings inside sprinkler rooms.
3861 | HFD and the number of hydrants behind each access gate must be displayed. Example: "HFD 6"
3862 | Blue markers are needed on driveway indicating the hydrants location.
3863 | Proof of gas test needed.
3864 | Ensure all exit and emergency lighting are operating properly throughout property.
3865 | NoData
3866 | Falcon lock needed on Key box and all Keyboxes must be red in color with 911.
3867 | NoData
3868 | Access gate, Keybox and fire alarm permit.
3869 | proof of permit needed
3870 | NoData
3871 | NoData
3872 | NoData
3873 | NoData
3874 | NoData
3875 | NoData
3876 | NoData
3877 | NoData
3878 | The owner/occupant has the responsibility of correcting or abating all fire code violations or hazards that occur in the business.
3879 | Always maintain approved occupancy of a building as stated be the certificate of occupancy. Failure to do so will result with the event to be stopped until such conditions are corrected and with the possibility of citations being issued.
3880 | Always renew or apply for permits that are required for the business at the City of Houston Fire Permit Office. All be permits are to be obtained prior to engaging in any activities, operations, practices, or functions regulated by this fire code.
3881 | Service all of the portable fire extinguishers in the business, when completed make sure that it has an up to date service sticker.
3882 | NoData
3883 | NoData
3884 | NoData
3885 | NoData
3886 | The kitchen suppression system must be serviced, when completed make sure that it has a current service tag marked acceptable(not yellow or red). The kitchen suppression system should be serviced every 6 months.
3887 | The owner/occupant has the responsibility of correcting or abating all fire code violations or hazards that occur in the business.
3888 | Maintain the allowed occupancy of the business, failure to do so will result in the event to be stopped until such condition are corrected.
3889 | Always renew or apply for permits that are required for the business at the City of Houston Fire Permit Office. All be permits are to be obtained prior to engaging in any activities, operations, practices, or functions regulated by this fire code.
3890 | Service the emergency egress lights in the business. In the event of power supply failure, the emergency egress lights shall automatically illuminate the area where the emergency egress light are placed.(front doors)
3891 | NoData
3892 | FOR REFERENCE
3893 | Provide secondary containment for drums and totes storing hazardous materials as required by code.
3894 | An updated HMIS is required for the storage and use of hazardous materials at this location. Refer to the material SDS sheet for all chemicals at this site. If you have questions after reading the instructions, please email jeannice.mitchell@houstontx.gov and I will set a time to meet and review them.It appears this location has been found to be over MAQ in the past. Ensure that all chemicals are accounted for and remove chemicals that are over the MAQ limits for an occupancy that is 100% sprinkled.Please do not delay reviewing this document and completing it. The compliance date is in 30 calendar days
3895 | Ensure adequate separation between incompatible materials stored within the warehouse is maintained.Do not store hazmat above 6 feet on any racks or shelves throughout the warehouse. This occupancy is not approved for high hazard high piled storage.
3896 | It appears a Certificate of Occupancy was issued in 2013 for this location. This permit is required to be posted on site. Request a copy of the Certificate of Occupancy from the Houston Permitting Center and update information if necessary.Compliance within 7 calendar days (Nov 6, 2020)
3897 | NoData
3898 | Correct yellow tagged Fire Sprinkler System dated 1/5/2021
3899 | NoData
3900 | Correct yellow tagged Fire Sprinkler System dated 1/5/2021
3901 | NoData
3902 | Contact a licensed Fire Protection Company to make any repairs necessary to clear the "trouble" signal on the fire alarm control panel.
3903 | INFORMATION
3904 | INFORMATION
3905 | INFORMATION
3906 | NoData
3907 | NoData
3908 | NoData
3909 | NoData
3910 | NoData
3911 | Fire Alarm needs annual inspection. Last noted inspection was in 2019.
3912 | All fire extinguishers are due for their annual inspection. Last noted inspection was in 2019.
3913 | NoData
3914 | NoData
3915 | NoData
3916 | NoData
3917 | NoData
3918 | NoData
3919 | Access Gate expired 09/2020. Renew within 7 days.
3920 | All gates must have a 911 knox box or an approved LSB 04 padlock.
3921 | All Access gates must comply to LSB 04. Current gates must remain open until all issues are corrected. Gates must comply within 30 days
3922 | NoData
3923 | NoData
3924 | NoData
3925 | NO VISIBLE VIOLATION FOUND
3926 | NoData
3927 | NoData
3928 | NoData
3929 | PLEASE REPAIR KEYBOX AT FRONT DOOR, AND LUBE HINGES AND FALCON LOCKS AT OTHER KEYBOX LOCATIONS
3930 | ONLY PANIC HARDWARE OR SIMILIAR SINGLE OPERATION TO OPEN/UNLOCK LOCKING DEVICES ALLOWED ON THESE DOORS. REMOVE ALL OTHER LOCKING DEVICES.
3931 | NoData
3932 | Fire Alarm Inspections are out of date.
3933 | NoData
3934 | NoData
3935 | NoData
3936 | NoData
3937 | NoData
3938 | A "fail safe" is required on the access gate.
3939 | Obtain a key box permit from the Houston Permitting Center.
3940 | NoData
3941 | NoData
3942 | NoData
3943 | A 911 key box is required on the access gate.
3944 | Obtain and post the Certificate of Occupancy.
3945 | Fire Extinguishers last annual April 2019
3946 | (72 Hours to return system to normal operations)email fire alarm report for red tag and complete a fire watch agreement form ASAP
3947 | semi-annual tag expired dated April 2020
3948 | Fire Alarm Panel Red Tagged on 5/21/2020.(72 Hours to return system to normal operations)email fire alarm report for red tag and complete a fire watch agreement form ASAP.
3949 | NoData
3950 | Red Tag on kitchen ansul system due to repositioning of extinguishing nozzles.
3951 | 5 year gas test is due. The state my require you to perform this test annually.
3952 | Boiler inspection is due.
3953 | Pertaining to all the fire egress doors and room fire doors on each floor.
3954 | Pertaining to all the fire egress doors and room fire doors on each floor.
3955 | Pertaining to all the fire egress doors and room fire doors on each floor.
3956 | NoData
3957 | NoData
3958 | NoData
3959 | NoData
3960 | LSB2020.1.3.6 Installation.Portable fire extinguishers shall be installed on the hangers or in the brackets supplied, mounted in cabinets, or set on shelves, unless the extinguisher is of the wheeled type.Compliance: 30 calendar days.
3961 | 109.2 Owner/occupant responsibility. Correction and abatement of violations of this code shall be the responsibility of the owner. If an occupant creates, or allows to be created, hazardous conditions in violation of this code, the occupant shall be held responsible for the abatement of such hazardous conditions.
3962 | 6103.2.2 Industrial vehicles and floor maintenance machines. LP-gas containers on industrial vehicles and floor maintenance machines shall comply with Sections 11.13 and 11.14 of NFPA 58. Industrial lift trucks stored inside of buildings shall be kept in an approved area. LP-gas containers not attached for use shall be stored outside of the building in accordance with Table 6104.3 .Compliance: immediately.
3963 | 604.2.4 Means of egress illumination. Emergency power shall be provided for means of egress illumination in accordance with Section 1006.3.Compliance: 30 calendar days.
3964 | Where access to or within a structure or an area is restricted because of secured openings or where immediate access is necessary for life-saving or fire-fighting purposes, the fire code official is authorized to require a key box or a fire depository box to be installed in an approved location. The key box shall be of an approved type listed in accordance with UL 1037, and shall contain keys to gain necessary access as required by the fire code official. Key boxes shall be provided in accordance with Houston Fire Department LSB Standard No. 05, “Key Boxes.”
3965 | For reference
3966 | Have all yellow and red tags serviced and properly tagged for all suppression and notification systems on location. "Alarm, sprinkler and spray booth"
3967 | Must obtain a Certificate of Occupancy for each building addressed to this location. Apply at Houston Permitting Office at 1002 Washington Ave. Houston, TX 77002
3968 | All systems must be maintained and operational
3969 | NoData
3970 | NoData
3971 | NoData
3972 | NoData
3973 | NoData
3974 | NoData
3975 | NoData
3976 | System need service, has a trouble light on. 6-5-19 last inspection date.
3977 | Need service. 8-19 last date
3978 | Need service. 2-20 last date
3979 | NEED SERVICE , LAST DATE 11-2019
3980 | NEED SERVICE, LAST DATE 5-2020
3981 | NoData
3982 | NEED SERVICE, LAST DATE 2-2019
3983 | NEED SERVICE ,HAS TROUBLE LIGHT ON. 8-28-2020 LAST DATE
3984 | NEED SERVICE. 4-2020 LAST DATE
3985 | NoData
3986 | NEED SERVICE. 7-2019 LAST DATE
3987 | NoData
3988 | NoData
3989 | NoData
3990 | NoData
3991 | NoData
3992 | Provide smoke detectors in both rooms.
3993 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
3994 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
3995 | Provide documentation/report for fire damper testing and any necessary repairs.
3996 | Provide certificate of flame resistance, it shall indicate the color for all decorative materials. 1. New curtains, new certificate or 2. New certificate showing retesting of flame resistance
3997 | Provide Boiler Permits #265332, 265333 (Expired 1/4/21)
3998 | NoData
3999 | NoData
4000 | NoData
4001 | OBTAIN 911 KEYBOX FROM LIST OF KEY BOX COMPANIES ATTACHED VIA EMAIL. MORE INFORMATION WILL BE INCLUDED IN THE LIFE SAFETY BUREAU STANDARD 5- KEY BOXES ATTACHED VIA EMAIL
4002 | GENERAL INFORMATION
4003 | Remove the swinging door by the rear exit door that blocks the exit. Remove the trash blocking the path leading to the rear exit door.
4004 | Remove the lock on the wooden door leading to the rear exit door.
4005 | KEY BOX COMPANY WILL ALSO HAVE THE "HOUSTON" FALCON PADLOCK APPROVED BY THE HOUSTON FIRE DEPARTMENT IN ORDER TO SECURE THE 911 KEY BOX AND ONLY BE OPENED BY THE HOUSTON FIRE DEPARTMENT ONCE YOU HAVE YOUR KEYBOX INSTALLED AND FALCOLN PADLOCK AVAILABLE, GIVE ME A CALL AND I WILL COME OVER TO UNLOCK THE LOCK FOR YOU. YOU MAY THEN PLACE ANY NECCESSARY ACCESS KEYS, KEYCARDS, CONTACT INFORMATION ETC INSIDE THE BOX AND I WILL SECURETHE BOX FOR YOU.
4006 | CITY OF HOUSTON REQUIRES A 911 KEY BOX PERMIT. CODED BY THE PERMIT OFFICE AS A K1 PERMIT
4007 | Have a licensed fire protection company perform an annual fire alarm inspection and correct any deficiencies.
4008 | Have a licensed fire protection company perform an annual fire sprinkler inspection and correct any deficiencies.
4009 | Have a licensed fire protection company perform a 5 year FDC inspection and correct any deficiencies.
4010 | The fire sprinkler system requires monitoring.
4011 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
4012 | NoData
4013 | Permit Expired 11/18/2020; Unpaid Fees $266.80
4014 | NoData
4015 | NoData
4016 | All fire extinguishers must be serviced and have a current service tag placed on them.
4017 | The fire alarm system must have an emergency lighting test performed on it.
4018 | The fire sprinkler system must have an annual inspection performed on it.
4019 | The gate code must be put inside of the key box for the gate leading to building B.
4020 | The elevator must have an annual inspection performed on it.
4021 | The key box, assembly, access gate and fire alarm permits must obtained from the permit office and placed inside of the Fire Marshal's Binder.
4022 | NoData
4023 | AFS tested fire alarm system on 1/07/21 and placed a red tag violation on System. Please have all issues corrected within 72 hours.
4024 | Amount Due: $385.38
4025 | NoData
4026 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
4027 | THE OWNER / OCCUPANT SHALL BE HELD RESPONSIBLE FOR THE CORRECTION AND ABATEMENT OF ALL VIOLATIONS LISTED IN THIS NOTICE OF VIOLATIONS REPORT. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4028 | FIRE EXTINGUISHERS EVERY 75 FEET IN THE BACK OF THE WAREHOUSE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4029 | BREAKER PANEL REQUIRED THREE FEET OF SPACE OF NO STORAGE OF CLEAREANCE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4030 | APPLY FOR AND OBTAIN A KEY BOX AND HIGH-PILED OPERATIONAL PERMIT FROM THE CITY OF HOUSTON PERMITTING CENTER LOCATED AT 1002 WASHINGTON AVE. (832-394-9000). COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4031 | AT THE TIME OF INSPECTION, APPROVED PLANS COULD NOT BE PRESENTED FOR INSPECTION BY THE FIRE MARSHAL. APPROVED PLANS ARE TO BE KEPT ON SITE AT ALL TIMES. IF APPROVED PLANS CANNOT BE LOCATED, A REQUEST TO THE BUILDING DEPARTMENT MAY BE ABLE TO DUPLICATE THE ORIGINAL. APPROVED PLANS MUST BE SUBMITTED TO FIRE MARSHAL OR THE PROCESS FOR HIGH-PILED STORAGE PLAN SUBMITTAL PROCESS SHALL BE RESTARTED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4032 | NFPA 13: 12.12.1.2 – WOOD PALLETS, WHERE STORED INDOORS, SHALL MEET THE FOLLOWING:(1) PALLETS SHALL BE STORED NO HIGHER THAN 6 FEET.(2) EACH PALLET PILE OF NO MORE THAN 4 STACKS SHALL BE SEPARATED FROM OTHER PALLET PILES BY AT LEAST 8 FEET OF CLEAR SPACE OR 25 FEET OF COMMODITY.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4033 | AISLES WIDTHS STATED ON THE APPROVED PLANS ARE NOT BEING MAINTAINED AND SHALL BE BROUGHT INTO COMPLIANCE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4034 | THE EXIT PATHWAYS AND EXIT STAIRWAYS LEADING AWAY FROM THE WAREHOUSE SHALL HAVE A CLEAR PATH TO AN AREA OF SAFE REFUGE.COMPLIANCE: WITHIN 7 CALENDAR DAYS.
4035 | NoData
4036 | NoData
4037 | NoData
4038 | NoData
4039 | NoData
4040 | NoData
4041 | NoData
4042 | NoData
4043 | NoData
4044 | NoData
4045 | Exit signs required at main entrance and back exit
4046 | Clearance to the gas hot water heaters must be maintained at least 3 feet
4047 | Please place two (2) fire extinguishers. One in hallway to stylist rooms and one in the main barber shop area. The extinguishers must have a min 2A,10B:C rating
4048 | Keep all exit door(s) and pathways clear. Please remove drop bars in front of exit. Either the iron gate or drop bars can be allowed with restrictions but not both
4049 | Non-functioning door needs label - NOT AN EXIT
4050 | NoData
4051 | Doors to electrical room(s) must be identified - ELECTRICAL ROOM
4052 | 3-way plugs or multiple outlet adapters are not allowed unless they are "resettable" type (overcurrent protected)
4053 | 3-way plugs or multiple outlet adapters are not allowed unless they are "resettable" type (overcurrent protected)
4054 | Multiplug adapters cannot be plugged into an extension cord
4055 | Extension cord cannot be substituted for permanent wiring, AC unit will need to be plugged into a receptacle
4056 | Extension cords cannot be daisy chained. I.E. Cannot plug an extension cord into another extension cord
4057 | No missing spacers allowed in electrical panels; All junction boxes, light switches and plug outlets must have cover plates installed
4058 | Minimum illumination level for all exit signs
4059 | Exit signs must remain illuminated for at least 90 min during a power outage
4060 | Obtain and post Certificate of Occupancy [104.1(9)]. Current yellow application receipt also acceptable
4061 | Sign/stickers posted on or next to doorway of main entrance - THIS DOOR TO REMAIN UNLOCKED WHILE BUILDING IS OCCUPIED or THIS DOOR TO REMAIN UNLOCKED DURING BUSINESS HOURS. Lettering must be at least 1" tall and contrasting color
4062 | Exit signs must be continually illuminated, either internally or externally
4063 | NoData
4064 | NoData
4065 | NoData
4066 | NoData
4067 | NoData
4068 | NoData
4069 | NO VIOLATIONS FOUND AT THIS TIME
4070 | Permit Expired 1/8/2021; Unpaid Fees $385.38
4071 | NoData
4072 | NoData
4073 | NoData
4074 | NoData
4075 | NoData
4076 | NoData
4077 | NoData
4078 | NoData
4079 | NoData
4080 | NoData
4081 | NoData
4082 | NoData
4083 | NoData
4084 | NoData
4085 | NoData
4086 | NoData
4087 | NoData
4088 | NoData
4089 | NoData
4090 | NoData
4091 | Stand by may be required
4092 | reg tag system
4093 | exit sign missing front door
4094 | NoData
4095 | NoData
4096 | 109.2 Owner/occupant responsibility. Correction and abatement of violations of this code shall be the responsibility of the owner. If an occupant creates, or allows to be created, hazardous conditions in violation of this code, the occupant shall be held responsible for the abatement of such hazardous conditions.
4097 | NoData
4098 | No violations at this time.
4099 | citation written
4100 | exit sign missing front door
4101 | exit sign missing front door
4102 | NoData
4103 | NoData
4104 | NoData
4105 | NoData
4106 | NoData
4107 | NoData
4108 | NoData
4109 | NoData
4110 | NoData
4111 | NoData
4112 | NoData
4113 | NoData
4114 | NoData
4115 | NoData
4116 | NoData
4117 | NoData
4118 | Bianca
4119 | FIRE ALARM PANEL NEEDS ANNUAL INSPECTION PERFORM. LAST DATE INSPECTED ON 10/2/2019.
4120 | NoData
4121 | NoData
4122 | NEED INTERCOM INSPECTION TEST, LAST INSPECTION 2-2016 BRING UP TO CODE, PLACE PAPER WORK IN FIRE MARSHAL BINDER
4123 | NEED TO DISPLAY SIGN ON DOOR FIRE ALARM
4124 | Both risers (main building and practice gym) were yellow-tagged in 2018 and still have not been corrected as of 1/26/2021. Pay reinspection fee for failure to correct yellow tags.
4125 | AS PER CODE, LAST INSPECTION ON EMERGENCY LIGHTING 6-2-2015 BRING UP TO CODE, PLACE PAPER WORK IN FIRE MARSHAL BINDER
4126 | LAST INSPECTION ON SPRINKLER RISER 2-2018 SPRINKLER RISER YELLOW TAGGED BRING UP TO CODE
4127 | SPRINKLER RISER YELLOW TAGGED VALVE #2 LEAKING BRING UP TO CODE
4128 | LAST INSPECTION ON SPRINKLER RISER 2-2018 SPRINKLER RISER YELLOW TAGGED BRING UP TO CODE
4129 | SPRINKLER RISER YELLOW TAGGED VALVE #2 LEAKING BRING UP TO CODE
4130 | NoData
4131 | NoData
4132 | NoData
4133 | NoData
4134 | NoData
4135 | Correct red-tagged fire alarm panel within 72 hours.2/3/2021 - Red tag corrected on 1/26/2021 - OK
4136 | Fire alarm panel is red-tagged due to phone lines #1 and #2 being down. Correct red tag conditions and return fire alarm system to full operational status within 72 hours.2/3/2021 - Red tag corrected on 1/26/2021 - OK
4137 | NoData
4138 | NoData
4139 | K1 FIRE PREVENTION PERMIT IS EXPIRED AT THIS TIME.
4140 | COMPLIANCE DATE: 15 CALENDAR DAYS
4141 | COMPLIANCE DATE: 15 CALENDAR DAYS
4142 | P2 permit is expired at this time.
4143 | NoData
4144 | NoData
4145 | Amount Due: $296.44
4146 | NoData
4147 | P2 permit is expired. Expired on 10/07/2020.Amount owed for permit 385.38 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
4148 | NoData
4149 | NoData
4150 | Apply for a compressed gas operational permit at the Houston Permitting Center.Compliance within 7 calendar days
4151 | FOR REFERENCE
4152 | The address identifier for your business at this site is "D". Replace the identifier with a similar sign as the letters that appear on all of the other buildings in the complex. It should be unobstructed from view by the main street leading to the building.Compliance within 30 calendar days.
4153 | Ensure all illuminated Exit signs and emergency lighting are working properly. Repair or replace any with deficiencies.Compliance within 30 calendar days
4154 | Apply for the Hot Works operational permit at the City of Houston Permitting Center.Compliance within 7 calendar days (Nov, 5 2020)
4155 | An application for a Certificate of Occupancy must be completed at the Houston Permitting Center. A receipt must be provided to our office for our records.Compliance within 7 calendar days (Nov 5, 2020)
4156 | FOR REFERENCE
4157 | An updated HMIS that reflects the storage/in use/open use chemicals for your location BLDG C only. Indoor and outdoor locations are also noted. This is to ensure that chemicals remain below maximum allowable quantity.
4158 | Obtain a permit through the Houston Permitting Center for LPG as required.
4159 | Have a small extinguisher installed on each forklift with LPG fuel. These extinguishers must be serviced annually.
4160 | Yellow Tag deficiencies on the Suppression system must be corrected and the system maintained in operational readiness condition.
4161 | An L1 permit must be obtained for the LPG on site. This permit is purchased at the Houston Permitting Center 1002 Washington Ave, Houston TX 77002
4162 | NoData
4163 | Annual drop test on the vertical rolling fire door must be completed with a tag affixed to the side.
4164 | Per NFPA 72 (National Fire Alarm Code), high velocity, low speed (HVLS) fans require interlocks that are connected to the water flow alarm of the sprinkler system.Provide documentation (from alarm company) that the HVLS fans have properly functioning interlocksconnected to the alarm panel.
4165 | Remove all vehicles from within the building as required by code. Vehicles are not to be parked or stored inside the building.
4166 | Ensure proper clearance is maintained around all electrical panels throughout the facility
4167 | Label the door leading into the riser and alarm room "ALARM ROOM" on a red placard with white lettering to easily identify the location of this equipment during an emergency.
4168 | Provide documentation that the alarm panel is in operational readiness condition with no trouble signal or red tags.
4169 | Ensure there is adequate clearance in front of and around electrical panels throughout the facility as described in the above code. Remove all combustibles and storage from the area.
4170 | NoData
4171 | 1-2018 NEED TO BE SERVICE
4172 | 6-11-2019 NEED TO BE SERVICE
4173 | 4-2020 LAST INSPECTION
4174 | 1-2018 NEED TO BE SERVICE
4175 | 8-2019 LAST INSPECTION
4176 | 7-15-2019 LAST INSPECTION. SYSTEM NEED SERVICING HAS TROUBLE SIGNALS
4177 | LAST INSPECTION 11-2019
4178 | 3-2020 LAST INSPECTION
4179 | 3-2020 LAST INSPECTION
4180 | NoData
4181 | Your k1 (key box) permit expired on 1-12-2021, renew your permit using the options given by the date listed.Total amount due is $
4182 | 1/20/2021 - Blue, OK
4183 | 3/30/2018 - OK
4184 | 7/3/2019 - OK
4185 | Obstructed drills OK
4186 | Drill log OK - Drills conducted monthly
4187 | 1/7/2019 - OK
4188 | 6/2018Have all portable fire extinguishers inspected
4189 | Add one fire extinguisher to hallway near nurse's office.
4190 | Remove all tables from auditorium egress hallway.
4191 | Correct all violations within 60 calendar days.
4192 | 6/2/2015Have sprinkler system inspected and any deficiencies corrected.
4193 | 12/18/2015Have 5-year hydro performed and have any deficiencies corrected.
4194 | 5/2020Have ANSUL system inspected and have any deficiencies corrected.
4195 | Per code.
4196 | Provide documentation that required annual fire safety training was conducted.
4197 | Place "Sprinkler Riser" sign on outside of hallway door that leads to storage area under/behind stage.
4198 | Remove all obstructions that prevent access to riser room. Remove items blocking electrical panels in storage area under/behind stage.
4199 | Remove open wire splice on refrigerator in kitchen (top-rear of refrigerator near kitchen hood).Cover open junction box in boiler room.
4200 | Replace all missing/damaged ceiling tiles (including inside riser room)
4201 | Some rooms are missing evacuation maps. Ensure maps are posted near all classroom exits.
4202 | 1/23/2021 - Fire alarm RED TAGCorrect red tag conditions within 72 hours (see inspection report 321799 e-mailed on 1/27/2021).
4203 | Renew expired elevator permit.
4204 | Have egress lighting test performed and provide documentation that any deficiencies were corrected.
4205 | NoData
4206 | NoData
4207 | NoData
4208 | NoData
4209 | NoData
4210 | NoData
4211 | NoData
4212 | NoData
4213 | NoData
4214 | NoData
4215 | Fire Alarm Inspections are out of date.
4216 | NoData
4217 | NoData
4218 | NEED TO BE SERVICE 6-19 LAST DATE
4219 | NEED TO BE SERVICE 12-19 LAST DATE
4220 | NEED TO BE SERVICE 12-19 LAST DATE
4221 | NoData
4222 | Last inspection date 10-11-19. Need service in October. Need to put a fire panel inside sign by the door. Room 164 -BCR/BDP
4223 | Need service. Last inspection 11-2017
4224 | NoData
4225 | NoData
4226 | NoData
4227 | NoData
4228 | NoData
4229 | ALL VIOLATIONS SHALL BE CORRECTED BY THE OWNER AND/OR INDIVIDUAL IN CHARGE ONCE ALL VIOLATIONS HAVE BEEN CORRECTED SUBMIT PHOTO VIA EMAIL OR TEXT AND I WILL APPROVE YOUR ANNUAL SAFETY SURVEY PERMIT
4230 | MANUAL ANSUL SYSTEM PULL STATION INSIDE KITCHEN WAS LAST INSPECTED ON 10/2017. MUST BE SERVICED EVERY 6 MONTHS EMAIL OR TEXT PHOTO OF UPDATED SERVICE TAG. CONTACT INFORMATION LOCATED ON INSPECTION REPORT
4231 | NoData
4232 | FDC SIGN NEXT TO RISER ROOM HAS FADED. REPLACE WITH A NEW FDC SIGN HAVING THE SAME DIMENSIONS OR LARGER. SEND PHOTO OF UPDATED SIGN VIA EMAIL OR TEXT
4233 | P2 permit is expired. Expired on 12/21/2020. Amount owed for permit 266.80 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
4234 | Move the guy wire next to the fire hydrant to maintain 3 feet of clearance around the hydrant.
4235 | Please make sure both Access gate (a4) and key box (k1) expired permits are renewed. My system shows permits expired on 01/23/2016 under project number - 07005723
4236 | Please renew your access gate (a4) permit.Permit expired on 01/09/2021.
4237 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
4238 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
4239 | Repaint Fire Lane
4240 | Please renew your key box (k1) expired permit.Permit expired on 05/19/2019.
4241 | THE SIGNS SHALL BE LOCATED ON OR ADJACENT TO THE CONNECTION AND SHALL BE CONSTRUCTED OF DURABLE MATERIAL. PROVIDE SPECIFIC SIGNAGE FOR THE FIRE DEPARTMENT CONNECTION WHICH SERVES ALL SCHOOLS (ELSIK AND HASTINGS 9TH GRADE CENTERS)
4242 | PROVIDE REPORT OF TEST RESULTS IF DECORATIVE MATERIALS ARE TO MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701. CERTIFICATE OF FLAME RESISTANCE SHALL INDICATE THE COLOR AND/OR NUMBER FOR ALL DECORATIVE MATERIALS THROUGHOUT SCHOOL. PROVIDE UPDATED CERTIFICATE OF FLAME RESISTANCE -STAGE CURTAINS: NAVY AND BLACK -FLAGS
4243 | CORRECT/REPAIR 3/12/2019 YELLOW TAG ON SPRINKLER SYSTEM -#1, 702 MECHANICAL ALL TWO WAY COMMUNICATION NOT IN OPERATIVE CONDITION SHALL BE REMOVED.
4244 | PROVIDE PORTABLE FIRE EXTINGUISHER -ROOM 112
4245 | AN APPROVED HVAC COMPANY SHALL CONDUCT A FULL-FUNCTION TEST AND MAINTENANCE ON ALL FIRE DAMPERS AT LEAST EVERY 4 YEARS. PROVIDE DOCUMENTATION/REPORT OF TESTING RESULTS AND MAINTAIN ON FILE FOR FIRE CODE OFFICIAL. ALL FAILURES OF THE FIRE DAMPER TESTING SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
4246 | REPAIR EXIT SIGN -GYM
4247 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL OF THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY 3 YEARS. LAST AUDIBILITY TEST DATED: UNKNOWN PROVIDE WRITTEN DOCUMENTATION/REPORT OF AUDIBILITY TEST AND MAINTAIN ON FILE FOR FIRE CODE OFFICIAL. ANY FAILURES OF THE AUDIBILITY TESTING SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
4248 | AN APPROVED LICENSED MASTER ELECTRICIAN OR LICENSED ELECTRICAL SERVICE COMPANY SHALL TEST ALL EMERGENCY LIGHTING SYSTEMS ANNUALLY. LAST TEST DATE: UNKNOWN PROVIDE WRITTEN DOCUMENTATION/REPORT OF TESTING RESULTS AND MAINTAIN ON FILE FOR FIRE CODE OFFICIAL. ANY FAILURES OF THE EMERGENCY LIGHTING SYSTEM SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
4249 | REPAINT FIRE LANE THROUGHOUT SCHOOL
4250 | A LICENSED SERVICE COMPANY SHALL CONDUCT HYDROSTATIC AND FLOW TESTS ON ALL FIRE DEPARTMENT CONNECTIONS EVERY 5 YEARS IN CONJUNCTION WITH THE STANDPIPE SYSTEM 5-YEAR TEST. PROVIDE DOCUMENTATION/REPORT AND BLUE TAG OF THE 5-YEAR TEST ON THE FIRE DEPARTMENT CONNECTION
4251 | BOILER CERTIFICATE OF OPERATIONS SHALL BE MAINTAINED ON PREMISES. PROVIDE CERTIFICATE FOR # 239325
4252 | PROVIDE DOCUMENTATION FOR DETECTOR SENSITIVITY TESTING. VERIFY ALL DETECTOR SENSITIVITY IS IN WORKING CONDITION. LAST SENSITIVITY TEST DATED: UNKNOWN
4253 | REMINDER: ALL CURTAINS, DRAPERIES, HANGINGS AND OTHER DECORATIVE MATERIALS SHALL MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701 OR BE NONCOMBUSTIBLE. PROVIDE CERTIFICATE OF FLAME RESISTANCE (SEE FIRE CODE BELOW, 807.2) OR REMOVE ALL THAT DO NOT MEET THE CRITERIA.
4254 | PROVIDE SIGNAGE "FIRE ALARM PANEL" ON/BY DOOR WHERE THE FIRE ALARM SYSTEM PANEL IS LOCATED. -ROOM 505 MDF (LIBRARY) PROVIDE SIGNAGE "SPRINKLER RISER" ON DOOR WHERE THE SPRINKLER RISER IS LOCATED. -313 MECHANICAL
4255 | ALL EXIT SIGNS SHALL BE ILLUMINATED AT ALL TIMES. REPAIR EXIT SIGN. -EXIT SIGN ON STAGE
4256 | CURRENT INFORMATION -FPS FIRE ALARM SYSTEM ANNUAL INSPECTION DATE: 11/15/2018 ACCEPTABLE BLUE TAG SPRINKLER SYSTEM INSPECTION DATE: 3/12/2019 ACCEPTABLE BLUE TAG ANNUAL FIRE EXTINGUISHER INSPECTION DATE: 6/2019 ANSUL SYSTEM BI-ANNUAL INSPECTION DATE: 7/2019 (2)
4257 | NoData
4258 | no p2 expired 11/20
4259 | no p2 expired 11/20
4260 | Please renew expired access gate (a4) and key box (k1) permits. Both permits expired on 09/21/2019.
4261 | Please add label to door - "Electrical Room"
4262 | Please maintain minimum aisle widths throughout store.
4263 | Please add red DOT tape around pole with fire extinguisher to identify location. Refer to the red tape already used to identify where red phone is located.
4264 | NoData
4265 | Please renew your expired access gate (a4) permit.Permit expired on 02/24/2020.
4266 | Please renew your expired permit
4267 | NoData
4268 | Remount the fire extinguisher in the kitchen to ensure the top of the fire extinguisher isn't higher than 5 feet from the ground.
4269 | Move the class k extinguisher located in the side exit hallway and remount in the kitchen area.
4270 | Remove obstructions in front of the exit located on the side of the business.
4271 | Have a licensed fire protection company inspect and tag the vent hood extinguishing system. Have the vent hoods cleaned and tagged with the date of professional cleaning.
4272 | Post address numbers on the front of the business.
4273 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
4274 | Repair the inoperable emergency illumination on the exit signs.
4275 | Post the occupant load.
4276 | NoData
4277 | NoData
4278 | EXPIRED P2
4279 | Please renew your expired permit
4280 | The City of Houston requires an occupancy with an electronic access gate and key box to hold and maintain a K1 (Key Box) and A4 ( Access Gate) permit. Permits can be obtained through the Houston Permitting Center located at 1002 Washington Ave Houston, Tx 77002. 832-394-8811
4281 | Please renew your expired access gates permit.permit expired on 12/11/2019.
4282 | NoData
4283 | NoData
4284 | NoData
4285 | NoData
4286 | Remove the electrical cord that passes through the wall of the shop into the golf cart garage.
4287 | Install a pin lock fail-safe on the swing gates.
4288 | None of the gates have 911 locks
4289 | Label all breaker box with the unit number they control.
4290 | Exit and Manual Gates are missing the HFD hydrant signs.
4291 | Provide a current natural gas test with permit for the complex.
4292 | Remove storage placed near the electric transformers and the water heaters.
4293 | Renew the Assembly permit before it expires on 12/30/2020.
4294 | Provide address numbers for the front of the business.
4295 | BREAKER PANELS REQUIRED A THREE FEET DISAANCE CLEARANCE WITH NO STORAGE HAZARDS.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4296 | FIRE EXTINGUISHERS ARE REQUIRED EVERY 75 FEET IN THE WAREHOUSE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4297 | AT THE TIME OF INSPECTION, APPROVED PLANS COULD NOT BE PRESENTED FOR INSPECTION BY THE FIRE MARSHAL. APPROVED PLANS ARE TO BE KEPT ON SITE AT ALL TIMES. IF APPROVED PLANS CANNOT BE LOCATED, A REQUEST TO THE BUILDING DEPARTMENT MAY BE ABLE TO DUPLICATE THE ORIGINAL. APPROVED PLANS MUST BE SUBMITTED TO FIRE MARSHAL OR THE PROCESS FOR HIGH-PILED STORAGE PLAN SUBMITTAL PROCESS SHALL BE RESTARTED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4298 | AISLES WIDTHS STATED ON THE APPROVED PLANS ARE NOT BEING MAINTAINED AND SHALL BE BROUGHT INTO COMPLIANCE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4299 | THE EXIT PATHWAYS AND EXIT STAIRWAYS LEADING AWAY FROM THE WAREHOUSE SHALL HAVE A CLEAR PATH TO AN AREA OF SAFE REFUGE.COMPLIANCE: WITHIN 7 CALENDAR DAYS.
4300 | NoData
4301 | NoData
4302 | All fire extinguishers must have current inspection tag.
4303 | Hang all fire extinguisher.
4304 | NoData
4305 | NoData
4306 | NoData
4307 | NoData
4308 | NoData
4309 | Correct the deficiencies on red tagged fire alarm panel.
4310 | NoData
4311 | NoData
4312 | NoData
4313 | NoData
4314 | 11/20/2020 - Red and Yellow taggedRed and yellow tags corrected 11/20/2020 - OK
4315 | 4/12/2019 - OK
4316 | 2/14/2018 - Blue, OK
4317 | 5/21/2019 - OK
4318 | Drills conducted monthly. Log OK.
4319 | 11/20/2020 - OK
4320 | 9/2019Have all portable fire extinguishers inspected.
4321 | Correct all violations within 60 calendar days.
4322 | 2/14/2018 - HAVE SPRINKLER SYSTEM INSPECTED
4323 | Have dampers tested and provide documentation that deficiencies were corrected.
4324 | 5/2020Have ANSUL system inspected.
4325 | Conduct and document required annual fire safety training.
4326 | Provide updated EOP for 20-21 school year.
4327 | Obstructed drills documented - OK
4328 | Updated expired elevator permit.
4329 | 1/17/2020Have egress lighting test performed and provide documentation that deficiencies were corrected.
4330 | NoData
4331 | NoData
4332 | NoData
4333 | NoData
4334 | NoData
4335 | NoData
4336 | Keys for failsafe boxes must be located in main gate access keybox
4337 | Access gates required to be operational from keybox
4338 | NoData
4339 | NoData
4340 | NoData
4341 | NoData
4342 | COMPLY WITH ABOVE CODE
4343 | NEMO TAHIRI
4344 | TAGS AND LABLES SHALL NOT BE REMOVE BY RESTAURANT PERSONNEL.
4345 | COMPLY WITH ABOVE CODE
4346 | COMPLY WITH ABOVE CODE
4347 | COMPLY WITH ABOVE CODE.
4348 | Permit Expired 12/20/2020; Unpaid Fees $266.80
4349 | Michelle Pirtle 713 910 7774
4350 | service yellow tag sprinkler system
4351 | service private hydrant
4352 | service no tag fire extinguisher in shop and elevator room.
4353 | 3 ft clearance from circuit breaker and water heater
4354 | Label shop, Label Fire alarm room
4355 | repair stairway door.
4356 | repair emergency lighting in hallway.
4357 | post current certificate of occupancy, k1 permit, a4 permit, elevator permit, fire alarm permit.
4358 | replace low batteries smoke detector.
4359 | NoData
4360 | NoData
4361 | NoData
4362 | NoData
4363 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
4364 | MUST MAINTAIN THE ALARN SYSTEM AT ALL TIMES. ALL TROUBLE AND SUPERVISERY SIGNALS MUST BE REPAIRED.
4365 | NoData
4366 | NoData
4367 | NoData
4368 | NoData
4369 | NoData
4370 | NoData
4371 | NoData
4372 | NoData
4373 | NoData
4374 | NoData
4375 | NoData
4376 | NoData
4377 | Compliance: 30 calendar days.
4378 | NoData
4379 | NoData
4380 | Fire extinguishers are due for annual inspection before the end of 12/2020.
4381 | Mount the fire extinguishers placed on the ground.
4382 | Replace missing ceiling tiles.
4383 | Clear and maintain 36 inches of clearance in front of the breaker panels.
4384 | Clear and maintain aisle clearance.
4385 | NoData
4386 | NoData
4387 | Correct the yellow tagged fire alarm panel.
4388 | Have a licensed fire protection company perform a 5 year FDC test and correct and deficiencies.
4389 | Clear and maintain 18 inches of ceiling clearance.
4390 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
4391 | Bianca
4392 | FIRE ALARM PANEL NEEDS ANNUAL INSPECTION PERFORM. LAST DATE INSPECTED ON 10/2/2019.
4393 | provide and install a metal can with a metal lid for storage of oily rags in shop area
4394 | Have a licensed fire protection company perform an annual sprinkler inspection and correct any deficiencies.
4395 | Have the emergency lighting tested and replace any inoperable lighting.
4396 | Amount Due: $385.38
4397 | NoData
4398 | NEED TO DO ANNUAL SPRINKLER SYSTEM TEST
4399 | NEED TO DO THE ANNUAL FIRE PUMP
4400 | Need to replace the elevator evacuation signs in every elevator lobby
4401 | NEED ANNUAL ALARM SYSTEM TEST
4402 | NEED AUDIBILITY SYSTEM TESTING
4403 | NEED EMERGENCY LIGHTING TESTING
4404 | NEED TO TEST THE EMERGENCY POWER
4405 | Management is responsible for the Life Safety Components of the High Rise building (as per the Fire Code)
4406 | Need a permit for the diesel storage (f7 permit)
4407 | Need to add a 911 box for the front entrance and garage entrance.
4408 | NEED TO DO THE ANNUAL FIRE EXTINGUISHER INSPECTION
4409 | NEED TO TEST THE EMERGENCY DAMPERS
4410 | NEED TO TEST THE FDC
4411 | NoData
4412 | NoData
4413 | Label the exterior of the doors leading to the Electrical/Fire Pump room.
4414 | Label elevator mainline disconnect switches.
4415 | Obtain F7 (flammable liquids) and K1 (key box)permits.
4416 | Provide keys for the fire pump, mechanical rooms and elevator fire service keys in the key box.
4417 | FIRE ALARM SYSTEM NEEDS TAG
4418 | NEED DIESEL PERMIT FOR DIESEL (FL7)
4419 | NEED ELEVATOR EVACUATION SIGN (GARAGE ELEVATOR)
4420 | NoData
4421 | NoData
4422 | NoData
4423 | NoData
4424 | Renew the facility's P2: Public Assembly permit which expired on 12/20/2020.
4425 | STAIRWAY REENTRY DOORS DID NOT RELEASE FROM THE SECURITY CONSOLE WHEN TESTED AS REQUIRED. THERE WAS SOME CONFUSION ON HOW THE SYSTEM IS SUPPOSED TO FUNCTION AND POSSIBLY A NEW SYSTEM WAS BEING PHASED IN. STAIR DOORS THAT ARE DESIGNATED AS REENTRY ARE TO REMAIN UNLOCKED UNTIL IT IS DETERMINED HOW SYSTEM IS TO BE OPERATED. SEVERAL DOORS THAT WERE LISTED AS NO REENTRY WERE UNLOCKED AND VISE VERSA. ENTIRE STAIRWAYS NEED TO BE EVALUATED ALONG WITH SIGNS TO DETERMINE IF THE CORRECT INFORMATION IS DISPLAYED ON EACH FLOOR. RECOMMEND MANAGEMENT, ENGINEERING, SECURITY AND ACCESS CONTROL COMPANY MEET TO DETERMINE HOW SYSTEM IS PERMITTED AND APPROVED. STEPS NEED TO BE PUT IN PLACE TO TEST CALL BOXES THAT REPORT TO SECURITY ARE WORKING PROPERLY AT ALL TIMES. COMPLIANCE WITHIN 60 CALENDAR DAYS.
4426 | MOBILITY IMPAIRMENT LIST NEEDS TO BE UPDATED EVERY 6 MONTHS. ALL SECTIONS OF THE FIRE DEPOSITORY BOX BOOK NEED TO BE REVIEWED AND UPDATED AS NEEDED. COMPLIANCE WITHIN 60 CALENDAR DAYS.
4427 | PRE ACTION SUPPRESSION SYSTEM LOCATED ON FLOOR # 12 DOES NOT HAVE INSPECTION TAGS IDENTIFYING WHEN THE SYSTEM WAS LAST TESTED. COMPLIANCE WITHIN 60 CALENDAR DAYS.
4428 | HFC 901.6.2-Records Facility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). Certificate of Occupancy: Core of Building C of O only Active Fire Permits: Up to date and Paid. Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation. Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards. Fire Alarm Permit: Sprinkler Percentage Letter and Form: Building System Test Documentation LSB # 2 Electronic Locks-Semi Annual Sprinkler System- Annual Fire Alarm System Test- Annual Fire Extinguishers- Annual Fire Hoses- Annual Fire Pumps Flow Test- Annual Emergency Power & Lighting- Annual Generator Test (ATS) - Annual Fire Alarm Audibility Test- 3 Year Fire Hose Pressure Test- 3 year Fire Dampers- 4 Year Fire Alarm Sensitivity- 5 Year FDC Test (Bldg. & Garage) - 5 Year PRV / PRD Test- 5 Year Stair pressurization Test- 5 Year Standpipe System- 5 Year Water Supply Tank Inspection- 5 Year Boiler- Permit Elevator-Annual Permit Dry Partial or Full Trip Test Gas Test- 5 Year COMPLIANCE WITHIN 60 CALENDAR DAYS.
4429 | LABEL ROOFTOP STANDPIPE TEST CONNECTION. "TEST CONNECTION" COMPLIANCE WITHIN 60 CALENDAR DAYS.
4430 | PERMITS - Permits the Inspector will be looking for are as follows: " Key Box Permit " Flammable and Combustible Permit " Fire Alarm Permit " Elevator Operating Permit " Boiler Permit " Other - Assembly, Access Gates, Batteries, etc. " Certificate of Occupancies " Fire Depository Box / Key Boxes " These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS.
4431 | MECHANICAL ROOMS THROUGHOUT THE BUILDING NEED TO BE EVALUATED FOR FIRE CAULKING WALL PENETRATIONS. STAIR 38 HAS AN OPEN WALL JUNCTION BOX THAT NEEDS TO BE COVERED. COMPLIANCE WITHIN 60 CALENDAR DAYS.
4432 | FIRE COMMAND ROOM APPEARS TO HAVE 2 MANUAL OVERRIDE SWITCHES FOR MAG LOCK RELEASE IN THE STAIRS. ONE LOCATED ON THE ALARM PANEL LABELED STAIR DOOR LOCK RELEASE AND ONE ON THE STAIR PRESSURIZATION PANEL. A DETERMINATION NEEDS TO BE MADE TO SEE IF BOTH ARE FUNCTIONING AND MAKE CLEAR WHICH ONE PROVIDES THIS FUNCTION. STAIR DOORS 40 A, 40 B FAILED TO RELEASE WHEN ALARM PANEL STAIR LOCK RELEASE WAS ACTIVATED. COMPLIANCE WITHIN 60 CALENDAR DAYS.
4433 | NUMEROUS STAIRWAY DOORS THROUGHOUT PARKING GARAGE AND BUILDING DO NOT LATCH COMPLETELY WHEN CLOSED AND NEED TO BE ADJUSTED. GARAGE DOORS 6 A, 8 C, 11 C. FLOORS UNDER CONSTRUCTION HAD STAIRWAY DOOR 30 A, 30 B 29 A, 29 B STAIR DOOR LOCK AND LATCH MECHANISMS REVERSED TO PREVENT DOORS FROM LATCHING. CONSTRUCTION SUPERVISORS NEED TO BE ADVISED THAT THIS IS NOT TO BE DONE AT ANY TIME WHILE BUILDING IS OCCUPIED ON ANY FLOORS. COMPLIANCE WITHIN 60 CALENDAR DAYS.
4434 | ELEVATOR LOBBY EMERGENCY EVACUATION MAPS ARE MISSING ON FLOORS 27 AND 28. COMPLIANCE WITHIN 60 CALENDAR DAYS.
4435 | FIRE FIGHTER COMMUNICATION PHONES FAILED TO SHOW ON THE ALARM PANEL THE FLOOR OF CONNECTION WHEN TESTED. PANEL HAS FLOORS LABELED. CONNECTIONS NEED TO BE CHECKED TO ENSURE INFORMATION IS AVAILABLE ON PANEL. COMPLIANCE WITHIN 60 CALENDAR DAYS.
4436 | NoData
4437 | NoData
4438 | Access gate permit (A4) is expired.
4439 | NoData
4440 | NoData
4441 | Keybox permit (k1) is expired.
4442 | Access gate permit (A4) is expired.
4443 | NoData
4444 | NoData
4445 | NoData
4446 | NEED SERVICE TO FIX RED TAG. 12-11-20 LAST DATE
4447 | NoData
4448 | NoData
4449 | NoData
4450 | COMPLIANCE WITHIN 60 CALENDAR DAYS
4451 | COMPLIANCE WITHIN 60 CALENDAR DAYS.
4452 | COMPLIANCE WITHIN 60 CALENDAR DAYS
4453 | COMPLIANCE WITHIN 60 CALENDAR DAYS.
4454 | COMPLIANCE WITHIN 60 CALENDAR DAYS.
4455 | Fire Fighter phones need to be tested to ensure they are all functioning properly.COMPLIANCE WITHIN 60 CALENDAR DAYS
4456 | COMPLIANCE WITHIN 60 CALENDAR DAYS.
4457 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualFire Extinguishers- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS
4458 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice.COMPLIANCE WITHIN 60 CALENDAR DAYS.
4459 | NoData
4460 | BUSINESS IS TO REPAIR ILLUMINATION LIGHTS NEAR WOMEN'S RESTROOM AREA
4461 | BUSINESS NEEDS SIGN ON OFFICE DOOR STATING ELECTRICAL ROOM OR PANEL
4462 | REPAIR CEILING TILES IN OFFICE
4463 | BUSINESS NEEDS TO APPLY FOR A CANDLE PERMIT IN ORDER TO CONTINUE USE OF STERNO CANDLES
4464 | BUSINESS IS TO APPLY FOR ASSEMBLY PERMIT IMMEDIATELY
4465 | BUSINESS IS TO APPLY FOR ASSEMBLY PERMIT IMMEDIATELY
4466 | BUSINESS MUST DISCONTINUE USE OF POWER STRIP INTO ANOTHER POWER STRIP
4467 | BUSINESS MUST MOVE SNACK STAND FROM BLOCKING EXTINGUISHER
4468 | MUST MOVE ALL COMBUSTIBLES AWAY FROM ELECTRICAL PANEL IN OFFICE
4469 | NoData
4470 | BUSINESS IS TO REPAIR ILLUMINATION LIGHTS NEAR WOMEN'S RESTROOM AREA
4471 | BUSINESS NEEDS SIGN ON OFFICE DOOR STATING ELECTRICAL ROOM OR PANEL
4472 | REPAIR CEILING TILES IN OFFICE
4473 | BUSINESS NEEDS TO APPLY FOR A CANDLE PERMIT IN ORDER TO CONTINUE USE OF STERNO CANDLES
4474 | BUSINESS IS TO APPLY FOR ASSEMBLY PERMIT IMMEDIATELY
4475 | BUSINESS IS TO APPLY FOR ASSEMBLY PERMIT IMMEDIATELY
4476 | BUSINESS MUST DISCONTINUE USE OF POWER STRIP INTO ANOTHER POWER STRIP
4477 | BUSINESS MUST MOVE SNACK STAND FROM BLOCKING EXTINGUISHER
4478 | MUST MOVE ALL COMBUSTIBLES AWAY FROM ELECTRICAL PANEL IN OFFICE
4479 | NoData
4480 | Please renew both your A4 & k1 expired permits.
4481 | NoData
4482 | NoData
4483 | NoData
4484 | NoData
4485 | NoData
4486 | NoData
4487 | NoData
4488 | NoData
4489 | NoData
4490 | NoData
4491 | NoData
4492 | NoData
4493 | NoData
4494 | NoData
4495 | NoData
4496 | NoData
4497 | NoData
4498 | NoData
4499 | Please renew expired permit
4500 | expired Permit
4501 | NoData
4502 | NoData
4503 | NEED SERVICE. HAS TROUBLE SIGNAL. 6-21-19 LAST DATE
4504 | FAILURE TO SERVICE FIRE EXSTINGUISHERS.5-18 LAST DATE
4505 | NoData
4506 | NEED SERVICE. 5-18 LAST DATE
4507 | Propane shall not be used indoors.
4508 | Replace or repair the red tagged fire extinguishers.
4509 | Remove the obstructions placed in front of the exit.
4510 | Have a licensed fire protection inspect and tag the extinguishing systems on the paint booths.
4511 | Secure the compressed gas cylinders.
4512 | Propane shall not be used in buildings.
4513 | Protected propane storage is required.
4514 | Remove propane storage from the building.
4515 | P2 permit is expired. Expired on 12/2/2020. Amount owed for permit 385.38 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
4516 | Please renew expired permits
4517 | NoData
4518 | NEED SERVICE. 3-20 LAST DATE
4519 | YELLOW TAG NEED TO BE FIX AND FIRE EXTINGUISHER NEED SERVICE 8-19 LAST DATE
4520 | NoData
4521 | NEED SERVICE . LAST DATE 6-21-19
4522 | NEED SERVICE . 8-19 LAST DATE
4523 | NoData
4524 | NoData
4525 | NoData
4526 | NoData
4527 | FIRE EXTEINGUISHER NEED SERVICE 4-19 LAST DATE
4528 | NEED SERVICE 4-19 LAST DATE
4529 | NoData
4530 | NoData
4531 | NoData
4532 | NoData
4533 | Amount Due: $533.60
4534 | NoData
4535 | NoData
4536 | NoData
4537 | NoData
4538 | NoData
4539 | NoData
4540 | NoData
4541 | NO VIOLATIONS FOUND AT THIS TIME
4542 | NoData
4543 | Have a licensed fire protection company punch the holes in the dates of service for the fire extinguishers.
4544 | Mount the class K fire extinguisher in the kitchen.
4545 | All liquid-fuel or LP-gas powered operated industrial trucks must be equipped with extinguishers.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4546 | A minimum 4-A:20-BC extinguisher must be located within 20 feet of your battery charging station.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4547 | The owner/occupant shall be held responsiblefor the correction and abatement of all violations listed in this notice ofviolations report. COMPLIANCE: WITHIN 30CALENDAR DAYS.
4548 | NoData
4549 | Extension cords are for day of use only and are not to be used as permanent wiring.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4550 | NoData
4551 | Nothing shall be allowed to be placed near a fire hydrant, FDC, or control valve that would prevent responding fire fighters from immediately recognizing the device and gaining access. A clear space of 3 feet must be maintained and an unobstructed view for approaching apparatus.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4552 | At the time of inspection, approved plans could not be presentedfor inspection by the fire marshal.Approved plans are to be kept on site at all times. If approved plans cannot be located, arequest to the building department may be able to duplicate the original. Approved plans must be submitted to firemarshal or the process for high-piled storage plan submittal process shall berestarted.COMPLIANCE: WITHIN 30CALENDAR DAYS.
4553 | Correctly fill out the HMIS for all hazardousmaterials stored at your facility. Theclassification of the hazardous materials shall comply with the 2012international fire code classifications system.It is highly advisable to seek technicalassistance in correctly completing the HMIS for the hazardous material beingstored at the facility.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
4554 | A permit shall be obtained prior to engaging in any activities, operations, practices, or functions regulated by this code and requiring a permit as listed in section 105.6. It shall be unlawful for any person to engage in any activities, operations, practices or functions without holding a current and valid permit.Issued permits shall always be kept at facility and shall be readily available for inspection by the fire code official.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4555 | Ensure that storage of incompatibles are within the parameters of this code at all times.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4556 | A workingspace (cleared of all combustible material) of not less than 30 inches inwidth, 36 inches in depth and 78 inches in height shall be provided in front ofelectrical service equipment.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
4557 | NoData
4558 | A permit is required to dispense fuel at your facility.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4559 | NoData
4560 | NoData
4561 | NoData
4562 | NoData
4563 | NoData
4564 | Have the required 6 mo. kitchen hood Ansul system inspected and tagged by a certified fire protection company. (scheduled for next week)
4565 | Ensure that floor plans with evacuation routes are posted in all rooms accessed by children throughout the facility. (rooms 4,5,6 and the indoor playground room were not able to be located at the time of inspection)
4566 | NoData
4567 | NoData
4568 | NoData
4569 | NoData
4570 | BLUE TAG ON FIRE ALARM DATED 1/20/21; LAST SENSITIVITY TEST N/A - SYSTEM IS SELF TESTING FIRE ALARM PERMIT HFD20036891 IS CURRENT LAST GAS TEST CONDUCTED 11/20/20 CERTIFICATE OF OCCUPANCY IS POSTED - 155 TOTAL FIRE EXTINGUISHERS TAGGED JUNE 2020 EXIT LIGHTS LAST CHECKED AND ALL OPERABLE IN JANUARY 2021
4571 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
4572 | NoData
4573 | Provide covers for electrical outlets.
4574 | NoData
4575 | NoData
4576 | A Fire Department stand-by may be required if red-tagged system is not serviced in a timely manner.
4577 | Fire alarm system is red tagged and must be serviced within 72 hours
4578 | Failure to service red tagged systems will be subject to citations and re-inspection fees.
4579 | A Fire Department stand-by may be required if red-tagged system is not serviced in a timely manner.
4580 | Fire alarm system is red tagged and must be serviced within 72 hours
4581 | Failure to service red tagged systems will be subject to citations and re-inspection fees.
4582 | NoData
4583 | NoData
4584 | NoData
4585 | NoData
4586 | NoData
4587 | NoData
4588 | NoData
4589 | NoData
4590 | NoData
4591 | 911 Falcon lock requested for the manual slide gate. Assessment of Certificate of Occupancy is pending on property.
4592 | A4 permit required for 2021
4593 | Provide documentation of extinguisher and fire code training.Conducted 1/27/2021
4594 | Update EOP for 20-21 school year.
4595 | NoData
4596 | Repair ASAP.
4597 | D1 permit is expired. Expired on 1/10/2021. Amount owed for permit 266.80 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
4598 | NoData
4599 | COMPLIANCE DATE: 15 CALENDAR DAYS
4600 | K1 permit is expired
4601 | NoData
4602 | NoData
4603 | Repair ASAP.
4604 | REPAIR FIRE ALARM PRIMARY PHONE LINE AS SOON AS POSSIBLE. 72 HOUR NOTICE
4605 | NoData
4606 | 6/2019 - Have all extinguishers inspected9/2020 - OK
4607 | Correct all violations within 30 calendar days.Provide action plan for violations that cannot be corrected by reinspection date listed on Page 1.
4608 | Provide load bank test report for generator.Load bank performed 10/12/2020 - OK
4609 | Document fire code training.Extinguisher training OKFire code training 1/2021 - OK
4610 | Remove potassium hydroxide from wooden shelf and store in corrosives cabinet.
4611 | Remove all multi-outlet extension cords that do not have built-in surge protection, including those supplying power to Promethean boards.Working action plan. Funds for replacement will be available 7/2021.
4612 | Replace missing ceiling tiles in stage dressing room.
4613 | Update evacuation maps and ensure placement in all rooms.
4614 | 4 boilers current, 1 expired. Update and place permit in binder.Boiler inspected 9/2020. Waiting for TDLR to process paperwork for certificate.
4615 | Provide HMIS for chemicals in laboratory storage.
4616 | Repair/replace non-working exit sign in chemistry classroom.
4617 | NoData
4618 | NoData
4619 | M3 permit required
4620 | IT THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
4621 | REPAIR HOLE /OPENING IN THE CEILINGTO PREVENT THE SPREAD OF FIRE.
4622 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES . KEEP UPDATED AND TRAIN QUATERLY.
4623 | Permits Expired 1/16/2021; Unpaid Fees $538.60
4624 | NoData
4625 | NoData
4626 | Provide Annual test documentation.
4627 | Provide Annual test documentation.
4628 | Expired, 10/2018.Only expired fire extinguisher in Mech 107A
4629 | 2 Knox boxes on front and side door, provide door keys. 5 Knox Boxes on gates, provide key for chain.
4630 | Provide Sprinkler Riser Signage
4631 | Reinspection Fee
4632 | Expired, 10/24/2018.
4633 | Provide Gas Test Documentation.
4634 | Provide Annual Elevator Permit.
4635 | Add electronic lock override switch to the fire alarm panel per above code and chapter 4 of the building code. Compliance in 60 days.
4636 | Remove items stored in front of breaker box on floor eleven HFC227 clean agent room per above code. Compliance in 60 days.
4637 | Information
4638 | Add swipe cards to all 5 key sets per above code. Compliance in 60 days.
4639 | Add 1 elevator hoistway key to the fire depository box making a total of 2 per above code. Compliance in 60 days.
4640 | Remove plastic cart being stored in the 402A electric room per above code. Compliance in 60 days.
4641 | HFC 901.6.2-Records Facility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). Certificate of Occupancy: Core of Building C of O only Active Fire Permits: Up to date and Paid. Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation. Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards. Fire Alarm Permit: Sprinkler Percentage Letter and Form: Building System Test Documentation LSB # 2 Electronic Locks-Semi Annual Sprinkler System- Annual Fire Alarm System Test- Annual Fire Extinguishers- Annual Fire Hoses- Annual Fire Pumps Flow Test- Annual Emergency Power & Lighting- Annual Generator Test (ATS) - Annual Fire Alarm Audibility Test- 3 Year Fire Hose Pressure Test- 3 year Fire Dampers- 4 Year Fire Alarm Sensitivity- 5 Year FDC Test (Bldg. & Garage) - 5 Year PRV / PRD Test- 5 Year Stair pressurization Test- 5 Year Standpipe System- 5 Year Water Supply Tank Inspection- 5 Year Boiler- Permit Elevator-Annual Permit Dry Partial or Full Trip Test Gas Test- 5 Year Provide compliance letter for Clean agent system on level 11. Provide compliance letter for pre-action systems on levels 15 and 12. COMPLIANCE WITHIN 60 CALENDAR DAYS.
4642 | The JLL generator room is over MAQ for diesel fuel. Provide approved plans showing approval for the quantity of diesel fuel being stored in that control area. If unable to show approval for the quantity of fuel, have the room re- permitted under the 2012 code. Compliance in 60 days.
4643 | Update elevator machine room sign on roof that has become un readable. Compliance in 60 days.
4644 | Label test connection on roof per above code. Compliance in 60 days.
4645 | Add signage to roof level stair C on the roof side per above code. Compliance in 60 days.
4646 | Information.
4647 | Update mobility impaired every 6 months per above code. Compliance in 60 days.
4648 | Update level 16 and 15 stairway sigange per above code and appendix H. Level 15 signage needs to be for re-entry stair A, B and C. Level 16 needs to instruct re-entry on level 15. Evaluate levels 10 through 16 for proper re-entry information and make changes in accordance with appendix H. Send sign layout to inspector for approval prior to printing. Compliance in 60 days.
4649 | Have clean agent system on level 11 tested per above code. Compliance in 60 days.
4650 | Add elevator pictorial to roof level service elevator lobby per above code. Compliance in 60 days.
4651 | Return the following areas to their designed fire resistance rating per above code. Go through all mechanical and electrical rooms and make corrections as needed. Locations noted during inspection. Level 15 south electrical and mechanical. Level 15 pre-action room. Level 14 south electrical and mechanical Level 13 electrical room. Level 13 central electric room, sheet rock. Fire pump room. Compliance in 60 days.
4652 | PERMITS - Permits the Inspector will be looking for are as follows: " Key Box Permit " Flammable and Combustible Permit " Fire Alarm Permit " Elevator Operating Permit " Boiler Permit " Other - Assembly, Access Gates, Batteries, etc. " Certificate of Occupancies " Fire Depository Box / Key Boxes " These are some but not all of the Permits available. " Present Permits that apply to facility Address listed " on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS.
4653 | Information
4654 | Remove the sign on level 13 stair A stating stop not an exit. Compliance gained during inspection.
4655 | NoData
4656 | NoData
4657 | NoData
4658 | NoData
4659 | NoData
4660 | C1 permit is expired. Expired on 12/11/2020. Amount owed for permit 177.85 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
4661 | All fire extinguishers must be mounted.
4662 | Fire extinguishers must be minimum rating of 2A10BC
4663 | Place fire extinguisher with a minimum rating of 2A 10BC
4664 | Remove structure blocking emergency exit.
4665 | NoData
4666 | Cover all exposed wires and replace missing junction covers.
4667 | Place fire extinguishers in a visible location.
4668 | Apply for certificate of occupancy.
4669 | NoData
4670 | NoData
4671 | NoData
4672 | Place fire extinguishers with a rating of 4A 40B.C
4673 | Remove accumulation of dust.
4674 | Apply for a certificate of occupancy at 1002 Washington ave. Telephone # 832-394-8880.
4675 | NoData
4676 | Have the required 2 year gas test performed and retain the approved permit on site, as set forth by state requirements for day cares. (the last gas test was noted as 3/1/2018)
4677 | All violations listed in this report must be corrected within 30 DAYS in order to avoid citations and re-inspection fees.
4678 | On 6/12/2020 the fire alarm was yellow tagged for deficiencies. Have a certified fire alarm company correct all deficiencies to bring the system back into full operation with no impairments within 30 DAYS, ensuring that a correction tag is placed once repairs are complete.
4679 | NoData
4680 | ALL WINDOWS NEEDED FOR SECONDARY EGRESS MUST BE PROPERLY MAINTAINED AND OPERATE IN A NORMAL MANOR.
4681 | ITS THE OWNER/AGENT RESPONSIBILITY ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
4682 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES. KEEP UPDATED AND TRAIN QUARTERLY.
4683 | GAS LINE/PIPE PRESSURE TEST MUST BE PERFORMED EVERY 5 YEARS TO CHECK FOR LEAKS.
4684 | NoData
4685 | NoData
4686 | All emergency door exits need illuminated exit signs, with emergency lighting installed.
4687 | No tag for annual inspection and yellow tagged corrected.
4688 | Need to find if both panels are connected and if so correct the Audibility failure.
4689 | Need annual test for emergency lights.
4690 | Remove all storage that is keep in classroom and exit pathway clear of any obstructions.
4691 | Needs updated tags for testing.
4692 | Tag shows yellow tagged with blue tag. Confusing tags need to be updated.
4693 | Door must open in the direction of travel.
4694 | The exterior gate needs to open in direction of travel and panic hardware installed.
4695 | All interior exit emergency exit doors in older wing and exterior gate need panic hardware installed
4696 | All doors with black mesh need to be removed.
4697 | Needs to be removed and panic hardware installed.
4698 | All exit obstructions need to be cleared and the exterior gate needs to open in direction of travel and panic hardware installed.
4699 | Egress light test OK
4700 | Compliance required within 30 calendar days.
4701 | Last sensitivity 3/17/15 - OK
4702 | Due. Have FACP inspected.
4703 | 7/31/19 - Yellow Corrected 8/10/19 - OK
4704 | Last hydro 9/11/19 - OK
4705 | Instal FDC sign with arrow on awning support.
4706 | Last inspection 8/2019 - OK
4707 | Have dampers tested and correct any deficiencies.
4708 | Maps OK
4709 | Drill log OK.
4710 | Last gas test 5/30/19 - OK
4711 | Due. Have audibility performed.
4712 | NoData
4713 | Last inspected January 31, 2020. Not in violation at time of inspection, but must be inspected prior to February 1st, 2021.
4714 | It is the owner/occupants responsibility to maintain all permits and inspections. I did not find any fire code violations during this inspection.
4715 | Fire alarm inspection company did not list the last smoke detector sensitivity test. Next Fire Alarm Inspection, have the company perform smoke detector sensitivity test unless correct documentation can be presented.
4716 | Please renew the expired key box permit from 11/07/2019.
4717 | NoData
4718 | NoData
4719 | Please renew your expired key box (k1) permit from 02/06/2020.
4720 | Please renew your expired key box (k1) permit. Permit expired on 01/08/2021. Also make sure your access gate (a4) permit is paid because that permit expires on 01/30/2021.
4721 | NoData
4722 | Multiplug adapters (power strips) must be plugged directly into outlet, no daisy-chaining allowed
4723 | 36" clearance in front of electrical panels and around transformer must be maintained
4724 | Re-inspection applied for failure to make corrections after extended timeframe, follow-up required
4725 | NoData
4726 | Door to Electrical room must be labeled
4727 | Please renew the expired Access Gate (a4) that expired on 07/02/2019.
4728 | Informational regarding exits and exit lighting, see 2.4.2.4
4729 | Please fix all broken signs in building
4730 | All fire doors in building must have the ball detent system allowing door to remain open removed. Fire doors are to remain closed at all times, NO HOLD OPEN DEVICES ALLOWED.
4731 | All interior fire doors must be labeled both sides.FIRE DOOR - KEEP CLOSED
4732 | NoData
4733 | Fire alarm panel requires annual test. Last test date 2013
4734 | Test report of exit signs and exit lighting required
4735 | A number of exit signs in the building do not have a backup power source (battery) to maintain required illumination during power outage. Replace any signs not meeting specifications. Specifically found signs near units 382, 409, 411, 412, and 432. The given list is not exhaustive, all signs must be checked to ensure capability to remain lit. Also found a number of exit signs to be very weak or not working when testing. This will be addressed with required report. See 2.4.2.41/29/21 - light above A-395 not working
4736 | Informational regarding exits and exit lighting, see 2.4.2.4
4737 | NoData
4738 | Test report of exits signs and exit lighting required
4739 | Please ensure all exit signs and lighting meet code
4740 | Exit directional arrow missing @ C-141
4741 | Informational regarding exits and exit lighting, see 2.4.2.4
4742 | Directional arrows missing from exit signs. Intermediary exit signs must point in the direction(s) of nearest exit(s).
4743 | NoData
4744 | Test report of exit signs and exit lighting required
4745 | Please ensure all exit signs and lighting meet code
4746 | Ensure all fire extinguishers have a annual acceptable service tag from a licensed fire protection company.
4747 | This location is required to have one (1) fire extinguisher with a minimum rating of 2:A 10:BC. The extinguisher should be mounted with the top being no higher than 5 feet off the ground, the bottom at least 4 inches off the ground, and positioned in such a way that it is easily accessible, readily visible, and not subject to damage. No point inside the occupancy should be greater than 75 feet from an extinguisher.
4748 | Provide address numbers on the front of the exterior of the building that at a minimum of 4 inches tall, 0.5 inches wide in stroke width, easily visible from the street, and that contrast in color with their background.
4749 | Systems or devices that are permanently out of service or any non-required life safety system or fire protection system that no longer functions as originally installed shall be removed or the appearance changed so as not to be mistaken for functioning life safety or fire protection equipment.
4750 | Ensure all exit signs are properly illuminated under battery back up power.
4751 | NoData
4752 | Please renew expired key box permit from 05/04/2019
4753 | All exits shall remain free from obstructions blocking a clear path to egress. Remove all objects blocking all exits and fire department equipment.Immediate compliance required.
4754 | Permit Expired 12/14/2020; Unpaid Fees $266.80
4755 | Provide a knox box mounted to the pole near your access gate like the your approved plans show with the keys to the facility in the box. Compliance by 3-5-2021
4756 | All doors leading into your high piled storage area shall have locks that are keyed the same. Repair all doors that will not open or the lock is malfunctioning. Compliance by 3-5-2021
4757 | Provide at least a 3ft. clearance around all electrical equipment.Compliance by 3-5-2021
4758 | Replace all missing or damaged ceiling tiles on the second floor and throughout the facility.Compliance by 3-5-2021
4759 | Have qualified fire door company perform annual drop test on all fire doors.Compliance by 3-5-2021
4760 | Have qualified fire sprinkler/ alarm company address all yellow tag issues and bring both systems into compliance.Have sprinkler company add the correct information on your hydraulic plates per NFPA 13 Figure A 24.5. (Info provided)Compliance by 3-5-2021
4761 | Have qualified fire extinguisher company mount extinguishers on all forklifts powered by fuel or propane and perform annual testing then appropriate tags.Have this company address your fire hose cabinets and service or remove.Compliance by 3-5-2021
4762 | All fire extinguishers shall be mounted from the hardware provide and not on floors or tables.Compliance by 3-5-2021
4763 | After bringing your warehouse back into compliance per your approved high piled plans, make sure that there are no dead end aisles.Compliance by 3-5-2021
4764 | Repair or replace all emergency lighting not working or broken in your facility and provide documentation that they are working at that time.Compliance by 3-5-2021
4765 | All doors leading into your high piled area shall have the letters HFD on the upper left hand corner on the outside of the doors per your approved plans.Compliance by 3-5-2021
4766 | Provide documentation from an approved alarm company that your large fans in your warehouse are wired to the fire alarm panel and will automatically shut off when the system goes into alarm.Compliance by 3-5-2021
4767 | Review your approved high piled floor plans and bring the warehouse back to the approved floor layout with aisle spacing.Compliance by 3-5-2021
4768 | Apply for a Lp-gas permit for the propane that you store on site. You can get this application on the City of Houston web page under fire permits.Compliance by 3-5-2021
4769 | All exits lights shall be illuminated.Compliance by 3-5-2021
4770 | NoData
4771 | NoData
4772 | Appropriately spaced extinguishers required around outside of building. The larger building requires the following:1) Minimum of one extinguisher each on N and South sides2) Minimum of two extinguishers each on W and E sidesThe smaller building requires the following:1) Minimum of one extinguisher each on N and South sides2) Minimum of one extinguisher each on W and E sides
4773 | NoData
4774 | Building identification needs to be clearly marked on at least two sides - 1) End of building (North side) and 2) Road facing (West side)
4775 | Lock on failsafe box for automatic gate entrance not in compliance with a4 permit. Key for failsafe lock must be located in main gate keybox. Fire marshal must install this key - not accessible by client
4776 | NoData
4777 | Appropriately spaced extinguishers required around outside of building. The larger building requires the following:1) Minimum of one extinguisher each on N and South sides2) Minimum of two extinguishers each on W and E sidesThe smaller building requires the following:1) Minimum of one extinguisher each on N and South sides2) Minimum of one extinguisher each on W and E sides
4778 | NoData
4779 | Building identification needs to be clearly marked on at least two sides - 1) End of building (North side) and 2) Road facing (West side)
4780 | Lock on failsafe box for automatic gate entrance not in compliance with a4 permit. Key for failsafe lock must be located in main gate keybox. Fire marshal must install this key - not accessible by client
4781 | NoData
4782 | NoData
4783 | NoData
4784 | Compliance: 30 calendar days.
4785 | NoData
4786 | NoData
4787 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
4788 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES. KEEP UPDATED AND TRAIN QUARTERY.
4789 | NoData
4790 | NoData
4791 | NoData
4792 | The owner/occupant shall be held responsible for the correction and abatement of all violations listed in this notice of violations report. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4793 | HIGH-PILEDCOMBUSTIBLE STORAGE. Storage of combustible materials in closelypacked piles or combustible materials on pallets, in racks or on shelves wherethe top of storage is greater than 12 feet (3658 mm) in height. When requiredby the fire code official, high-piled combustible storage alsoincludes certain high-hazard commodities, such as rubber tires. Group Aplastics, flammable liquids, idle pallets and similar commodities, where thetop of storage is greater than 6 feet (1829 mm) in height.Lower any high-hazard combustibles to below 6 feet in height.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4794 | Using the format provided, a currentHMIS statement shall be submitted to the hazmat/high-piled 180 team forreview to assure you are within the MAQ's.Correctly fill out a new HMIS for allhazardous materials stored at your facility.The classification ofthe hazardous materials shall comply with the 2012 international fire codeclassifications system.It is highly advisable to seektechnical assistance in correctly completing the HMIS for the hazardousmaterial being stored at the facility.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
4795 | NoData
4796 | NoData
4797 | Make all code violation corrections prior to the re-inspection date noted on page 1 of the report.
4798 | Provide documentation for a 3yr Audibility test. Must have one of two things to be acceptable and the Documentation should contain Company’s ACR#, Tester’s FAL#, and date. A) Must show each audibility device’s ambient decibel level and the decibel level when the device is active. The difference in DB level must fall within NFPA 72’s acceptable range for the device to pass the test. OR B) A document from their company on company’s letter head that has the following information – 1) Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all audibility devices passed the audibility test as required by NFPA 72.
4799 | Fire Rated Caulk needed in the following areas:1. Rectangular opening in the wall near the riser, above the chiller.2. Hole above AHU-3 / small breaker box near LGXFMR-7LK (Large Breaker Box)
4800 | If the system is an addressable / Intelligent system - provide the digital diagnostic reading showing the detectors status. If the system is conventional - test each device with synthetic smoke and provide documentation. The documentation is required to show: 1)Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all smoke detector devices passed the sensitivity test as required by NFPA 72.
4801 | Apply for a Key Box Permit.
4802 | Have intercom system tested and place report in binder.
4803 | Provide instructions for fire alarm and intercom operation. Instructions must be located at the respective systems.
4804 | Audibility test due. Have test performed.
4805 | Log not current. Update log and place in FMB.
4806 | Last inspection 12/2018 - OK
4807 | At least one half of documented fire drills are notated "Obstructed." - OK
4808 | Training log not current. Update log and place in FMB.
4809 | Add "Roof Access" signs on doors to all mechanical rooms that contain roof access ladders.
4810 | Add sign with an arrow near awning that indicates FDC location.
4811 | Last inspection 8/2018 - Blue, OK
4812 | Last inspection 7/2018 - Yellow HAVE YELLOW TAG CONDITIONS CORRECTED
4813 | No record of fire damper tests. Have dampers tested and place report in FMB.
4814 | Evacuation maps must be specific to each room. Update maps using only two colors or two line patterns (solid vs. broken) to indicate primary and secondary exits.
4815 | Log does not show fire drills for April or May. Update log in FMB.
4816 | Remove all combustible items from mechanical rooms.
4817 | Reference.
4818 | Last sensitivity test 3/17/15 - OK
4819 | Last inspection 8/2018 - OK
4820 | Provide copy of emergency evacuation plan for inspector to review. Plan should include (at minimum) occupant notification procedure, evacuation procedure, refuge areas, and method for verifying that all occupants have exited the building.
4821 | 5 year hydrostatic test is past due. Have hydro performed. Replace missing FDC caps. FDC couplings are stiff and need to be maintained.
4822 | Multiple egress lighting failures. Have all emergency lights tested and correct all deficiencies. Place annual 90 minutes test log in Fire Marshal binder. Place quarterly in-house inspection log in Fire Marshal binder.
4823 | Compliance required within 60 calendar days. Update fire marshal binder (FMB), and use packet provided by inspector as a guide for required documentation.
4824 | Gas test pending. Provide documentation once test is complete.
4825 | Remove slide bolt from walk-in freezer door. Prohibit installation of any lock/latch that could prevent door from being opened from inside the freezer.
4826 | NoData
4827 | NoData
4828 | NoData
4829 | Please renew Public Assembly Permit within 10 Business days.
4830 | NoData
4831 | Please Apply for New Public Assembly Permit within 10 Business days.
4832 | NoData
4833 | NoData
4834 | NoData
4835 | NoData
4836 | NoData
4837 | NoData
4838 | NoData
4839 | NoData
4840 | NoData
4841 | NoData
4842 | NoData
4843 | NoData
4844 | RESOLVE YELLOW TAG ISSUE ON RISER #1
4845 | HAVE AN APPROVED LICENSED MASTER ELECTRICIAN OR LICENSED ELECTRICALSERVICECOMPANY SHALL TEST ALL EMERGENCY LIGHTING SYSTEMS ANNUALLY...STROBE LIGHT AT THE END OF ASILE 2-2 BJCOMPLIANCE WITHIN 30 DAYS
4846 | THE ROLLING FIRE DOORS SHALL BE ANNUALLY INSPECTED BY A LICENSED FIRE PROTECTION COMPANY TO ENSURE PROPER OPERATION IN THE EVENT OF EMERGENCY COMPLIANCE WITHIN 30 DAYS
4847 | ALL ACCESS DOORS SHELL DO KEYED TO THE KEY THAT WILL BE STORED IN THE 911 KEY BOXCOMPLIANCE WITHIN 30 DAYS
4848 | NoData
4849 | NoData
4850 | NoData
4851 | NoData
4852 | NoData
4853 | No violations found at this time.
4854 | NoData
4855 | NoData
4856 | NoData
4857 | NoData
4858 | NoData
4859 | NoData
4860 | NoData
4861 | NoData
4862 | NoData
4863 | NoData
4864 | NoData
4865 | NoData
4866 | NoData
4867 | NoData
4868 | NoData
4869 | NoData
4870 | NoData
4871 | NoData
4872 | NoData
4873 | NoData
4874 | NoData
4875 | MAKE SURE ALL PORTABLE FIRE EXTINGUISHERS HAVE A CURRENT INSPECTION TAG ON THEM AND HUNG ON A BRACKET
4876 | MAKE SURE ALL PORTABLE FIRE EXTINGUISHERS HAVE A CURRENT INSPECTION TAG ON THEM AND HUNG ON A BRACKET
4877 | MAKE SURE BOTH THE LEFT AND RIGHT SIDE EXIT DOORS REMAIN UNLOCKED DURING BUSINESS HOURS
4878 | INSTATLL SPACERS IN THE OPEN GAPS OF THE ELECTRICAL PANEL
4879 | HAVE ALL PORTABLE FIRE EXTINGUISHERS SERVICED AND TAGGED
4880 | REMOVE GAMING MACHINES FROM IN FRONT OF SECONDARY EXIT DOOR AND KEEP SECONDARY EXIT DOOR UNLOCKED DURING BUSINESS HOURS REMOVE TABLE FROM IN FRONT OF MAIN ENTRANCE/EXIT DOOR AND KEEP BOTH THE LEFT AND RIGHT SIDE EXIT DOOR UNLOCKED DURING BUSINESS HOURS
4881 | REMOVE GAMING MACHINES FROM IN FRONT OF SECONDARY EXIT DOOR AND KEEP SECONDARY EXIT DOOR UNLOCKED DURING BUSINESS HOURS REMOVE TABLE FROM IN FRONT OF MAIN ENTRANCE/EXIT DOOR AND KEEP BOTH THE LEFT AND RIGHT SIDE EXIT DOOR UNLOCKED DURING BUSINESS HOURS
4882 | MAKE SURE THE KITCHEN SUPRRESSION SYSTEM IS SERVICED AND INSPECTED EVERY 6 MONTHS
4883 | LABEL THE STORAGE ROOM WITH THE ELECTRICAL PANEL IN IT "ELECTRICAL PANELS INSIDE"
4884 | NoData
4885 | NoData
4886 | NoData
4887 | NoData
4888 | NoData
4889 | NoData
4890 | NoData
4891 | NoData
4892 | NoData
4893 | NoData
4894 | NoData
4895 | NoData
4896 | NoData
4897 | NoData
4898 | NoData
4899 | NoData
4900 | NoData
4901 | NoData
4902 | NoData
4903 | NoData
4904 | NoData
4905 | NoData
4906 | NoData
4907 | NoData
4908 | FIRE ALARM SYSTEM IS NOT IN OPERATION AND REQUIRES REPAIR.ALL VIOLATIONS HAVE BEEN CORRECTED.
4909 | SPRINKLER SYSTEM HAS BEEN YELLOW TAGGED AND REQUIRES ANNUAL INSPECTION.ANSUL SYSTEM HAS BEEN RED TAGGED DUE TO INPROPER COVERAGE. ALL VIOLATIONS HAVE BEEN CORRECTED.ALL VIOLATIONS HAVE BEEN CORRECTED.
4910 | SPRINKLER SYSTEM HAS BEEN YELLOW TAGGED AND REQUIRES ANNUAL INSPECTION.ANSUL SYSTEM HAS BEEN RED TAGGED DUE TO INPROPER COVERAGE. ALL VIOLATIONS HAVE BEEN CORRECTED.ALL VIOLATIONS HAVE BEEN CORRECTED.ALL VIOLATIONS HAVE BEEN CORRECTED.
4911 | NoData
4912 | NoData
4913 | NoData
4914 | NoData
4915 | NoData
4916 | Permits failed to be renewed
4917 | HAVE FIRE ALARM PANEL INSPECTED AND TAGGED BY A LICENSED FIRE PROTECTION EQUIPMENT COMPANY.
4918 | HAVE SPRINKLER SYSTEM INSPECTED AND TAGGED BY A LICENSED FIRE PROTECTION EQUIPMENT COMPANY.
4919 | ADD NO SMOKING SIGNS TO FRONT ENTRANCE.
4920 | POST ALL PERMITS IN A LOCATION THAT IS READILY AVAILABLE FOR INSPECTION.
4921 | RENEW FIRE ALARM PERMIT.RENEW BOILER PERMIT.
4922 | APPLY FOR A NAME CHANGE ON CERTIFICATE OF OCCUPANCY.
4923 | POST OCCUPANT LOAD NEAR MAIN EXIT.
4924 | NoData
4925 | NoData
4926 | NoData
4927 | You can use any of the listed exit signs of the fire code, as long as they are illuminated at all times, but they must be UL924 rated.
4928 | Remove the items blocking the exit door on the north side of the factory floor.
4929 | Owner/occupant is responsible for correcting all fire code violations and obtaining any necessary Certificates. The owner/occupant must obtain a Certificate of Occupancy through the Building Department located at 1002 Washington Avenue. Phone number for Occupancy is 832-394-8800. Phone number for Houston Permitting Center is 832-394-9000.
4930 | Must place address numbers to the front of the business that are minimum 4 inches tall and at least a 1/2 inch wide numbers.
4931 | Replace missing switch plate. Place cover on the electrical panel and cover open breakers with metal or plastic spacers.
4932 | Move portable fire extinguishers that are being obstructed or move the obstruction.
4933 | Place "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED" on this inside of the door. This reminds the employees to unlock the doors when the building is occupied.
4934 | Must be internally or externally illuminated.
4935 | NoData
4936 | #NAME?
4937 | #NAME?
4938 | #NAME?
4939 | #NAME?
4940 | NoData
4941 | NoData
4942 | NoData
4943 | NoData
4944 | Annual Fire Alarm Test was done January 2020. Recent one is required
4945 | NoData
4946 | NoData
4947 | NoData
4948 | NoData
4949 | I arrived on location and spoke Building Manager Liane Guillemette about citizens complaints of nonfunctioning elevators in Building H. Ms. Liane stated that no one notified her of problems with the elevators. Ms. Liane provide supporting documentation of an annual inspection performed on 10/1/2020. Ms.Liane also provide documentation of repairs performed in December and January. Ms. Liane was educated on the management responsibility to maintain the elevators in operable condition at all times. Complaint was also forwarded to the building dept. Inspector Hopkins. I arrived on location and spoke Building Manager Liane Guillemette about citizens complaints of nonfunctioning elevators in Building H. Ms. Liane stated that no one notified her of problems with the elevators. Ms. Liane provided supporting documentation of an annual inspection performed on 10/1/2020. Ms.Liane also provided documentation of repairs performed in December and January. Ms. Liane was educated of the management responsibility to maintain the elevators in operable condition at all times. Complaint was also forwarded to the building dept.
4950 | EXIT gate's micro switch does not open the gate as required.
4951 | Fail safe lock and manual gate lock keys are not in the 911 lock box.
4952 | HFD Hydrant Signs missing on Entrance and Exit Gate
4953 | Complete a natural gas testObtain a permit for a natural gas test from the Houston Permitting Center.
4954 | Fire Extinguishers are out of date.
4955 | Have a licensed fire protection company repair the red tagged alarm panel and correct any deficiencies.
4956 | NoData
4957 | Nonrequired fire protection systems shall be maintained or removed.
4958 | The exceptions listed in the IFC2012.903.2 must be met in order to be considered nonrequired.
4959 | NoData
4960 | The exit door in "Classroom B" does not open freely. Make the appropriate adjustments so that the door opens with a force of less than 15 pounds.
4961 | The vent hood in this occupancy is required to be inspected/serviced every 6 months. Have the vent inspected/serviced and ensure a current service tag is attached.
4962 | Throughout the occupancy are many single station battery operated smoke detectors/alarms. Replace the batteries in any smoke detectors that do not go into alarm when tested, or remove the smoke detector from the occupancy as the occupancy is protected by fire alarm system. Repair or replace any CO detectors found to the inoperable.
4963 | NoData
4964 | NoData
4965 | NoData
4966 | NoData
4967 | NoData
4968 | Renew the expired permit.
4969 | Post the occupant load.
4970 | Repair the broken exit sign located above the side exit. Ensure the emergency lighting is functioning properly.
4971 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
4972 | NoData
4973 | NoData
4974 | NoData
4975 | NoData
4976 | NoData
4977 | NoData
4978 | NoData
4979 | NoData
4980 | NoData
4981 | NoData
4982 | Repair the inoperable emergency illumination on the exit signs.
4983 | Renew the assembly permit.
4984 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
4985 | #NAME?
4986 | - PROVIDE FIRE ALRM AUDIBILTY TEST AND SMOKE SENSITIVITY TEST - AUDIBILITY TEST (EVERY 3 YEARS) - SENSITIVITY TEST (EVERY 2 YEARS)
4987 | Fire extinguishers need to have their annual inspection
4988 | NoData
4989 | NoData
4990 | NoData
4991 | NoData
4992 | NoData
4993 | Repair the hardware on the rear exit door that requires excessive force to open.
4994 | Ensure the rear exit is maintained clear of storage.
4995 | Replace the ceiling tiles after the roof is repaired.
4996 | Test emergency illumination and provide documentation of test.
4997 | Clear and maintain space in front of breaker panels.
4998 | Micro switch malfunction, repair or replace.
4999 | THE FIREALARM PERMIT WAS ISSUED 2/11/19 AND IS EXPIRED; THIS PERMIT MUST BE RENEWED ANNUALLY
5000 | Provide address numbers on the front of the business.
5001 | Remove obstructions in front of the class K fire extinguisher located in the kitchen.
5002 | LIGHT COVERS, BULB COVERS OR CAGES ARE NECESSARY IN ALL LIGHT FIXTURES IN CHILD CARE AREAS AND WHERE ACCIDENTAL DAMAGE OR BREAKAGE MAY OCCUR
5003 | ALL EMERGENCY EXIT SIGNS ARE ILLUMINATED, TESTED AND WORKING THERE IS A STRONG SMELL OF SEWAGE AND SOILED CARPET AT THE ENTRANCE OF THE BUILDING; IT APPEARS RAW SEWAGE IS COMIING IN FROM THE RESTAURANT NEXT DOOR; INVESTIGATE PROBLEM WITH THE OWNER OF THE STRIP CENTER AND ENSURE THIS PROBLEM IS CORRECTED IMMEDIATELY
5004 | THE ALARM SYSTEM IS BLUE TAGGED - TAGS WAS ISSUED 1/23/20 (PAST DUE FOR INSPECTION) AND SYSTEM MUST BE INSPECTED IMMEDIATELY
5005 | FIRE DRILLS MUST BE CONDUCTED MONTHLY
5006 | PROVIDE EVIDENCE OF MONTHLY FIRE DRILLS – KEEP THESE RECORDS ON SITE FOR ATLEAST 3 YEARS ENSURE FIRE DRILLS ARECONDUCTED MONTHLY, WITHOUT FAIL
5007 | NoData
5008 | THE FIRE EXTINGUISHERS ARE TAGGED/INSPECTED NOVEMBER 2019 AND ARE ALL PAT DUE - INSPECT AND TAG ALL EXTINGUISHERS IMMEDIATELY
5009 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THEPROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THEPREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEALALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURINGSUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIREDPRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THEFIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THATARE AN IMMEDIATE LIFE SAFETY HAZARD
5010 | THE CERTIFICATE OF OCCUPANCY AND ALLREQUIRED PERMITS ARE POSTED CONSPICUOUSLY
5011 | Arrived on scene to find the fire alarm and sprinkler system red tagged as of January 2021.I issued 72 hours Notice to have both fire systems returned to compliance or to provide a plan of action. I notified management to initiate a 24 hours fire watch of the entire complex until the fire systems are returned to compliance status.
5012 | NoData
5013 | NoData
5014 | NoData
5015 | NoData
5016 | NoData
5017 | NoData
5018 | NoData
5019 | NoData
5020 | NoData
5021 | - NO VIOLATIONS NOTED - PAPERWORK HANGING FROM ACOUSTICAL CEILING TILE (REMOVED WHILE ON LOCATION)
5022 | HAVE RISER # 3 TESTED TO ADDRESS THE YELLOW TAG. COMPLIANCE WITHIN 30 DAYS.
5023 | NoData
5024 | NoData
5025 | Compliance: 30 calendar days.
5026 | Compliance: 30 calendar days.
5027 | NoData
5028 | NoData
5029 | NoData
5030 | NoData
5031 | NoData
5032 | NoData
5033 | NoData
5034 | NoData
5035 | FIRE ALARM PANEL YELLOW TAGGED BRING UP TO CODE
5036 | FIRE ALARM PANEL YELLOW TAGGED
5037 | ANSUL SYSTEM NEEDS SEMI-ANNUAL INSPECTION
5038 | FIRE ALARM PERMIT NEEDS TO BE UPDATEDEXPIRED 10-27-2020
5039 | NoData
5040 | BOTH SYSTEMS YELLOW TAGGED BRING UP TO CODE
5041 | FIRE ALARM YELLOW TAGGED
5042 | SPRINKLER SYSTEM YELLOW TAGGED
5043 | NoData
5044 | NoData
5045 | GROUP I OR R OCCUPANCIES LOCATED IN A BUILDING CONTAINING A FUEL-BURNING APPLIANCE OR IN A BUILDING WHICH HAS AN ATTACHED GARAGE SHALL BE EQUIPPED WITH SINGLE-STATION CARBON MONOXIDE ALARMS. THE CARBON MONOXIDE ALARMS SHALL BE LISTED AS COMPLYING WITH UL 2034 AND BE INSTALLED AND MAINTAINED IN ACCORDANCE WITH NFPA 720 AND THE MANUFACTURE'S INSTRUCTION.CARBON MONOXIDE DETECTOR SHALL BE PLACED IN THE VICINITY OF THE FUEL-BURNING APPLIANCE (WATER HEATER).COMPLIANCE: WITHIN 30 CALENDAR DAYS.
5046 | PORTABLE FIRE EXTINGUISHER SHALL BE MAINTAINED IN A FULLY CHARGED AND OPERABLE CONDITION.PORTABLE FIRE EXTINGUISHER SHALL BE SERVICED BY QUALIFIED PERSONNEL IN ACCORDANCE WITH LSB STANDARD 02 AND AS REQUIRED BY NFPA 10.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
5047 | CORRECTION AND ABATEMENT OF VIOLATIONS OF THIS CODE SHALL BE THE RESPONSIBILITY OF THE OWNER.GENERAL INFORMATION: THREE JUVENILES CURRENTLY RESIDING IN RESIDENCE (12, 13 AND 16 YEARS OF AGE).COMPLIANCE: WITHIN 30 CALENDAR DAYS.
5048 | THE DISCONNECTING MEANS FOR EACH SERVICE, FEEDER OR BRANCH CIRCUIT ORIGINATING ON A SWITCHBOARD OR PANELBOARD SHALL BE LEGIBLY AND DURABLY MARKED TO INDICATE ITS PURPOSE.ALL BREAKER SWITCHES IN ELECTRICAL PANEL SHALL BE LABELED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
5049 | NoData
5050 | 24" clearance must be maintained between ceiling and combustible materials
5051 | 2 multiplugs need to be removed. Only UL listed resettable multiplug adapters are allowed in businesses
5052 | 2 multiplugs need to be removed. Only UL listed resettable multiplug adapters are allowed in businesses
5053 | Missing spacer in one electrical panel
5054 | Signs need repair for non-working lights when tested
5055 | NoData
5056 | NoData
5057 | NoData
5058 | NoData
5059 | NoData
5060 | NoData
5061 | NoData
5062 | All fire protection systems installed must be maintained in operational readiness condition. Have all deficiencies repaired within 30 calendar days.
5063 | For Reference
5064 | NoData
5065 | NoData
5066 | NoData
5067 | NoData
5068 | LAST INSPECTION ON SPRINKLER RISER 2-2018 SPRINKLER RISER YELLOW TAGGED BRING UP TO CODE
5069 | SPRINKLER RISER YELLOW TAGGED VALVE #2 LEAKING BRING UP TO CODE
5070 | NoData
5071 | EXPIRED P2 PERMIT
5072 | 1/6/2021 - Blue, OK
5073 | 12/13/2019 - OK
5074 | 10/2020 - OK
5075 | 5/15/2019 - OK
5076 | Obstructed drills OK
5077 | Drills conducted monthly - Log OK
5078 | 1/6/2021 - OK
5079 | 5/2019 - Have all portable fire extinguishers inspected.
5080 | Correct all violations within 60 calendar days.
5081 | 2/9/2018 - YellowHave sprinkler systems (main building and gym) inspected and have all deficiencies corrected.Deficiency listed on 2019 inspection report, project #19120911. Not corrected as of 1/26/2021. Reinspection fee issued under inspection #258544. Failure to correct deficiencies within 60 days will result in citations.
5082 | 6/7/2017Main building - BlueGym riser - YELLOWCorrect yellow tag on gym sprinkler riser.
5083 | Conduct and document required annual fire safety training.
5084 | Current evacuation maps do not show primary and secondary exits.Update all maps to show two exit routes in contrasting colors.
5085 | Expired 12/31/2019Update expired elevator permit.
5086 | Place "Roof Access" sign on door to room 148 (Switch gear room).
5087 | Have egress lighting tested and provide documentation that any deficiencies were corrected.
5088 | PROVIDE EVACUATION MAPS: MAIN OFFICE, 6.
5089 | EXPIRED P2 PERMIT
5090 | NoData
5091 | NoData
5092 | 5-27-2020 IN COMPLIANCE
5093 | 7-2020 IN COMPLIANCE
5094 | 7-2020 IN COMPLIANCE
5095 | NoData
5096 | NoData
5097 | NoData
5098 | NEED SERVICE 9-10-19 LAST DATE
5099 | NoData
5100 | 6-2020 PANEL IN COMPLIANCE. NO VIOLATION
5101 | 6-2020 IN COMPLIANCE. NO VIOLATION
5102 | 7-2020 IN COMPLIANCE. NO VIOLATION
5103 | 7-2020 IN COMPLIANCE. NO VIOLATION
5104 | Fire alarm system is yellow tagged. Initiated a 72 Hrs. Notice of Violations and a Fire Watch Assignment Agreement.Arrived on location to find fire alarm system with a white service tag dated 1/29/2021 replacing yellow tag dated 1/20/2021. Supporting photos attached to inspection record.
5105 | NoData
5106 | Portable fire extinguisher(s) require updated testing
5107 | NoData
5108 | Silver portable fire extinguisher(s) require updated testing
5109 | 24" clearance must be maintained between ceiling and combustible materials
5110 | Only UL listed resettable multiplug adapters are allowed in businesses
5111 | Only UL listed resettable multiplug adapters are allowed in businesses
5112 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs
5113 | Obtain and post Certificate of Occupancy [104.1(9)]
5114 | Directional arrows showing incorrect direction to exit
5115 | NoData
5116 | NoData
5117 | The fork lift requires a fire extinguisher with a minimum rating of 10BC.
5118 | Remove obstructions in front of exits.
5119 | The spray booth suppression systems are past due for inspection.
5120 | Clear and maintain 3 feet of clearance around the spray booth.
5121 | Provide a "Falcon padlock" or a "Knox padlock" for the 911 key box.
5122 | Ensure all compressed gas cylinders are secured.
5123 | Provide protected storage for propane cylinder.
5124 | Remove propane cylinder from inside the shop. Outdoor storage is required.
5125 | Repair or replace the emergency illumination on the exit signs.
5126 | Exits are required to be unlocked while the building is occupied.
5127 | NoData
5128 | NoData
5129 | NoData
5130 | COMPLIANCE DATE: 15 CALENDAR DAYS
5131 | P2 permit is expired at this time.
5132 | Informational regarding exits and exit lighting, see 2.4.2.4
5133 | Building F CO missing in binder. Please add CO to binder.
5134 | NoData
5135 | Test report of exit signs and exit lighting required
5136 | Please ensure all exit signs and lighting meet code
5137 | NoData
5138 | Please repair all access gates. Have vehicles removed from the Fire Lanes. Gates shall remain open until all repairs are brought up to L.S.B #4 Standards.
5139 | Vehicles shall not block any fire department access gates.
5140 | Please trim the tree by the manual access gate. (the middle manual drive through gate to left of the office) Vertical clearance shall be 13'6"
5141 | remove all worn out old tires that are creating a fire hazard nuisance .
5142 | remove all use tires that are creating a fire hazard for the public residence located also in the rear next to the waste old tire storage
5143 | NoData
5144 | NoData
5145 | NoData
5146 | NoData
5147 | 10/11/2019 - Blue, OK
5148 | 5/21/2019 - OK
5149 | Obstructed drills OK
5150 | Last drill 1/8/2021. Drills conducted monthly - OK
5151 | 8/2018Have all portable fire extinguishers inspected.
5152 | Add one extinguisher to stage.
5153 | Correct all violations within 60 calendar days.
5154 | Sprinkler system does not have a new installation tag affixed. Have new installation tag placed on sprinkler system.
5155 | 11/4/2020 - RedHi-Tek improperly tagged panel during annual inspection. Tag posted states yellow, but report states red. Red tag was due to ground fault listed by HISD Security Maintenance in 9/2020. Ground fault corrected 1/5/2021.Verify that deficiencies noted on Hi-Tek's inspection tag have been corrected.
5156 | 11/4/2020Provide audibility test report for inspector to review.
5157 | Have load bank performed and provide report for inspector to review.
5158 | 10/13/2019Have sprinkler system inspected and correct any deficiencies.
5159 | New installation 2015. Provide flow test report for standpipes.
5160 | New installation 2015Have 5 year hydro performed and correct any deficiencies.
5161 | 10/12/2019Have fire pump flow test performedNote: pump is likely due for full flow test (water discharged from test header).
5162 | 5/2020Have ANSUL system inspected.
5163 | Remove all combustible items currently stored under stairs.
5164 | Conduct and document required annual fire safety training.
5165 | Remove leaking hydrochloric acid bottle from cabinet in 3rd floor chemistry storage.Thoroughly clean acid spill and repair damaged cabinet.Provide flammable liquid and acid cabinets for proper storage of hazardous materials.
5166 | Provide building/gate lock keys. Inspector will place keys in existing Knox Boxes.Remove combination lock from gate near FDC and replace with Falcon or Knox lock.
5167 | Update EOP for 20-21 school year.
5168 | Provide sensitivity report and provide documentation that deficiencies were corrected.
5169 | Update expired elevator permit (9/30/2019).
5170 | Obtain Keybox (K1) permit for the six Knox boxes currently at location.
5171 | Test egress lighting, correct deficiencies, and provide documentation.
5172 | NoData
5173 | NoData
5174 | AS PER CODE
5175 | AS PER CODE
5176 | AS PER CODE , NO HANGING COMBUSTIBLE MATERIAL FROM CEILING.
5177 | AS PER CODE
5178 | TEST ALL EMERGENCY LIGHTS. PLACE PAPER WORK IN FIRE MARSHAL BINDER.
5179 | AS PER CODE, THE PERSON IN CHARGE SHALL ENSURE THAT ALL STUDENTS AND STAFF MEMBERS ARE PROPERLY TRAINED IN EVACUATION PROCEDURES.
5180 | SPRINKLER RISER YELLOW TAGGED CHECK VALVE 2 LEAKING FIRE ALARM PANEL SYSTEM TROUBLE & SILENCED BRING ALL UP TO CODE
5181 | NEED ANNUAL TWO-WAY COMMUNICATION INSPECTION AND TESTED TO VERIFY ALL COMPONENTS ARE OPERATIONAL . PLACE PAPER WORK IN FIRE MARSHAL BINDER
5182 | NoData
5183 | ONLY PANIC HARDWARE OR SIMILIAR SINGLE OPERATION TO OPEN/UNLOCK LOCKING DEVICES ALLOWED ON THESE DOORS. REMOVE ALL OTHER LOCKING DEVICES.
5184 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
5185 | Provide documentation/report for annual 'Load Test' and any necessary repairs.
5186 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
5187 | Provide Documentation/Report and tag for the 5th Year FDC Hydrostatic test.
5188 | Provide documentation/report for fire damper testing and any necessary repairs.
5189 | Repaint Fire Lane
5190 | Provide Boiler Permits: 239325, 202117, 202118
5191 | NoData
5192 | NoData
5193 | NoData
5194 | A Fire Department stand-by may be required if red-tagged system is not serviced in a timely manner.
5195 | Fire alarm system is red tagged and must be serviced within 72 hours
5196 | Failure to service red tagged systems will be subject to citations and re-inspection fees.
5197 | NoData
5198 | Did not find any fire code violations upon inspection of 1109 Hub Street. I was sent to 1107 Hub street, but that address does not exist. The owner/occupant of the business needs to continue and expedite the process of obtaining the Certificate of Occupancy which began in April, 2020.
5199 | NoData
5200 | High-Piled Combustible Storage: Storage of combustible materials in closely packed piles or combustible materials on pallets, in racks or on shelves where the top of the storage is greater than 12 feet in height. When required by the fire code official, high-piled combustible storage also includes certain high-hazard commodities, such as rubber tires, Group A plastics, flammable liquids, idle pallets and similar commodities, where the top of the storage is greater than 6 feet in height.
5201 | NoData
5202 | It is the owner/occupants responsibility to correct the following violations:-Permits to be obtained: A4 (Access Gate), H3 (Cutting/Welding)-Permits to be canceled: F7 (Flammable/Combustible Liquid Storage)-Permits pending approval: H1 (Hazardous Materials Tier 1) HMIS requested -Install a Knox Box on a post near the gated entrance 48"-60" off the ground and in such a way that it is readily accessible, easily visible, and not subject to damage. The Knox Box should have a electronic means of opening the gate, and a key to the exterior lock on the fail safe box.-Install a NFPA 704 Placard on the front gate and on each man door entrance to the warehouse. This placard should represent the highest threat level present of anystored commodityfor each category.-Pallets stored inside are not to be stored at a height of 6 feet or greater.-Cover all open spaces inside the breaker boxes using the proper breaker box filler plate and properly secure all breaker labels to the inside of the breaker box door.-Create and maintain a clear path of travel to and a working space in front of the breaker boxes.-Remove propane tanks found in the warehouse.
5203 | NoData
5204 | NoData
5205 | NoData
5206 | NoData
5207 | NoData
5208 | NoData
5209 | A tent permit is required for tents greater than 400 sq. ft. Obtain a permit or reduce the size of the tent.
5210 | NoData
5211 | Have a licensed fire protection company service and tag the fire extinguishers.
5212 | Fire extinguishers with a minimum rating of 2A:10BC are required in the business.
5213 | Remove tables blocking the second exit.
5214 | Have a licensed fire protection company service and tag the vent hood suppression systems. The Vent hoods require professional cleaning. Ensure stickers with the date of cleaning are placed on the vent hoods.
5215 | Discontinue the use of "piggyback" extension cords in the kitchen area.
5216 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
5217 | Repair the main entrance door to ensure all doors swing in direction of egress.
5218 | Repair or replace the inoperable emergency illumination.
5219 | A propane permit is required for cooking. Obtain the permit or remove the propane tank located in the rear of the property.
5220 | Post the occupant load (98).
5221 | All exits are required to be unlocked while the building is occupied.
5222 | NoData
5223 | NoData
5224 | Tag Date: 12/2020
5225 | KEEP ALL STORAGE AT LEAST 3 FEET AWAY FROM THE ELECTRICAL PANELS LOCATED TO THE LEFT OF THE STAGE. PLACE HIGHLY VISIBLE TAPE ON THE FLOOR TO SIGNIFY WHERE NOT TO PLACE STORAGE. ELECTRICAL PANELS MUST BE MADE ACCESSIBLE IN THE EVENT THE POWER MUST BE SHUT OFF AND TO KEEP COMBUSTIBLE MATERIALS FROM CATCHING FIRE IN THE EVENT THERE ARE SPARKS DUE TO AN UNEXPECTED POWER SURGE
5226 | GAS TEST IS REQUIRED FOR ALL PUBLIC ASSEMBLIES EVERY 5 YEARS. LAST PERFORMED ON FEBRUARY 2009. GAS TEST SHALL BE PERFORMED BY A LICENSED PLUMBER
5227 | LICENSED PLUMBER WILL OBTAIN A PLUMBING PERMIT TO PERFORM THE GAS TEST. KEEP DOCUMENTATION OF ALL GAS TESTS PERFORMED FOR YOUR RECORDS AND TO SHOW PROOF OF GAS TEST PASSING.
5228 | CORRECTION OF ALL VIOLATIONS SHALL BE THE RESPONSIBILITY OF THE OWNER AND/OR PERSON IN CHARGE
5229 | NoData
5230 | NoData
5231 | NoData
5232 | NoData
5233 | NoData
5234 | NoData
5235 | NoData
5236 | Make all violation corrections prior to the reinspection date noted on the front page of the report.
5237 | Repair the life safety emergency egress light near the lunch room exit.
5238 | Exit sign illumination intensity level must be at least 5 foot-candles (54 lux).
5239 | Emergency Exit signs must stay illuminated at all times and during a loss of power. Repair all exit signs that are not lit.
5240 | Renew the fire alarm permitHFD18032748
5241 | NoData
5242 | NoData
5243 | NoData
5244 | NoData
5245 | In respect to Prospect Park at Willowbrook, 17776 Tomball Parkway #28-B, please be advised that failure to renew the c1, l1 and p2 permit will render a Re-inspection Fee of $386.44. Renew at the Houston Permitting Center.
5246 | Re-inspection fee is being issued due to failure to renew p2, c1, l1 permit. Issued on 2.2.21.
5247 | Make all code violation corrections prior to the re-inspection date noted on page 1 of the Inspection Report.
5248 | The annual fire alarm system inspection is expired. Provide for an annual inspection of the FAS by a state certified company. Provide a current fire alarm annual inspection report for review by the inspecting fire code official. The most current annual fire alarm inspection report shall be kept in the Fire Marshal’s Binder. The fire alarm panel shall also have an annual blue inspection tag that is current placed on the panel.
5249 | Must have one of two things to be acceptable and the Documentation should contain Company’s ACR#, Tester’s FAL#, and date. A) Must show each audibility device’s ambient decibel level and the decibel level when the device is active. The difference in DB level must fall within NFPA 72’s acceptable range for the device to pass the test. OR B) A document from their company on company’s letter head that has the following information – 1) Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all audibility devices passed the audibility test as required by NFPA 72.
5250 | Provide documentation for a current "Full" 3yr dry-pipe valve drip test.
5251 | Apply for a Fire Lane Permit for Bendwood Elementary. If Bendwood and Wildcat Way School share a parking lot, and the fire lane plans shall be on one drawing / fire lane plan, then only 1 fire lane permit shall be needed.
5252 | Provide 3 sets of Fire Lane Plot Plans per the Life Safety Bureau Standard (LSB 3). The Inspecting code official shall review and mark the plan noting where the fire lane shall be marked and signs shall be placed. After plans are approved, the occupant shall install the fire lane according to the approved plans.
5253 | Maintain minimum storage height below ceilings as stated in the above code.Several location were noted, especially in storage rooms and near the door leading to the FDC.
5254 | Fire rated caulk is needed in the following areas:- custodial room by the fire alarm room- A/C duct and hole in the wall
5255 | Punch out the chevron directional arrow that points toward the exit doors on the exit sign located in the hall / corridor near the cafeteria.
5256 | Make all code violation corrections prior to the re-inspection date noted on page 1 of the Inspection Report.
5257 | The annual fire alarm system inspection is expired. Provide for an annual inspection of the FAS by a state certified company. Provide a current fire alarm annual inspection report for review by the inspecting fire code official. The most current annual fire alarm inspection report shall be kept in the Fire Marshal’s Binder. The fire alarm panel shall also have an annual blue inspection tag that is current placed on the panel.
5258 | Must have one of two things to be acceptable and the Documentation should contain Company’s ACR#, Tester’s FAL#, and date. A) Must show each audibility device’s ambient decibel level and the decibel level when the device is active. The difference in DB level must fall within NFPA 72’s acceptable range for the device to pass the test. OR B) A document from their company on company’s letter head that has the following information – 1) Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all audibility devices passed the audibility test as required by NFPA 72.
5259 | Provide documentation for a current "Full" 3yr dry-pipe valve drip test.
5260 | Apply for a Fire Lane Permit for Bendwood Elementary. If Bendwood and Wildcat Way School share a parking lot, and the fire lane plans shall be on one drawing / fire lane plan, then only 1 fire lane permit shall be needed.
5261 | Provide 3 sets of Fire Lane Plot Plans per the Life Safety Bureau Standard (LSB 3). The Inspecting code official shall review and mark the plan noting where the fire lane shall be marked and signs shall be placed. After plans are approved, the occupant shall install the fire lane according to the approved plans.
5262 | Maintain minimum storage height below ceilings as stated in the above code.Several location were noted, especially in storage rooms and near the door leading to the FDC.
5263 | Fire rated caulk is needed in the following areas:- custodial room by the fire alarm room- A/C duct and hole in the wall
5264 | Punch out the chevron directional arrow that points toward the exit doors on the exit sign located in the hall / corridor near the cafeteria.
5265 | NO VIOLATIONS found at the time of inspection.
5266 | NoData
5267 | The owner/occupant has the responsibility of correcting or abating all fire code violations or hazards that occur in the business.
5268 | Maintain the allowed occupancy of the business, failure to do so will result in the event to be stopped until such condition or obstruction are corrected.
5269 | Always renew or apply for permits that are required for the business at the City of Houston Fire Permit Office. All be permits are to be obtained prior to engaging in any activities, operations, practices, or functions regulated by this fire code.(any required permits for the business)
5270 | All issued permits shall be kept on the premises and readily available for inspection by the fire code official.
5271 | NoData
5272 | NoData
5273 | NoData
5274 | NoData
5275 | Need a permit for the diesel storage (f7 permit)
5276 | Need to replace the elevator evacuation signs in every elevator lobby
5277 | NEED ANNUAL ALARM SYSTEM TEST
5278 | NEED TO TEST THE FDC
5279 | Management is responsible for the Life Safety Components of the High Rise building (as per the Fire Code)
5280 | Need to add a 911 box for the front entrance and garage entrance.
5281 | NEED TO DO THE ANNUAL FIRE EXTINGUISHER INSPECTION
5282 | NEED TO TEST THE EMERGENCY POWER
5283 | NEED AUDIBILITY SYSTEM TESTING
5284 | NEED TO DO ANNUAL SPRINKLER SYSTEM TEST
5285 | NEED TO DO THE ANNUAL FIRE PUMP
5286 | NEED TO TEST THE EMERGENCY DAMPERS
5287 | NEED EMERGENCY LIGHTING TESTING
5288 | NEE TO DO THE ANNUAL FIRE ALARM TESTING
5289 | ALL FIRE EXTINGUISHERS NEED TO BE MOUNTED
5290 | ALL EXIT SIGNS NEED TO BE ILLUMINATED
5291 | FIRE PUMP NEEDS SERVICED AND TAGGED
5292 | NEED TO UPDATE ALL 5 SETS OF KEYS
5293 | NoData
5294 | NoData
5295 | All automatic access gates shall have a manual pull in the case of power outage for emergency operations per Life Safety Bureau Standard 4.Compliance by 1-4-2021
5296 | An operational permit is required when a automatic access gate is in use. Apply for an access gate permit on the City of Houston website under fire department permits.Compliance by 1-4-2021
5297 | NoData
5298 | NoData
5299 | Provide covers for electrical outlets.
5300 | COMPLIANCE DATE: 15 CALENDAR DAYS
5301 | H3 permit is expired at this time.
5302 | NoData
5303 | NoData
5304 | NoData
5305 | NoData
5306 | NoData
5307 | Correct the yellow tag deficiencies on the fire sprinkler system.
5308 | Repair the fire alarm panel.
5309 | Replace the missing breaker cover on the breaker panel located in the pool service closet.
5310 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
5311 | Failure to correct gate issues and permit before the follow up inspection date.
5312 | All automatic access gates shall have a manual pull in the case of power outage for emergency operations per Life Safety Bureau Standard 4.Compliance by 1-4-2021
5313 | An operational permit is required when a automatic access gate is in use. Apply for an access gate permit on the City of Houston website under fire department permits.Compliance by 1-4-2021
5314 | COMPLETE AND SIGN THE HAZARDOUS MATERIALS INVENTORY STATEMENT ACCORDING TO INSTRUCTIONS BEFORE THE COMPLIANCE DATE LISTED ON THE FRONT OF THE REPORT
5315 | Doors to electrical room(s) must be identified
5316 | Current sensitivity test required to be on file or signed letter, on company letterhead, with technician name and license if using a "smart" panel
5317 | NoData
5318 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs
5319 | Private hydrant(s) requires annual flow test
5320 | Current audibility test needs to be conducted. Last test date showing 2/3/12
5321 | Sign for FDC needs to be place above the connections for identification
5322 | Directional arrows showing incorrect direction to exit or missing
5323 | NoData
5324 | NoData
5325 | Correct all violations within 60 calendar days.
5326 | Conduct and document required annual fire safety training.2/3/2021 - Training conducted 1/6/2021 - OK
5327 | Conduct and document obstructed fire drills.January drill was obstructed. School will conduct and document more obstructed fire drills.
5328 | Have 90 minute egress lighting test performed and provide documentation that deficiencies were corrected.2/3/2021 - Test performed 12/27/2020. Deficiencies corrected 1/27/2021 - OK
5329 | NoData
5330 | NoData
5331 | NoData
5332 | NoData
5333 | NoData
5334 | NoData
5335 | Have the required 6 mo. kitchen hood Ansul system inspected and tagged by a certified fire protection company. (scheduled for next week)
5336 | Ensure that floor plans with evacuation routes are posted in all rooms accessed by children throughout the facility. (rooms 4,5,6 and the indoor playground room were not able to be located at the time of inspection)
5337 | DO NOT BLOCK WINDOWS FROM OPENING COMPLETELY OPENING WITH ANY DEVICE. DO NOT BLOCK SECONDARY EGRESS.
5338 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
5339 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES. KEEP UPDATED PER CODE AND TRAIN QUARTERLY.
5340 | GAS PRESSURE TEST MUST BE PERFORMED EVERY 5 YEARS. KEEP PERMIT AT OCCUPANCY.
5341 | NoData
5342 | Provide portable fire extinguisher
5343 | Provide Key Box Permit
5344 | Provide Fire Alarm Permit
5345 | Provide assembly permit
5346 | Fire alarm has a trouble code that must be repaired.
5347 | Ensure all exit and emergency lights are in working order.
5348 | Please renew the K1, key box permit.Expired 6/3/2019.
5349 | NoData
5350 | Require documented 3yr audibilty report for fire alarm
5351 | FDC cap missing on outside of building
5352 | Require documented sensitivity test for fire alarm
5353 | One additional illuminated Exit sign required. Sign needs to be placed similar to sign near front of store and point to the rear exit door.
5354 | NoData
5355 | Failure to comply with inspection report by follow up date. Please follow these instructions to take care of this re-inspection fee before the date listed.
5356 | Replace all missing ceiling tiles in rear bathroom.Compliance by 11-17-2020
5357 | Have qualified sprinkler company address the yellow tag issues and bring system into compliance.Have company perform 5 year testing on sprinkler system. Last done in 2012.Compliance by 11-17-2020
5358 | Repair or replace all emergency lighting not working in the warehouse and office space.Compliance by 11-17-2020
5359 | Replace the missing 911 box near your front entrance. Also, provide a new lock on the box on the side gate. Current lock is painted on and wont open.Compliance by 11-17-2020
5360 | Replace the painted over HFD letters on the back access door and the access door in the expanded warehouse.Compliance by 11-17-2020
5361 | Remove all combustible items a minimum of 3 feet away from the electrical boxes near front dock.Compliance by 11-17-2020
5362 | Remove pallets and all other items blocking the means of egress throughout the warehouse.Immediate compliance required.
5363 | Please renew the A4, access gate permit.Expired 11/30/2020.
5364 | NoData
5365 | NoData
5366 | NoData
5367 | NoData
5368 | NoData
5369 | NoData
5370 | NoData
5371 | NoData
5372 | NoData
5373 | NoData
5374 | NoData
5375 | All fire extinguishers must be serviced and have a current service tag placed on them.
5376 | The fire alarm system must have an audibility test performed on it.
5377 | An emergency lighting test must be performed on the fire alarm system.
5378 | The yellow tag on the fire alarm panel must be corrected and removed.
5379 | The public assembly permit must be renewed.
5380 | NoData
5381 | NoData
5382 | NoData
5383 | NoData
5384 | NoData
5385 | NoData
5386 | NoData
5387 | AT THE TIME OF INSPECTION, APPROVED PLANS COULD NOT BE PRESENTED FOR INSPECTION BY THE FIRE MARSHAL. APPROVED PLANS ARE TO BE KEPT ON SITE AT ALL TIMES. IF APPROVED PLANS CANNOT BE LOCATED, A REQUEST TO THE BUILDING DEPARTMENT MAY BE ABLE TO DUPLICATE THE ORIGINAL. APPROVED PLANS MUST BE SUBMITTED TO FIRE MARSHAL OR THE PROCESS FOR HIGH-PILED STORAGE PLAN SUBMITTAL PROCESS SHALL BE RESTARTED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
5388 | THE EXIT PATHWAYS AND EXIT STAIRWAYS LEADING AWAY FROM THE WAREHOUSE SHALL HAVE A CLEAR PATH TO AN AREA OF SAFE REFUGE.COMPLIANCE: WITHIN 7 CALENDAR DAYS.
5389 | AISLES WIDTHS STATED ON THE APPROVED PLANS ARE NOT BEING MAINTAINED AND SHALL BE BROUGHT INTO COMPLIANCE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
5390 | NoData
5391 | FYI: Already signed Statement of Compliance.
5392 | Already signed Statement of Compliance.
5393 | Need a gas leak test performed every 5 years by a licensed plumber. FYI: Last gas leak was 5/12/2010 (#10026701).
5394 | FYI: Already signed Statement of Compliance.
5395 | NoData
5396 | NoData
5397 | NoData
5398 | NoData
5399 | NoData
5400 | NoData
5401 | NoData
5402 | NoData
5403 | The vent hood suppression system is due for service before the end of 03/2021.
5404 | Fire extinguishers are due for annual service before the end of 03/2021.
5405 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
5406 | It is the owner/occupants responsibility to correct the violation found.
5407 | The FDC on the south side of the building was found to have 2.5 inch "male" couplings. Contact a licensed fire protection company to have the FDC replaced with a fitting that has 2.5 inch "female" couplings.
5408 | NoData
5409 | Repair emergency fail safe. Rusted do not function properly
5410 | Location and placement of the fire extinguisher shall be placed in accordance with the manufactures guidelines or Section 1.3.8, near the kitchen entryway, accessible and no closer than 5 feet from the cooking appliance.
5411 | repair exit lighting and emergency lighting.
5412 | Isabel Alcola 7136452525
5413 | Used existing wires to interconnect smoke detector. apt# 6,15 check all other unit.
5414 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
5415 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES. KEEP PLANS UPDATED AND TRAIN QUARTERLY.
5416 | APPLY FOR CERTIFICATE OF OCCUPANCY. OBTAIN A PHYSICAL COPY AND POST ON PROPERTY.
5417 | NoData
5418 | NoData
5419 | NoData
5420 | NoData
5421 | NoData
5422 | NoData
5423 | NoData
5424 | NoData
5425 | Renew New Public Assembly & Candles Permits within 10 Business days.
5426 | NoData
5427 | NoData
5428 | AT LOCATIONS WHERE HAZARDOUS MATERIALS ARESTORED IN QUANTITIES REQUIRING FIRE DEPARTMENT PERMITS AND AT WAREHOUSELOCATIONS, KEY BOXES SHALL BE LOCATED AT THE MAIN FIRE DEPARTMENT ACCESSENTRANCE TO THE FACILITY, EITHER AT A GUARD SHACK OR GATE HOUSE, OR SIMILARLOCATION AND APPROVED 911 FALCON LOCK ATTACHEDCOMPLIANCE WITHIN 30 DAYS
5429 | A WORKING SPACE (CLEARED OF ALL COMBUSTIBLEMATERIAL) OF NOT LESS THAN 30 INCHES IN WIDTH, 36 INCHES IN DEPTH AND 78 INCHESIN HEIGHT SHALL BE PROVIDED IN FRONT OF ELECTRICAL SERVICE EQUIPMENT.COMPLIANCE WITHIN 30 DAYS.
5430 | A PERMIT SHALL BE OBTAINED PRIOR TO ENGAGING IN ANY ACTIVITIES, OPERATIONS, PRACTICES, OR FUNCTIONS REGULATED BY THIS CODE AND REQUIRING A PERMIT AS LISTED IN SECTION 105.6.IT SHALL BE UNLAWFUL FOR ANY PERSON TO ENGAGE IN ANY ACTIVITIES, OPERATIONS, PRACTICES OR FUNCTIONS WITHOUT HOLDING A CURRENT AND VALID PERMIT.COMPLIANCE WITHIN 30 CALENDAR DAYS.ISSUED PERMITS SHALL BE KEPT AT FACILITY AT ALL TIMES AND SHALL BE READILY AVAILABLE FOR INSPECTION BY THE FIRE CODE OFFICIAL.APPLY FOR AND OBTAIN A L1 LP-GASOPERATIONAL PERMIT FROM THE CITY OF HOUSTON PERMITTING CENTER LOCATED AT 1002 WASHINGTON AVE.(832-394-9000).
5431 | EXTENSION CORDS SHALL NOT BE USED FOR APERMIT SOURCE OF POWER IN FACILITY.COMPLIANCEWITHIN 30 DAYS
5432 | ENSURE THAT ALL DUMPSTERS ARE MAINTAINED 10FEET MINIMUM FROM THE BUILDING AT ALL TIMES.COMPLIANCE: WITHIN30 CALENDAR DAYS.
5433 | IMMEDIATE COMPLIANCEIS REQUIRED. (NFPA 13 Table A12.12.1.1)OUTDOOR STORAGE OF IDLE PALLETS:- MINIMUM DISTANCE OF RECOMMENDED CLEARANCEBETWEEN OUTSIDE IDLE WOOD PALLET STORAGE AND METAL BUILDING: UNDER 50 PALLETS - 20 FEET 50 - 200 PALLETS - 30 FEETOVER 200 PALLETS – 50 FEETCOMPLIANCEWITHIN 30 CALENDAR DAYS.
5434 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
5435 | KEEP EMERGENCY EVACUATION PLAN ON PRPERTY AT ALL TIMES. KEEP UPDATED PER CODE AND TRAIN QUARTERLY.
5436 | APPLY FOR CERTIFICATE OF OCCUPANCY. OBTAIN THE CERTIFICATE OF OCCUPANCY AND POST AT THE OCCUPANCY.
5437 | NoData
5438 | NoData
5439 | NoData
5440 | Renew p2 (Assembly) permit at the Houston Permitting Office, 1002 Washington (832.394.8811). Failure to renew the permit will render a Re-inspection Fee.
5441 | NoData
5442 | NoData
5443 | Renew p2 (Assembly) permit at the Houston Permitting Office, 1002 Washington (832.394.8811). Failure to renew the permit will render a Re-inspection Fee.
5444 | NoData
5445 | The owner/occupant has the responsibility of correcting or abating all fire code violations or hazards that occur in the business.
5446 | Remove the accumulation of trash and organize the storage area to protect against the spread of fire. Make sure the electrical panels are accessible if needed by emergency personal.
5447 | The kitchen suppression system must be serviced, when completed make sure that it has a current service tag marked acceptable(not yellow or red). The kitchen suppression system should be serviced every 6 months.
5448 | Always maintain approved occupancy of a building as stated be the certificate of occupancy. Failure to do so will result with the event to be stopped until such conditions are corrected.
5449 | Place a sign or sticker to help indicate where the portable fire extinguishers is located in the business, by the ice machine in the kitchen area
5450 | NoData
5451 | Clean kitchen vent hoods at intervals to prevent the accumulation of grease build up, records shall be kept to provide time and date of cleaning.(every 90 days)
5452 | Always renew or apply for permits that are required for the business at the City of Houston Fire Permit Office. All be permits are to be obtained prior to engaging in any activities, operations, practices, or functions regulated by this fire code.(L5/LPG is required for the business)
5453 | All issued permits shall be kept on the premises and readily available for inspection by the fire code official.
5454 | NoData
5455 | NoData
5456 | NoData
5457 | NoData
5458 | NoData
5459 | NoData
5460 | Your key box (k1), spraying and dipping (s1), and hot works (h3) fire permits expired on 1-14-2021. Renew these permits using the instructions above by the date listed above.Total fee is $711.47
5461 | NoData
5462 | NoData
5463 | NoData
5464 | NoData
5465 | REPLACE MISSING OUTLET AND SWITCH COVERS.
5466 | OBTAIN AND MOUNT AT LEAST 2 FIRE EXTINGUISHERS WITH A MINIMUM RATING OF 2A:10BC TO ENSURE THERE'S AN EXTINGUISHER WITHIN 75 FEET OF UNOBSTRUCTED TRAVEL DISTANCE.
5467 | REPAIR OR REPLACE THE EMERGENCY ILLUMINATION ON THE EXIT SIGNS AS WELL AS THE STAND ALONE EMERGENCY LIGHTING TO ENSURE IT IS FULLY OPERATIONAL.
5468 | REMOVE STORAGE IN FRONT OF EXIT PATH.
5469 | OBTAIN AND POST AN ASSEMBLY PERMIT. REQUIRED FOR OCCUPANT LOADS GREATER THAN 49.
5470 | -ENSURE ALL EXITS ARE UNLOCKED WHILE THE BUILDING IS OCCUPIED. -PLACE STICKERS ON EXIT DOORS STATING: "THIS DOOR TO REMAIN UNLOCKED WHEN THE BUILDING IS OCCUPIED".
5471 | #NAME?
5472 | DISCONTINUE THE USE OF EXTENSION CORDS AS A PERMANENT SOURCE OF WIRING.
5473 | MOUNT THE FIRE EXTINGUISHERS ACCORDING TO THE CODE LISTED ABOVE.
5474 | NoData
5475 | POST ADDRESS NUMBERS ON THE FRONT OF THE BUSINESS. NUMBERS ARE REQUIRED TO BE A MINIMUM OF 4 INCHES IN HEIGHT AND PLACED ON A CONTRASTING BACKGROUND.
5476 | CLEAR AND MAINTAIN 36 INCHES IN FRONT OF BREAKER PANELS.
5477 | NoData
5478 | The permit amount for oxidizing gas is &gt;504 cu. ft. on site. With 4 "H" bottles (2 oxygen, 2 nitrous) on site of min. 240 cu. ft. each, a C7: Compressed Gas permit must be obtained and posted on site. Permits may be obtained at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811 www.houstonpermittingcenter.orgCompliance is required within 2 weeks: 2/24/2021
5479 | NoData
5480 | annual inspection due last inspected 10/2018
5481 | NoData
5482 | fire sprinkler system annual inspection due last inspected 3/21/2018
5483 | fire extinguishers annual inspection due last inspected 10/2018
5484 | NoData
5485 | NoData
5486 | NoData
5487 | Must repair both gates fail safe and put key inside 911 box and paint red
5488 | Toggle switch need to be operational paint 911 in white and paint 911 box red
5489 | Must be placed on the entrance gate HFD and zero at the bottom
5490 | Need to be renewed
5491 | Must be located at entrance gate make sure it can be seen at night time
5492 | NoData
5493 | NoData
5494 | NoData
5495 | NoData
5496 | NoData
5497 | OBTAIN AND POST THE FOLLOWING PERMITS: -GATE PERMIT (A4) -911 KEYBOX PERMIT (K1)
5498 | Fire Alarm Panel is missing the current Annual Inspection Tag.COMPLIANCE WITHIN 60 CALENDAR DAYS.
5499 | Trash needs to be emptied after use in the Oily Rag cans located in the Elevator Mechanical Rooms.COMPLIANCE WITHIN 60 CALENDAR DAYS.
5500 | Submit Current Fire Safety Plan for approval.COMPLIANCE WITHIN 60 CALENDAR DAYS.
5501 | Mobility Impairment list needs to be updated every 6 months in the Fire Depository Box Book.COMPLIANCE WITHIN 60 CALENDAR DAYS.
5502 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualFire Extinguishers- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
5503 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice.COMPLIANCE WITHIN 60 CALENDAR DAYS.
5504 | Maintain Clearance around hot water heater
5505 | Alarm permit expired
5506 | NoData
5507 | NoData
5508 | NoData
5509 | NoData
5510 | Renew the facility's P2: Public Assembly permit which expired on 12/20/2020.
5511 | NoData
5512 | An approved operational fire sprinkler system is required prior to occupying the building.
5513 | An approved operational fire alarm system is required prior to occupying the building.
5514 | A C/O or a temporary C/O is required prior to occupying the building.
5515 | NoData
5516 | NoData
5517 | NoData
5518 | Please renew the K1, key box permit.Expired 9/6/2019.
5519 | NoData
5520 | NoData
5521 | NoData
5522 | NoData
5523 | NoData
5524 | NoData
5525 | NoData
5526 | It is the owner/occupants responsibility to correct all violations listed below:-Contact a licensed fire protection company to have the fire alarm system serviced and ensure a blue acceptable annual service tag is attached. Ensure that an audibility test has been performed within the past 3 years, and a sensitivity test has been performed within the past 2-5 years. Repair or replace damaged smoke detector in the custodial closet.-Wet chemical extinguishing systems in commercial kitchens are required to be serviced every 6 months. Contact a licensed fire protection company to service the ANSUL system and ensure a current service tag is attached.-Commercial kitchen hoods in low-volume cooking operations such as places of religious worshipare required to beinspected and serviced as necessary every 12 months. Contact a licensed professionalto have the vent hood inspected. Ensure a service tag is attached following the completion of the service.-Have all exit signs inspected to ensure they are properly illuminated under regular service power and battery back up power.-Ensure all ceiling tiles that were found to be missing are put back into place and are properly seated. (second floor classroom and custodial closet)-Remove the white tape being used tocover the open space in the breaker boxin the electrical closet in the school roomand replace with a breaker box filler plate.Side NotesGas test performed and finaled on 09/02/20Fire drill logs inspected and found to be complete
5527 | NoData
5528 | NoData
5529 | NoData
5530 | Please renew the A4, access gate permit.Expired 2/1/2020.
5531 | NoData
5532 | NoData
5533 | NoData
5534 | fire sprinkler system annual inspection due; last inspection 11/30/2017
5535 | fire extinguishers annual inspection due; last inspection 7/2018
5536 | hood ansul system semi-annual inspection due; last inspection 4/2020
5537 | Have a licensed fire protection company service and tag the fire extinguishers.
5538 | Have a licensed fire protection company inspect and repair any deficiencies on the vent hood suppression system.
5539 | Post the occupant load.
5540 | Remove locking bar on the rear exit while the building is occupied. Repair hardware if necessary.
5541 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
5542 | NoData
5543 | NoData
5544 | NoData
5545 | NoData
5546 | NoData
5547 | NoData
5548 | Update fire safety plan and submit to inspector for approval.
5549 | 1) Add one standardized floor plan making a total of 3 sets per code. 2) Add top level re-entry to the elevator diagram per code.
5550 | Add one more elevator hoist way key making a total of two keys per code.
5551 | Cover junction box in fire pump room per code.
5552 | Go through electrical, and mechanical rooms and ensure fire rated resistance rating is maintained. Make additional corrections as needed per code.
5553 | Go through all stairways, electrical and mechanical rooms and ensure all fire doors close and latch from the open position per code.
5554 | Add one fire phone, making a total of 3 per code.
5555 | Install lock out tag out station so it is readily accessible.
5556 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriateinspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualFire Extinguishers- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
5557 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. • Present Permits that apply to facility Address listed • on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS.
5558 | 1/2021 - OK
5559 | 12/26/2020 - Blue, OK
5560 | 12/26/2020 - OK
5561 | 1/23/2018 - Blue, OK
5562 | 10/2020 - OK
5563 | 8/16/2018 - OK
5564 | Monthly drills conducted. Log OK
5565 | 1/7/2020 - OK
5566 | 1/31/2020 - BlueRiser was yellow tagged 1/23/2018 due to a leaking check valve. There is no service tag on panel to indicate this was corrected. Have sprinkler contractor properly tag the riser.
5567 | Correct all violations within 60 calendar days.
5568 | 1/31/2020 - Have sprinkler system inspected and have any deficiencies corrected.Riser was yellow tagged 1/23/2018 due to a leaking check valve. There is no service tag on system to indicate this was repaired. Verify check valve was repaired/replaced and provide documentation.
5569 | Conduct and document required annual fire safety training.
5570 | Evacuation maps are too broad. Update maps to show smaller portions of building.
5571 | Conduct and document obstructed fire drills.
5572 | FDC is located at corner of property and not near building. Location is not obvious. Replace existing FDC sign so that location is easily determined upon approach to building.
5573 | Place "Roof Access" sign on door to room 806.
5574 | Have egress lighting test performed and provide documentation that deficiencies were corrected.
5575 | NoData
5576 | NoData
5577 | NoData
5578 | Clear and maintain clearance around the spray booths.
5579 | provide and install 911 emergency red box along with a falcon lock for emergency entrance in case of fire or other emergencies.
5580 | NoData
5581 | provide all expose wiring under conduit piping to keep from been expose for fire hazard
5582 | provide and install emergency 911red box
5583 | provide and install a falcon lock with an extra key front your gate lock on the 911 red box
5584 | provide and install street address numbers at lease (4) inches tall
5585 | NoData
5586 | apply for a flammable and combustible liquid storage permit at 1002 Washington for storing more than (25) of waste oil in a plastic container with a storage capacity of (200) gallons or more
5587 | KnoxBox.com 3200 series
5588 | Correct all red & yellow tags on property.
5589 | Repair all yellow tags
5590 | Annual flow test is required for all private F/H on property.
5591 | Informed all residents on the proper use of all open flame cooking devices.
5592 | Check for proper "Fail Safe" operations
5593 | Micro Switch located inside 911 box is defective. Also, a 911 Falcon lock is required.
5594 | Verify all draft stops integrity on property
5595 | HFD 9" Fire Hydrant sign is faded and needs replacing on main access gate
5596 | Blue reflector is required in middle of Apparatus Access road to identify F/H locations.
5597 | Verify all units have working smoke alarms
5598 | Check when your last Gas test was done on property. My records show 02/08/2019.
5599 | Please update your Access gate (a4) permit with HPC. A4 permit expired on 04/06/2020
5600 | Please update your Key box (k1) permit with HPC.K1 permit expired on 04/06/2020
5601 | Please have a gate contractor repair all deficient equipment with your access gates.
5602 | NoData
5603 | NoData
5604 | NoData
5605 | NoData
5606 | Portable fire extinguishers require updated testing
5607 | NoData
5608 | All electrical circuits must be labeled
5609 | F7 permit required for oil storage tanks
5610 | Portable fire extinguishers require updated testing
5611 | NoData
5612 | NoData
5613 | All circuits must be labeled
5614 | Portable fire extinguishers require updated testing
5615 | Extension cords not allowed for permanent wiring. Remove from water cooler / toaster oven
5616 | No missing spacers allowed in electrical panels
5617 | 36" Working clearance must be maintained in front of electrical panels
5618 | Apply for f-7. Storage of cooking oil.
5619 | Address must be visible.
5620 | Clear area around electrical panel.
5621 | Replace missing cover plate.
5622 | Remove extension cord used as permanent source of power.
5623 | All fire extinguishers must be serviced and have a current service tag placed on them.
5624 | An audibility test must be performed on the fire alarm system.
5625 | The Fire alarm system must have an emergency lighting test performed on it.
5626 | The yellow tag on the fire alarm panel must be corrected and removed.
5627 | The public assembly permit must be renewed.
5628 | Circuits labeled on panel
5629 | Obtain and post Certificate of Occupancy [104.1(9)]. Current yellow application receipt also acceptable - Proj# 20025514
5630 | Portable fire extinguisher(s) annual maintenance expired; require current inspection
5631 | Portable fire extinguishers are required to be mounted per code
5632 | Minimum rating for all extinguishers will be 2A,10B:C
5633 | Keep all exit door(s) and pathways clear. Iron gate and filing cabinet to be removed
5634 | Spray/Dip (S1) permit for spray booth on site
5635 | NoData
5636 | Spray booth must be inspected every 6 months by a licensed fire protection company
5637 | Sign required
5638 | Address of business is required to be clearly legible from the main facing roadway, see code above for lettering requirements
5639 | All junction boxes, light switches and plug outlets must have cover plates installed
5640 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs
5641 | Mark 2nd exit with exit sign instead of pointing to stairwell
5642 | Keybox (K1) permit required for gate
5643 | Flammable/Combustible (F7) permit for tanks >60 gal holding waste oil (Class IIIB)
5644 | Iron gate in front of exit door must be removed in front of only exit from the area
5645 | NoData
5646 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
5647 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
5648 | Provide documentation/report for fire damper testing and any necessary repairs.
5649 | Inspect and Service tag commercial kitchen hood system. Correct all red tag impairments immediately.
5650 | Repaint Fire Lane
5651 | Provide address numbers on building.
5652 | Provide documentation/report for Natural Gas Test.
5653 | The kitchen hood suppression system is due for inspection before the end of 12/2020.
5654 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
5655 | Apply for, obtain, and post on site a P2: Public Assembly permit. This is required based on your facility's A-2 occupancy type with occupant load over 50 persons as denoted on your certificate of occupancy. The permit may be obtained at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811 www.houstonpermittingcenter.orgThis permit must be obtained prior to operations being initiated.
5656 | NoData
5657 | NoData
5658 | NoData
5659 | NoData
5660 | NoData
5661 | NoData
5662 | APPLY FOR A CERTIFICATE OF OCCUPANCY AT 1002 WASHINGTON AVE. ALL COMPANIES INSIDE THE CITY LIMITS OF HOUSTON SHALL HAVE A OCCUPANCY PERMIT BEFORE OCCUPYING THE BUILDING. COMPLIANCE BY 4-4-2019
5663 | SUBMIT A HMIS SHOWING HAZARDOUS MATERIALS THAT ARE BEING STORED AND AMOUNTS INSIDE AND OUTSIDE YOUR WAREHOUSE. THE GUIDELINE TO FILL OUT THIS REPORT WILL BE PROVIDED. COMPLIANCE WITHIN 30 DAYS.
5664 | NO VIOLATIONS FOUND AT THIS TIME REMINDER CONTINUE TO HAVE ACCESS TO CLASS K EXTINGUISHER AND ANSUL PULL STATION IN CASE OF A GREASE FIRE
5665 | Fire extinguisher must be mounted on the wall.Compliance within 30 days.
5666 | Make necessary repairs stated on yellow tag.Compliance within 30 days.
5667 | Exit sign must be maintained and operable.Compliance within 30 days.
5668 | Remove all combustible materials being stored from under all stairs.Compliance within 30 days.
5669 | Permit required from City of Houston to have a keybox.Compliance within 30 days.
5670 | Keybox required for HFD to have access to facilityCompliance within 30 days
5671 | NoData
5672 | NoData
5673 | NoData
5674 | NoData
5675 | NoData
5676 | NoData
5677 | NoData
5678 | NoData
5679 | Maintain clean filters in paint booth.
5680 | Information
5681 | NoData
5682 | NoData
5683 | NoData
5684 | NoData
5685 | NoData
5686 | #NAME?
5687 | - PROVIDE FIRE ALRM AUDIBILTY TEST AND SMOKE SENSITIVITY TEST - AUDIBILITY TEST (EVERY 3 YEARS) - SENSITIVITY TEST (EVERY 2 YEARS)
5688 | The required permits shall be purchased within 2 weeks and maintained on site to avoid citations.
5689 | Obtain an L1: LPG operational permit and post on site for the storage and use of propane.Permits may be obtained at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811 www.houstonpermittingcenter.org
5690 | Obtain a P2: Public Assembly operational permit. This permit is required due to your facility's A-2 occupancy type with occupant load over 50 persons, as stipulated on the Certificate of Occupancy.Permits may be obtained at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811 www.houstonpermittingcenter.org
5691 | NoData
5692 | NoData
5693 | NoData
5694 | NoData
5695 | NoData
5696 | NoData
5697 | NoData
5698 | Have all fire extinguishers inspected and tested. The most recent service tag is dated March 2019. Must be done annually.
5699 | Have the fire alarm system inspected and tested. Most recent tag is dated 9/23/16. Must be done annually. Repair any impairments that would cause a yellow or red tag.
5700 | Have the FDC inspected and tested. Did not find tag related to inspection and test. If performed within the past 5 years, inspection and testing does not need to be performed, but proof of this service must be provided. Repair any impairments that would render a yellow or red tag.
5701 | Have the kitchen suppression system inspected and tested. Most recent tag is dated March 2019. Must be done every 6 months. Repair any impairments that would cause a yellow or red tag.
5702 | Have the Class K fire extinguisher inspected and tested. Most recent tag is dated March 2019. Must be done annually.
5703 | Have the fire pump inspected and tested. Most recent tag is dated January 2020. Must be done annually. Repair any impairments that would render a yellow or red tag.
5704 | NoData
5705 | Renew p2, c1 permit at the Houston Permitting Center, 1002 Washington (832.394.8811). Failure to renew within 10 days will render a Re-inspection Fee.
5706 | NoData
5707 | NoData
5708 | NoData
5709 | NoData
5710 | NoData
5711 | NoData
5712 | NoData
5713 | NoData
5714 | NoData
5715 | NoData
5716 | NoData
5717 | NoData
5718 | NoData
5719 | NoData
5720 | NoData
5721 | Reinspection fee issued for failure to renew expired D2 permit at Eisenhower HS. Renew expired permit ($266.80) and pay reinspection fee.
5722 | NoData
5723 | NoData
5724 | NoData
5725 | NoData
5726 | NoData
5727 | NoData
5728 | NoData
5729 | NoData
5730 | NoData
5731 | NoData
5732 | Please contact the HPC Office @ 832-394-8811 with all questions regarding expired (k1) permit.
5733 | Please contact the HPC Office @ 832-394-8811 with all questions regarding expired permits
5734 | NoData
5735 | Fire extinguishers need to have their annual inspection
5736 | NoData
5737 | NoData
5738 | NoData
5739 | NoData
5740 | Expired Access Gate (A4) and Key Box (K1) permit 9/11/20.
5741 | Please contact the HPC Office @ 832-394-8811 with all questions regarding expired permits
5742 | Please contact the HPC Office @ 832-394-8811 with all questions regarding expired permits
5743 | COMPLIANCE DATE: 15 CALENDAR DAYS
5744 | K1 permit is expired at this time.
5745 | NoData
5746 | NoData
5747 | Provide Intercom test.
5748 | Provide annual emergency light report.
5749 | NoData
5750 | Access Gate (a4) and Key Box (k1) permits expired 12/14/20.
5751 | NoData
5752 | NoData
5753 | NoData
5754 | H3 permit expired 12/20/20
5755 | NoData
5756 | The following annual operational permits shall be obtained and posted on site within 2 weeks:-P2: Public Assembly (101-299 occupants)-Fire Alarm PermitPermits are available at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811 www.houstonpermittingcenter.org
5757 | NoData
5758 | Fire extinguisher must be inspected annually.
5759 | Mount fire extinguisher
5760 | Replace missing electrical cover plate.
5761 | NoData
5762 | NoData
5763 | Move the storage blocking direct access to the exit in the warehouse and maintain a clear path to all exits. Immediate compliance required.
5764 | Place a fire pump and electrical room sign on the outside of the doors leading into these rooms.Compliance by 3-5-2021
5765 | Remove the propane bottles not being used on forklifts and secure them outside the building.Compliance by 3-5-2021
5766 | All forklifts powered by propane, fuel, or diesel shall have a tagged mounted fire extinguisher.Compliance by 3-5-2021
5767 | Move large dumpster a minimum of 10 feet from the building and the smaller dumpster a minimum of 5 feet from the building.Compliance by 3-5-2021
5768 | COMPLIANCE DATE: 15 CALENDAR DAYS
5769 | M3 and C7 fire prevention permit are expired at this time.
5770 | M3 and C7 permit is expired at this time.
5771 | NoData
5772 | Approved no violations.
5773 | NoData
5774 | Last inspection 7/31/2020. Tagged acceptable, but fire alarm inspection report shows that strobes are not in sync. Have strobe synchronization issue corrected.2/5/2021 - Strobes replaced 1/4/2021 to correct sync issue.
5775 | Audibility report shows 8 devices registered at >110db. Have volume of these devices lowered.Volume lowered and verified by SCI on 1/4/2021
5776 | NoData
5777 | NoData
5778 | NoData
5779 | NoData
5780 | NoData
5781 | Repair and replace sheet rock inside the storage and boiler rooms.
5782 | The last gate needs to have the correct number of hydrants on that is on the property behind that gate.
5783 | Proof of gas test needed.
5784 | Needs to be renewed.
5785 | no storage under exit stairways.
5786 | Falcon locks needed on gates with the keys to the locks on the gates. KEYBOX PERMIT NEEDED.
5787 | No trees or brush should be in contact of a building. Trim vegetation away from building.
5788 | Label the doors of boiler and storage roomsPropane cannot be storage on property.Label unit electrical boxes can be labeled inside or outside.
5789 | NoData
5790 | NoData
5791 | Replace the front damaged 911 box with an approved UL listed knox box using the information given.Compliance by 11-10-2020
5792 | Provide documentation that all warehouse HVLS (high volume low speed) fans have been tied into the alarm/ sprinkler system per NFPA 72Compliance by 11-10-2020
5793 | NoData
5794 | NoData
5795 | Renew K-1 permit.
5796 | Renew K-1 permit
5797 | NoData
5798 | NoData
5799 | Keys for failsafe boxes must be located in main gate access keybox
5800 | Access gates required to be operational from keybox
5801 | Remove storage along hallway
5802 | NoData
5803 | Repair broken exit sign.
5804 | Provide Audibility Report. 5/12/2020. Provide report for correction of all failed devices.
5805 | Repair holes in ceiling
5806 | Correct 5/12/20 Yellow Tags on Fire Alarm Panel (2). Pics included.
5807 | Provide Gas Test Documentation.
5808 | Provide Wheelchair Lift Permit.
5809 | Provide exit sign to back exit.
5810 | Provide Fire Alarm Signage on Door
5811 | Provide documentation that you sprinkler system has had 5 year testing completed.Compliance by 9-4-2020
5812 | Provide documentation that your large fans are tied into the alarm panel and will automatically shut off during alarm.Compliance by 9-4-2020
5813 | No violations found at this time.
5814 | NoData
5815 | NoData
5816 | NoData
5817 | 1/2019 - Have all fire extinguishers inspectedInspected 9/2020 - OK
5818 | Trim vegetation in prayer garden away from exit pathway.Vegetation trimmed away from exterior exit pathway.
5819 | Correct all violations within 30 calendar days.
5820 | 8/1/2019 - Have alarm panel inspected.1/25/2021 - RedCorrected 1/28/2021 - OK
5821 | 8/2019 - Have hose cabinets inspected.Inspected 9/21/2020 - OK
5822 | 2/2017 - Have hoses pressure tested or replaced.
5823 | Remove combustible items currently stored in mechanical room (trash cans and floor cleaners).Prohibit future storage of combustible materials in mechanical rooms.
5824 | Conduct 90 minute egress test and correct any deficiencies.2/5/2021 - Lighting tested and deficiencies corrected 1/29/2021
5825 | NoData
5826 | NoData
5827 | I did not find any fire code violations upon inspection at this time. Fire Alarm permit is valid until July 9, 2021. C of O is 18031571.FACU inspection 3/11/2020Sensitivity test 3/11/2020Extinguishers March of 2020
5828 | FIRE SPRINKLER SYSTEM IS STILL YELLOW TAG. BUSINESS IS NOT IN COMPLANCE WITH THE CODE AT THIS TIME.
5829 | Jolie Shay
5830 | FIRE SPRINKLER SYSTEM IS YELLOW TAG. THERE ARE SEVERAL YELLOW TAGS ON THE FIRE SPRINKLER SYSTEM. CORRECT ALL YELLOW TAGS.
5831 | FIRE SPRIMKLER SYSTEM IS YELLOW TAG. FIRE SPRINKLER SYSTEM SHALL BE MAINTAINED IN AN OPERATIVE CONDITION AT ALL TIMES AND SHALL BE REPLACED OR REPAIRED WHERE DEFECTIVE. THERE ARE 7 RISERS THAT HAVE SEVERAL YELLOW TAGS.
5832 | Please contact the HPC office @ 832-394-8811 for any questions you may have regarding these expired permits.
5833 | NoData
5834 | Fire extinguishers due for annual inspection.
5835 | Fire alarm system due for annual inspection.
5836 | Place sign indicating location of fire alarm panel.
5837 | Fire extinguishers need servicing. Some fire extinguishers are missing.
5838 | NoData
5839 | Jolie Shay
5840 | FIRE SPRINKLER SYSTEM IS YELLOW TAG. THERE ARE SEVERAL YELLOW TAGS ON THE FIRE SPRINKLER SYSTEM. CORRECT ALL YELLOW TAGS.
5841 | FIRE SPRIMKLER SYSTEM IS YELLOW TAG. FIRE SPRINKLER SYSTEM SHALL BE MAINTAINED IN AN OPERATIVE CONDITION AT ALL TIMES AND SHALL BE REPLACED OR REPAIRED WHERE DEFECTIVE. THERE ARE 7 RISERS THAT HAVE SEVERAL YELLOW TAGS.
5842 | CITATIONS WILL BE ISSUED WHEN ALL OTHER EFFORTS TO GAIN VOLUNATRY COMPLIANCE.
5843 | NoData
5844 | NoData
5845 | NoData
5846 | NoData
5847 | NoData
5848 | Replace any electrical box covers that are missing.
5849 | repair sheet rock inside boiler and storage rooms.
5850 | The first 2 access gates needs a hydrant sign that reads HFD 0.
5851 | Certificate of occupancy needs to be up dated to show the office and 14 units
5852 | Directory sign needed for property at each access onto property.
5853 | email sent to manager with instructions on automatic gate installations.
5854 | NoData
5855 | NoData
5856 | NoData
5857 | NoData
5858 | NoData
5859 | NoData
5860 | NoData
5861 | NoData
5862 | NoData
5863 | NoData
5864 | NoData
5865 | NoData
5866 | NoData
5867 | Labels missing on fuses in electrical box in electrical room
5868 | Tenant is using BBQ pit on balcony
5869 | Exit sign broken in front door
5870 | Building over capacity
5871 | Labels missing on fuses in electrical box in electrical room
5872 | Tenant is using BBQ pit on balcony
5873 | Building over capacity
5874 | NoData
5875 | NoData
5876 | NoData
5877 | NoData
5878 | FIRE DETECTION, ALARM AND EXTINGUISHING SYSTEMS SHALL BE MAINTAINED IN AN OPERATIVE CONDITION AT ALL TIMES,AND SHALL BE REPLACED OR REPAIRED WHERE DEFECTIVE. THE FIRE PROTECTION SPRINKLER SYSTEM SHALL BE TESTEDANNUALLY BY A LICENSED COMPANY AND ALL TROUBLE (YELLOW) TAG(S) SHALL BE REMOVED AND ACCEPTABLE (WHITE) SERVICE TAG(S)SHALL BE AFFIXED TO ENSURE SYSTEM IS MAINTAINED IN OPERATIVE CONDITION.COMPLIANCE WITHIN14 DAYS
5879 | NoData
5880 | NoData
5881 | NoData
5882 | NoData
5883 | NoData
5884 | NoData
5885 | NoData
5886 | NoData
5887 | NoData
5888 | NoData
5889 | NoData
5890 | NoData
5891 | NoData
5892 | NoData
5893 | NoData
5894 | NoData
5895 | NoData
5896 | NoData
5897 | NoData
5898 | NoData
5899 | NoData
5900 | NoData
5901 | NoData
5902 | NoData
5903 | NoData
5904 | NoData
5905 | NoData
5906 | NoData
5907 | NoData
5908 | NoData
5909 | NoData
5910 | NoData
5911 | NoData
5912 | NoData
5913 | NoData
5914 | NoData
5915 | NoData
5916 | NoData
5917 | NoData
5918 | NoData
5919 | NoData
5920 | NoData
5921 | NoData
5922 | There must be an emergency lighting test performed on all emergency lights.
5923 | All fire extinguishers must be serviced and have a current service tag.
5924 | The fire alarm permit must be renewed.
5925 | NoData
5926 | NoData
5927 | NoData
5928 | Compliance: 30 calendar days.
5929 | Arrived on scene to find the fire alarm and sprinkler system red tagged as of January 2021.I issued 72 hours Notice to have both fire systems returned to compliance or to provide a plan of action. I notified management to initiate a 24 hours fire watch of the entire complex until the fire systems are returned to compliance status.Visited location on 2/8/2021 to find fire alarm panel had been replaced. A white service tag is attached dated 2/6/2021 replacing the red tag dated 11/25/2020.
5930 | NoData
5931 | NoData
5932 | NoData
5933 | Fire protection systems shall be maintained in accordance with the original installation standards for that system.
5934 | NoData
5935 | NoData
5936 | Vegetation blocking complete access to the Fire Hydrant. Must have 3 feet of clearance around the whole fire hydrant.
5937 | NoData
5938 | NoData
5939 | NoData
5940 | NoData
5941 | NoData
5942 | Red tag on elevator recall and panel will not reset
5943 | NoData
5944 | NoData
5945 | #NAME?
5946 | NoData
5947 | 109.2 Owner/occupant responsibility. Correction and abatement of violations of this code shall be the responsibility of the owner. If an occupant creates, or allows to be created, hazardous conditions in violation of this code, the occupant shall be held responsible for the abatement of such hazardous conditions.
5948 | 506.1 Where required. Where access to or within a structure or an area is restricted because of secured openings or where immediate access is necessary for life-saving or fire-fighting purposes, the fire code official is authorized to require a key box or a fire depository box to be installed in an approved location. The key box shall be of an approved type listed in accordance with UL 1037, and shall contain keys to gain necessary access as required by the fire code official. Key boxes shall be provided in accordance with Houston Fire Department LSB Standard No. 05, “Key Boxes.”
5949 | 703.4 Testing. Horizontal and vertical sliding and rolling fire doors shall be inspected and tested annually to confirm proper operation and full closure. Fire doors, fire dampers, and other similar equipment shall be inspected and tested in accordance with Houston Fire Department LSB Standard No. 02, “Inspection and Testing of Fire Protection and Life-Safety Equipment.” A written record shall be maintained and be available to the fire code official.Compliance: 30 calendar days.
5950 | 3205.4 Aisle maintenance. When restocking is not being conducted, aisles shall be kept clear of storage, waste material and debris. Fire department access doors, aisles and exit doors shall not be obstructed. During restocking operations using manual stocking methods, a minimum unobstructed aisle width of 24 inches (610 mm) shall be maintained in 48-inch (1219 mm) or smaller aisles, and a minimum unobstructed aisle width of one-half of the required aisle width shall be maintained in aisles greater than 48 inches (1219 mm). During mechanical stocking operations, a minimum unobstructed aisle width of 44 inches (1118 mm) shall be maintained in accordance with Section 3206.9.Compliance: 30 calendar days.
5951 | 3201.3 Construction documents. At the time of building permit application for new structures designed to accommodate high-piled storage or for requesting a change of occupancy/use, and at the time of application for a storage permit, plans and specifications shall be submitted for review and approval. In addition to the information required by the International Building Code, the storage permit submittal shall include the information specified in this section. Following approval of the plans, a copy of the approved plans shall be maintained on the premises in an approved location.Compliance: 30 calendar days.
5952 | 304.3.3 Capacity exceeding 1.5 cubic yards. Dumpsters and containers with an individual capacity between 1.5 cubic yards [40.5 cubic feet (1.15 m3)] and 15 cubic yards (405 cubic feet) (12 m3) or more shall not be stored in buildings or placed within 5 feet (1524 mm) of combustible walls, metal walls, building openings or combustible roof eave lines. Dumpsters and containers 15 cubic yards (405 cubic feet) (12 m3) capacity, or more, shall be a minimum of 10 feet (3 m) from combustible walls, metal walls, building openings, or roof eave lines. Dumpsters and containers shall not be placed on public sidewalks, streets, or other public property. No rubbish or combustible waste shall be placed, stored, or allowed to accumulate outside of dumpsters or containers. Lids of dumpsters shall be kept closed at all times.Compliance: 30 calendar days.
5953 | F/A panel has been repaired. F/A panel has a white service tag dated 1/6/2021 replacing red tag dated 1/5/2021.
5954 | NoData
5955 | NoData
5956 | No violations at this time.
5957 | INFORMATION
5958 | INFORMATION
5959 | INFORMATION
5960 | EXPIRED P2 PERMIT
5961 | EXPIRED P2 PERMIT
5962 | EXPIRED K1 PERMIT
5963 | NoData
5964 | NoData
5965 | NoData
5966 | NoData
5967 | FAILURE TO SERVICE FIRE EXTINGUISHERS 8-18 LAST DATE
5968 | NoData
5969 | 8-18 Last date . NEED SERVICING
5970 | NoData
5971 | NoData
5972 | NoData
5973 | Fire Alarm panels do not have the required tags:Initial Installation TagInstallation CertificateAnnual Inspection Tag
5974 | FDS signs do not have the required information.
5975 | Obtain an Access Gate PermitSubmit Plans to Inspector Arnt 713-503-5949
5976 | Post the maximum occupant load on all areas of Assembly.
5977 | Fire Sprinklers Do not have Current Tags:Annual TagSprinkler Data Plate is missing
5978 | Fire Extinguishers are out of date or missing annual tag.
5979 | Install Key Boxes on all secured exterior exits/entrances and place access keys/fobs in the boxes.
5980 | Place a Fire Depository Box as required by LSB #6Place all required information and keys in the Fire Depository Box as per LSB #6
5981 | Obtain a Key Box/Fire Depository Box Permit
5982 | Maintain and Update the Building File Check List. Comply with all required tests as they come due.
5983 | NoData
5984 | Obtain a P2 Places of Assembly Permit for the assembly places in excess of 49 maximum occupant load.
5985 | NoData
5986 | NoData
5987 | NoData
5988 | Must have a current annual inspection tag from a licensed fire protection company.
5989 | Must mount 1- 2A, 20B;C rated fire extinguisher near the cutting and welding rigs. Mount 1-2A, 10B;C rated fire extinguisher on the far west side of the structure. Must mount 1- 4A, 40B;C rated fire extinguisher on the paint booth side of the structure.
5990 | Must obtain a Spraying or dipping(S1) permit from the City of Houston Permitting Center.
5991 | It is the responsibility of the owner/occupant to correct all fire code violations, obtain any Certificates, and purchase all fire permits listed in this inspection report.
5992 | Must have a Licensed Fire Protection equipment company Inspect, test, and tag the spray booth at least every six months for correct operation.
5993 | Must mount 1- 2A, 20B;C rated fire extinguisher near the cutting and welding rigs. Mount 1-2A, 10B;C rated fire extinguisher on the far west side of the structure. Must mount 1- 4A, 40B;C rated fire extinguisher on the paint booth side of the structure.
5994 | Must mount 1- 2A, 20B;C rated fire extinguisher near the cutting and welding rigs. Mount 1-2A, 10B;C rated fire extinguisher on the far west side of the structure. Must mount 1- 4A, 40B;C rated fire extinguisher on the paint booth side of the structure.
5995 | NoData
5996 | NoData
5997 | NoData
5998 | NoData
5999 | NoData
6000 | NoData
6001 | Maintain minimum clearance from ceilings in storage rooms.
6002 | Discontinue storage in Mechanical Room.
6003 | All Compressed Gas cylinders must be immediately secured to the wall by chain.
6004 | Maintain clear access to Fire Alarm Panel Room at all times.
6005 | Provide current Fire/Alarm permit:Permit# is HFD17030759 issued 8/7/2019 and document presented was expired.Provide current C7 permit:Project# is 13079997 and document presented expired 8/8/2020
6006 | Repair ASAP.
6007 | Make sure all evacuation maps are room specific.
6008 | NoData
6009 | NoData
6010 | NoData
6011 | NoData
6012 | NoData
6013 | The building or structure shall not be occupied till a Certificate of Occupancy is issued to the business. The fire code official, with the joint approval of the building official, is authorized to permit the temporary occupancy of a building, or portion thereof, when standby personnel is provided.
6014 | The owner/occupant has the responsibility of correcting or abating all fire code violations or hazards that occur in the business.
6015 | Standby personnel is required when a TCO(temporary certificate of occupancy) is issued to the building/business. Failure to be in compliance will led to citations being issued.
6016 | The kitchen suppression system must be serviced, when completed make sure that it has a current service tag marked acceptable(not yellow or red). The kitchen suppression system should be serviced every 6 months.
6017 | Always renew or apply for permits that are required for the business at the City of Houston Fire Permit Office. All be permits are to be obtained prior to engaging in any activities, operations, practices, or functions regulated by this fire code.(any required permits for the business like Standby, P2, C1, & L5 permits, etc.)
6018 | There shall be no smoking inside the business as stated by the City of Houston, Texas, Ordinance No. 2006-1054 ( Ordinance ).
6019 | As per the fire code, all cooking should be separated from other tents/ canopies by a minimum of 20 feet of the structure/business.
6020 | No smoking in areas where "No Smoking" signs are posted, this includes any type of tobacco use(also hookah type smoking devices).
6021 | The decorative materials hanging on the walls(leafs) must be made of a fire retardant material. Proof must be provided to show that those items are fire resistance.
6022 | Clean kitchen vent hoods at intervals to prevent the accumulation of grease build up, records shall be kept to provide time and date of cleaning. (every 90 days)
6023 | Post no smoking signs inside the bar sitting area of the business(a total of 4 signs needed).
6024 | The portable fire extinguishers need to be serviced, 1 by the office and 2 at the outside patio area. Make sure that they all have a current service tag marked approved.
6025 | Make sure that all LPG cylinders are placed outside of the business, secured inside a metal cage or cabinet.
6026 | Always maintain approved occupancy of a building as stated on the certificate of occupancy. Failure to do so will result with the event/business to be stopped until such conditions are corrected with the possibility of citations being issued.
6027 | Install the required fire alarm panel and sprinkler system for the business. When completed make sure that it has an up to date service tag marked acceptable.(not yellow or red)
6028 | NoData
6029 | NoData
6030 | NoData
6031 | NoData
6032 | NoData
6033 | NoData
6034 | NoData
6035 | NoData
6036 | NoData
6037 | NoData
6038 | NoData
6039 | DOCUMENTATION OF THE WEEKLY RUN CHECKS OVER THE LAST 12 MONTHS MUST BE PROVIDED FOR THE FILE (COMPLIANCE DATE: NOV 7, 2019)
6040 | NOTIFICATION OF INOPERABLE (RED TAGGED) SYSTEMS MUST BE MADE TO THE FIRE MARSHALL'S OFFICE WIHTIN 24 HOURS. ANY FUTURE INSPECTIONS IDENTIFYING INOPERABLE ALARM/EXTIGUISHING SYSTEMS MUST BE MADE APPROPRIATELY. (FOR REFERENCE)
6041 | A REPORT FOR THE ANNUAL INSPECTION OF THE FIRE ALARM SYSTEM FOR PLANT 3 MUST BE PROVIDED TO THE FIRE MARSHAL'S OFFICE UPON RECEIPT BY NOV TUBOSCOPE. ALL DEFICIENCIES NOTED ON THE ANNUAL INSPECTION THAT IS IN PROGRESS AT THIS TIME MUST BE CORRECTED (COMPLIANCE DATE: WITHIN 30 DAYS OF NOTIFICATION)
6042 | THE REQUIRED TESTING MUST BE COMPLETED AND ANY DEFICIENCIES FOUND MUST BE CORRECTED. (COMPLIANCE DATE: NOV 7, 2019)
6043 | THE LOAD TEST ON THE GENERATOR MUST BE PERFORMED AND THE REPORT PROVIDED FOR THE FILE. NOTE: THIS TEST IS TO BE PERFORMED ANNUALLY (COMPLIANCE DATE: NOV 7, 2019)
6044 | ALL DEFICIENCIES NOTED ON WESTERN STATES FIRE PROTECTION REPORT DATED 9/3/2019 MUST BE REPAIRED OR REPLACED AND THE SYSTEM MAINTAINED IN OPERATIONAL READINESS STATUS. COMPLIANCE DATE: NOV 7,2019)
6045 | A TEST OF THE FIRE DEPARTMENT CONNECTION FOR BUILDING 3-700 MUST BE COMPLETED ONCE WATER HAS BEEN RESTORED. ANY DEFICIENCIES NOTED MUST BE CORRECTED IMMEDIATELY (COMPLIANCE DATE: WITHIN 30 DAYS OF WATER BEING RESTORED)
6046 | (FOR REFERENCE)
6047 | APPROVED PLANS BY THE CITY OF HOUSTON ARE ON SITE (FOR REFERENCE)
6048 | (FOR REFERENCE)
6049 | (FOR REFERENCE)
6050 | IDENTIFICATION FOR ALL PIPING FROM THE ABOVE GROUND STORAGE TANKS AND WITHIN THE BUILDING MUST BE LABELED WITH THEIR CONTENTS AND DIRECTIONAL ARROWS SHALL BE INCLUDED ON ALL PIPING WITH THE DIRECTION OF FLOW REFERENCE ASME 13.1 SHUT OFF VALVES MUST HAVE SIGNAGE TO CLEARLY INDICATE THEIR LOCATION AND EACH VALVE LABELED BY THE CONTENTS (COMPLIANCE DATE: NOV 7, 2019)
6051 | REPAIR OR REPLANCE ALL DIFICIENCIES ASSOCIATED WITH THE CLASS 1 DIV 1 ELECTRICAL IN THE BUILDING. (COMPLIANCE DATE: NOV 7 2019)
6052 | THE FIRE SPRINKLER SYSTEM REQUIRED FOR BUILDING 3-700 MUST BE OF AN "EXTRA HAZARD" DESIGN AND NOT A "PIPE SCHEDULE". THE SYSTEM SHOULD BE CAPABLE OF PROVIDING A DESIGN DENSITY OF 0.40 gpm/ft2 OVER A DESIGN AREA OF 2,500 sqft IN ACCORDANCE WITH NFPA 13. AN UPGRADE TO THE EXISTING AUTOMATIC SPRINKLER SYSTEM WAS IDENTIFIED IN THE CORRECTIVE ACTION PLAN IN 2010. A HYDRAULIC PLATE HAS NOT BEEN INSTALLED ON THE RISER PROVIDE THE HYDRAULIC CALCULATIONS TO THE IMPROVED SYSTEM THAT MEETS THE DESIGN DENSITY AS REFERENCED ABOVE AND INSTALL A HYDRO PLATE ON THE RISER WITH THE PROPER INFORMATION (COMPLIANCE DATE: 7 CALENDAR DAYS, OCT 16, 2019)
6053 | A STANDBY IS REQUESTED FOR THE FOLLOWING: - DUE TO THE THREAT TO HUMAN LIFE AND THE ENVIORNMENT THIS FACILTIY POSES AS A HAZARDOUS MATERIALS SITE (H2) - CONTINUED OPERATIONS AND USE OF BUILDING 3-700 WITH AN INOPERABLE FIRE PROTECTION AND MONITORING NOTIFICATION SYSTEMS. - FOR THE 'UNSAFE CONDITIONS' IDENTIFIED DURING THE INSPECTION LISTED ABOVE (FOR REFERENCE)
6054 | A 704 PLACARD MUST BE PLACED AT EACH ENTRANCE IDENTIFYING THE USE OF THE BUILDING - THE IDENTIFIERS USED SHOULD MATCH THAT OF THE MOST HAZARDOUS IN EACH CATEGORY WITHIN THE BUILDING - THIS WAS IDENTIFIED ON THE TECHNICAL REPORT IN 2007 AND NOT COMPLETED EACH TANK WITHIN THE BUILDING SHALL BE LABELED WITH THE CHEMICAL(S) CONTAINED WITHIN AND A 704 PLACARD (COMPLIANCE DATE: NOV 7, 2019)
6055 | AN UPDATED HMIS, HAZMAT ROUTING FORM AND HAZARDOUS MATERIALS SUMMARY SHEET MUST BE COMPLETED FOR BUILDING 3-700 AND SUBMITTED FOR REVIEW THESE ITEMS ARE ALL ATTACHED IN THE HAZARDOUS MATERIALS PACKET (COMPLIANCE DATE: NOV 7, 2019)
6056 | TRAINING FOR PERSONNEL AND PROPER "NO STORAGE" SIGNAGE MUST BE INSTALLED TO PREVENT THE USE OF LPG FORK LIFTS AND THE STORAGE OF HIGH HAZARD COMMODITY WITHIN THE BUILDING. - REMOVE PALLETS STORED UNDER THE MEZZANINE IMMEDIATELY - REMOVE AND DISCONTINUE THE USE OF LPG FORK LIFTS INSIDE THE BUILDING. (COMPLIANCE DATE: IMMEDIATELY)
6057 | (FOR REFERENCE)
6058 | (FOR REFERENCE)
6059 | (FOR REFERENCE)
6060 | AN UPDATED ACTION PLAN SUBMITTED BY PDG ARCHITECTS REGARDING NOV TUBOSCOPE'S CORRECTIVE ACTIONS TO BRING BLDG 3-700 (AN H2 FACILITY) INTO COMPLIANCE WAS FILED ON 7/5/2011. REQUIREMENTS IDENTIFIED BY FIRE PROTECTION ENGINEER ED COPE'S TECHNICAL REPORT DATED JULY 5, 2007, WAS TO HAVE BEEN COMPLETED BY MAY 2012 PER NOV TUBOSCOPE'S ACTION PLAN. THERE HAS BEEN AN 8 YEAR LAPSE IN THE COMPLETION OF WORK REQUIRED AND THE CERTIFICATE OF OCCUPANCY ISSUED FOR THIS BUILDING TO DATE 10/2019). AN APPLICATION MUST BE FILED WITH THE CITY OF HOUSTON FOR THE PROPER INSPECTIONS TO BE COMPLETED AND THE ISSUANCE OF A CERTIFICATE OF OCCUPANCY FOR BUILDING 3-700 (COMPLIANCE DATE FOR THIS APPLICATION: 15 CALENDAR DAYS - NOV 24, 2019)
6061 | NoData
6062 | LOCK AND LATCH HANDLES MUST BE REMOVED AND PANIC OR FIRE EXIT HARDWARE MUST BE INSTALLED PER CODE FOR THE H2 BUILDING 3-700 (COMPLIANCE DATE: NOV 7, 2019)
6063 | THE ABOVE GROUND STORAGE TANKS AND PIPING FOUND TO HAVE CORRODED AREAS DURING INSPECTION/TESTING MUST HAVE THE SECTIONS REPAIRED OR REPLACED. (COMPLIANCE DATE: NOV 7, 2019)
6064 | IT IS THE RESPONSIBILITY OF NOV TUBOSCOPE TO CREATE A MAINTENANCE SCHEDULE THAT ENSURES ALL FIRE AND LIFE SAFETY EQUIPMENT IS SERVICED AND TESTED ACCORDING TO LOCAL, STATE AND FEDERAL REGULATIONS THE REQUIRED MAINTENANCE SCHEDULES HAVE NOT BEEN MET AND HAVE SHOWN TO BE SEVERELY DEFICIENT PROVIDE A MAINTENANE SCHEDULE FOR ALL OF THE FOLLOWING: - ALARM SYSTEM - EXTINGUISHING SYSTEM - GAS DETECTION SYSTEM - TANK/PIPING SYSTEM (PER MANUFACTORER) (COMPLIANCE DATE: NOV 7, 2019)
6065 | (FOR REFERENCE)
6066 | 704 PLACARDS ON ABOVE GROUND TANKS SHALL BE 12" CHEMICALS IDENTIFIED FOR EACH TANK WITHIN THE BUILDING SHALL BE NO LESS THAN 6" WITH .5 IN WIDTH
6067 | THE EXTERIOR CANOPIED AREA (APPROX 200 SQFT) IS CURRENTLY NOT SPRINKLERED AND LOCATED APPROX 5' FROM THE EXIT OF THE WEST SIDE OF THE BUILDING. APPROVED PLANS IN 2010 INDICATE A DRY ANTI-FREEZE SYSTEM WAS TO BE INSTALLED. THIS WORK HAS NOT BEEN COMPLETED. ALL CONTENTS MUST BE REMOVED FROM UNDER THIS CANOPY AND STORED IN A REMOTE AREA WITH PROPER SEPARATION DISTANCES, PILE VOLUMES AND CONTAINMENT AS IDENTIFIED IN THE TECHNICAL REPORT IN 2007. (COMPLIANCE DATE: NOV 7, 2019)
6068 | PROVIDE A COPY OF THE MOST RECENT TIER II REPORT FOR THE FILE (COMPLIANCE DATE: IMMEDIATELY)
6069 | (FOR REFERENCE)
6070 | ALL EMERGENCY LIGHTING MUST BE TESTED AS REQUIRED BY THE HOUSTON FIRE STANDARDS AND THE REPORT PROVIDED FOR THE FILE. (COMPLIANCE DATE: NOV 7,2019)
6071 | TO FOLLOWING ISSUES IDENTIFIED DURING THE GENERAL INSPECTION 10/3/2019 ARE DEEMED 'UNSAFE CONDITIONS' PER CODE: 1. IMPROPER OCCUPANCY - A CERTIFICATE OF OCCUPANCY OR TEMPORARY CERTIFICATE OF OCCUPANCY HAS NOT BEEN ISSUED FOR BUILDING 3-700 2. IMPROPER MAINTENANCE OF FIRE AND LIFE SAFETY EQUIPMENT - ANNUAL/QUARTERLY INSPECTIONS OF THE FIRE ALARM SYSTEM HAVE NOT BEEN COMPLETED SINCE THE INSTALL OF "PLANT 3 FACP" IN 2015. - ANNUAL VAPOR/GAS DETECTION CALIBRATION TESTS HAVE NOT BEEN PROVIDED SINCE THE INSTALL OF THE SYSTEM IN 2015 - ANNUAL/QUARTERLY/5 YEAR INSPECTIONS OF THE EXTINGUISHMENT SYSTEM HAVE NOT BEEN COMPLETED - THE EXTINGUISHMENT SYSTEM IS CURRENTLY RED TAGGED (9/3/2019) WATER IS NOT BEING PROVIDED TO THE SYSTEM IT APPEARS THIS ISSUE BEGAN 2 YEARS AGO WITH THE INSTALL OF A 12" WATER LINE DOWN HOLMES ROAD. - ANNUAL LOAD TESTS FOR BACKUP POWER NOT COMPLETE - CLASS 1 - DIV 1 ELECTRICAL IN NEED OF REPAIR IN THE BUILDING - THE USE OF NON-APPROVED LPG FORK LIFT (PARKED) IN THE BUILDING - STORAGE OF FLAMMABLE LIQUID DRUMS ABOVE 6' ON THE MAZZANINE AND IDLE WOOD PALLETS STORED BENEATH THEM AND WITHIN 2' OF MEZZANINE EGRESS (THERE IS TO BE NO STORAGE IN THE BUILDING PER FPE TECHNICAL REPORT) PICTURES ATTACHED (FOR REFERENCE)
6072 | A 911 KEY BOX MUST BE INSTALLED AT THE ENTRANCE TO BUILDING 3-700 WITH THE KEY TO ACCESS THE BUILDING PROVIDED WITHIN. (COMPLIANCE DATE: NOV 7, 2019)
6073 | A reinspection fee has been assessed for the failure to maintain corrosion on the AST piping and complete the required labels with direction of flow on the exterior and interior of the building.A reinspection for Feb 9th, at 10am is scheduled. A citation will be issued if the work is not complete. This citation is not written to the company but to the person in charge of abating this violation.
6074 | NoData
6075 | Emergency contact information is needed.
6076 | Update mobility impairment list every 6 months.
6077 | Not able to communicate
6078 | Provide compliance letters
6079 | NoData
6080 | Permit has expired and requires renewing.
6081 | Repair ASAP.
6082 | NoData
6083 | A compressed gas permit is required for storage/use of oxygen in amounts greater than 504 cubic ft. Obtain permit at the Houston Permitting Center.
6084 | NoData
6085 | NoData
6086 | NoData
6087 | NoData
6088 | CITATIONS CAN BE ISSUED IF COMPLIANCE IS NOT OBTAINED.
6089 | IT IS THE OWNER/OCCUPANTS RESPONSIBILITY TO CORRECT VIOLATIONS.
6090 | THE FOLLOWING PERMITS NEED TO BE RENEWED FOR 2018: L1 - LIQUID GAS K1 - KEY/FIRE DEPOSITORY BOX H3 - HOT WORKS OPERATIONS C8 - COMPRESS GAS NON FLAM C7 - COMPRESS GAS A4 - ACCESS GATES IF ANY CHANGES HAVE OCCURED IN THE FACILITY AND IT IS DETERMINED A PERMIT IS NO LONGER NEEDED, CONTACT FIRE INSPECTOR JEREMY SMITH. SEE CONTACT INFORMATION ON PAGE ONE
6091 | POST NEW PERMITS ONCE RECEIVED.
6092 | REINSPECTION FEES CAN BE APPLIED IF VIOLATIONS ARE NOT CORRECTED UPON FOLLOW UP INSPECTION.
6093 | This not a violation.
6094 | All NFPA 704 signage shall be replaced so that the Health, Fire, Reactivity, and Specific hazards are legible.Compliance: 30 calendar days.
6095 | Both the sprinkler riser and the fire alarm panel shall be inspected by a licensed fire alarm or sprinkler company. The yellow tags on both the fire pane and sprinkler risers shall be addressed immediately.Compliance: 30 calendar days.
6096 | All key boxes must have a key inside them to gain access to all HFD access doors at facility along with an appropriate lock to secure the box or a Knox box.Compliance: 30 calendar days.
6097 | This is not a violation.
6098 | All combustibles shall be removed from electrical service areas to the distances detailed in HFC 605.3. Remove all boxes and Helium tank away from electrical panel.Compliance: 30 calendar days.
6099 | NoData
6100 | Repair ASAP.
6101 | NoData
6102 | COMPLIANCE DATE: 15 CALENDAR DAYS
6103 | P2 fire prevention permit is expired at this time.
6104 | PERMITS HAVE EXPIRED ARE REQUIRE RENEWING.
6105 | A key box is required for the access gate.
6106 | COMPLIANCE DATE: 15 CALENDAR DAYS
6107 | F7 Fire Prevention permit is expired at this time
6108 | NoData
6109 | NoData
6110 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
6111 | Signs posted outside of doors.
6112 | NoData
6113 | Evacuation placard must be clear of obstruction first front window clear of all art work evac. placard only for display.
6114 | NoData
6115 | Obstructions to exit door need to be cleared.
6116 | NoData
6117 | NoData
6118 | Add numbers of address to building.
6119 | NoData
6120 | Proper permanent post and sign need to be added facing the street.
6121 | NoData
6122 | Need correct signage for these rooms.
6123 | Required unexpired permits need to be added to FMB. Old permits with old address need to be removed and current one added to new binder.
6124 | NoData
6125 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
6126 | NoData
6127 | No violations found.
6128 | NoData
6129 | NoData
6130 | Replace all recalled fire extinguishers in units.
6131 | NoData
6132 | SEE BUILDING DETAILS FOR FIRE AND LIFE SAFTY MAINTANCE DATES ATTACHMENTS WILL HAVE COPY OF THE HMIS FOR THIS BUILDINGNO VIOLATION FOUND
6133 | NoData
6134 | Access Gates toggle switch is not installed.
6135 | NoData
6136 | Access Gates are missing the required fail safe.
6137 | NoData
6138 | NoData
6139 | NoData
6140 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
6141 | Provide a copy of the Certificate of Occupancy to the code official. COMPLIANCE 30 DAYS.
6142 | 2012 IFC Section 5001.5.2 Hazardous Materials Inventory Statement (HMIS). Where required by the code official, an application for a permit shall include an HMIS, such as Superfund Amendments and Reauthorization Act of 1986 (SARA) Title III, Tier II Report or other approved statement. The HMIS shall include the following information: 1. Product Name. 2. Component. 3. Chemical Abstract Service (CAS) number. 4. Location where stored or used. 5. Container size. 6. Hazard classification. 7. Amount in storage. 8. Amount in use-closed systems. 9. Amount in use-open systems. COMPLIANCE 30 DAYS. Use the forms provided. Additional forms may be found at: http://houstontx.gov/fire/formsandpermits/index.html http://www.houstontx.gov/fire/business/hmisinstructions.pdf Based upon the amounts and classifications provided on the required HMIS, a supplemental Notice of Violation may be issued to require additional operational permits. THE FORM SUBMITTED SHALL SHOW THE PROPERTY ADDRESS, CONTROL AREA ID, PRINTED NAME OF THE PERSON SUBMITTING THE FORM AND THEIR SIGNATURE, AND DATE. IF THE BUILDING HAS MULTIPLE CONTROL AREAS THE FORMS SHALL SHOW THE AMOUNTS IN EACH CONTROL AREA. THE FORM, AS SUBMITTED, SHOWS AMOUNTS IN EXCESS OF THE MAQ FOR THE OCCUPANCY CLASSIFICATION AND COULD RESULT IN MOVING THIS OCCUPANCY TYPE TO AN H OCCUPANCY. COMPLIANCE 30 DAYS Status_____________Date________________Inspector's ILMS-ID_____________ 2012 IFC Section 3201.3 Construction documents. At the time of the building permit application for new structures designed to accommodate high-piled storage or for requesting a change of occupancy/use, and at the time of application for a storage permit, plans and specifications shall be submitted for review and approval. In addition to the information required for review by the International Building Code, the storage permit submittal shall include the information specified in this section. Following approval of the plans, a copy of the approved plans shall be maintained on the premises in an approved location. Provide a copy of the approved high-piled storage plans for the fire code official to review and complete the inspection process. These approved documents are required to be maintained on location for future inspections. The approved Department 180 plans should include the sprinkler details for the high-piled storage area. In those details it should include the height restrictions for the plastic storage bins noted during the inspection. After review of those details the storage bins shall be stored as described in the sprinkler details. COMPLIANCE 30 DAYS.
6143 | NoData
6144 | Please provide the correct key, to be placed in the 911 box for the master lock on the manual gate. (The first gate next to the exit gate facing Westview) Please repair the failsafe pull cable and piping on the exit gate facing Westview. Replace or Repair 911 box the cable is in.
6145 | NoData
6146 | Secure compressed gas cylinders.
6147 | The locked gate in the rear of the restaurant is required to be unlocked while the building is occupied. Replace hardware to open from egress side and lock from the outside if necessary.
6148 | NoData
6149 | NoData
6150 | NoData
6151 | NO VIOLATIONS FOUND
6152 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
6153 | NoData
6154 | NoData
6155 | NoData
6156 | NoData
6157 | NoData
6158 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
6159 | NoData
6160 | NoData
6161 | NoData
6162 | NoData
6163 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
6164 | Plans for the event have been submitted and approved for the Lonestar Volleyball Event in halls A and B.
6165 | George R Brown Currently has an assembly permit for events. ILMS project#5026247
6166 | George R Brown Currently has an assembly permit for events. ILMS project#5026247
6167 | NoData
6168 | Please renew the K1, key box permit.Expired 6/20/2019. Please renew the A4, access gate permit.Expired 3/1/2019.
6169 | NoData
6170 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
6171 | 911 Key Box permit (K1) has expired 11-4-19.Please renew permit in 10 days.
6172 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
6173 | NoData
6174 | Fire Drills must be conducted monthly and documentation must be made and located in the FMB
6175 | NoData
6176 | At no time should any exit path way be obsturcted. Attention to second floor area next to clinic. Please consult clinic that at no time block with large table the exit path way.
6177 | NoData
6178 | NoData
6179 | NoData
6180 | NoData
6181 | NoData
6182 | Emergency lighting must be tested annually and documented into the FMB
6183 | NoData
6184 | Need the documentation of the last test and placed in the FMB
6185 | New standard for key box needs to be serviced by updating the old 911 box with new Knox Box see attachment email with information.
6186 | See attachment information on Knox Box.
6187 | All areas not protected with fire stops in electrical and mechanical rooms must be protected from fire spread. Technical Assistance maybe needed for building code related material use.
6188 | NoData
6189 | NoData
6190 | A copy of the last updated test needs to be placed inside the FMB.
6191 | The last inspection with current date should be placed inside the FMB
6192 | Above doors need adjusting to close correctly
6193 | Permits should be made available in the FMB
6194 | Any alarm room of fire command room not identified should be marked outside the door stating the use of that room.
6195 | Should be made available in the FMB
6196 | All information on service, permits and fire drills must be in a FMB and made available on request to the Fire Marshalls Office.
6197 | Permits should be made available in the FMB
6198 | Please renew permits (A4) Access Gate/ (K1) Key Box. Both expired 12-12-20.
6199 | NoData
6200 | AISLES WIDTHS STATED ON THE APPROVED PLANS ARE NOT BEING MAINTAINED AND SHALL BE BROUGHT INTO COMPLIANCE. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
6201 | USING THE FORMAT PROVIDED, A CURRENT HMIS STATEMENT SHALL BE SUBMITTED TO THE HAZMAT / HIGH-PILED 180 TEAM FOR REVIEW. THE HMIS FORM AND INSTRUCTIONS ON HOW TO FILL OUT THE FORM CAN BE FOUND AT THE CITY OF HOUSTON WEBSITE: HTTP://WWW.HOUSTONTX.GOV/FIRE/FORMS/HMIS CORRECTLY FILL OUT A NEW HMIS FOR ALL HAZARDOUS MATERIALS STORED INSIDE THE BUILDING. THE WAREHOUSE AREA AND THE HAZARDOUS MATERIALS STORAGE ROOM REQUIRE SEPARATE HMIS'S. THE CLASSIFICATION OF THE HAZARDOUS MATERIALS SHALL COMPLY WITH THE 2012 INTERNATIONAL FIRE CODE CLASSIFICATIONS SYSTEM. IT IS HIGHLY ADVISABLE TO SEEK TECHNICAL ASSISTANCE IN CORRECTLY COMPLETING THE HMIS FOR THE HAZARDOUS MATERIAL BEING STORED ON THE FACILITY. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
6202 | ALL STANDPIPE SYSTEMS SHALL BE INSPECTED, TESTED AND SERVICED IN ACCORDANCE WITH THE REQUIREMENTS OF THIS SECTION, NFPA 25 AND HFD LSB STANDARD NO. 02. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
6203 | NO LPG GAS STORED INSIDE BUILDING. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
6204 | NoData
6205 | Repair (2) Exit Signs
6206 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
6207 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
6208 | Provide documentation/report for fire damper testing and any necessary repairs.
6209 | Inspect and Service tag commercial kitchen hood system. Correct all red tag impairments immediately.
6210 | Repaint Fire Lane throughout School
6211 | Provide certificate of flame resistance for hanging Flags.
6212 | Provide Boiler Permits (7 Expired)
6213 | Provide Elevator Permits: Wheelchair Lift, 2 HP
6214 | Provide updated permits on site: Fire Alarm, Hot Works
6215 | Please renew Permits (A4) Access Gate and (K1) 911 Key Box. Both expired 12-11-20.
6216 | Please renew the A4, access gate permit.Expired 3/1/2019.
6217 | Please renew your expired access gate (a4) permit permit expired on 01/25/2021.
6218 | Please renew your Key box & access gate permits that expired on 03/04/2020. If you have any questions regarding these expired permits, please contact the HPC office at 832-394-8811.
6219 | NoData
6220 | NoData
6221 | Have a licensed fire protection company service and tag the fire extinguishers.
6222 | NoData
6223 | Your key box (k1) and high piled storage (h2) fire permits expired on 1-24-2021.Renew these permits from the options listed on this form by the date listed.Total amount due is $681.82
6224 | NoData
6225 | The Fire Alarm Panel located at 7777 SW Freeway has been tagged yellow. Immediate compliance is required. Once the corrections have been completed please forward to me a letter from the servicing company confirming that compliance has been achieved. Also include a picture of the fire alarm panel with the white correction tag (front and rear of the tag).
6226 | The permit amount for oxidizing gas is &gt;504 cu. ft. on site. With 4 "H" bottles (2 oxygen, 2 nitrous) on site of min. 240 cu. ft. each, a C7: Compressed Gas permit must be obtained and posted on site. Permits may be obtained at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811www.houstonpermittingcenter.orgCompliance is required within 2 weeks: 2/24/2021
6227 | NoData
6228 | FireTron notified my office of Yellow Tag violations. After speaking with Anthony Madison this was verified. Immediate compliance is required. Once compliance has been achieved, email me a letter of compliance from the state certified company hired to correct the issues.
6229 | Repair ASAP.
6230 | NoData
6231 | NoData
6232 | NoData
6233 | NoData
6234 | NoData
6235 | NoData
6236 | NoData
6237 | NoData
6238 | Vent hoods are due for cleaning before the end of 12/2020.
6239 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
6240 | The class K fire extinguisher lost pressure.
6241 | NoData
6242 | NoData
6243 | NoData
6244 | NoData
6245 | Have a licensed fire protection company service and tag the fire extinguishers.
6246 | Have a licensed fire protection company service and tag the vent hood suppression system. The vent hood requires professional cleaning.
6247 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
6248 | Repair the emergency illumination on the exit sign located on the rear exit.
6249 | Post the occupant load.
6250 | NoData
6251 | NoData
6252 | NoData
6253 | Repair ASAP.
6254 | Repair ASAP.
6255 | CURRENTLY NO SERVICE TAGS AT ABOVE LOCATIONS. HAVE FIRE PROTECTION COMPANY ADD MISSING TAGS TO ALL ABOVE LOCATIONS SHOWING PROOF OF ALL REQUIRED QUARTERLY/ANNUAL/5YR INSPECTIONS.
6256 | PLACE REQUIRED SIGNAGE ON OUTSIDE OF CONTAINER PER ABOVE CODE AT BOTH ENTRANCES. ALSO PLACE A LABEL "LITHIUM BATTERY STORAGE" AT SAME LOCATIONS.
6257 | ONLY PANIC HARDWARE IS ALLOWED, AND THEY SHALL BE ACCESSIBLE FROM THE EXTERIOR BY USE OF A KEY WHICH WILL BE LOCATED IN 911 KEYBOX. CURRENTLY AT LEAST ONE HFD DOOR HAS NO KEY OPENABLE LOCK FROM EXTERIOR SIDE - REPLACE WITH APPROVED LOCKING DEVICE.
6258 | PROVIDE LABELED KEYS TO THIS CONTAINER TO CODE OFFICIAL SO THAT THEY MAY BE PUT IN 911 KEYBOX
6259 | Remove all combustible from boiler and equipment room.
6260 | label all Electrical circuits and rooms
6261 | Repair open wiring in shop
6262 | Replace sheet rock boiler room
6263 | Get a building construction permit to fix your draft stop and fire wall
6264 | You need to get a 4x4 blue reflector to mark your fire hydrant
6265 | All building with gas coming in them need to be tested
6266 | You need boiler permits for all boilers
6267 | You need to place address numbers on all your doors.
6268 | Show tags to fire alarm and pull station test
6269 | some keys are missing out of your key boxes and one is broken​
6270 | need on entrance gate
6271 | some of your signs are missing facing street side need to be replaced
6272 | I need to see a technical report for you elevators
6273 | NoData
6274 | Information only.
6275 | Information only.
6276 | Gas test required every 5 years. Call your plumber and have gas test performed. Plumber must obtain permits from city. FYI: Last test was on 8/30/2013 project #13087409.
6277 | Information only.
6278 | Label boiler room doors.
6279 | Please renew the A4, access gate permit.Expired 6/25/2019.
6280 | NoData
6281 | NoData
6282 | Please renew 911 Key Box permit, expires 3-7-21.
6283 | NoData
6284 | Please Renew Public Assembly & Open Flames Candles permits within 10 Business days
6285 | All fire extinguishers must be mounted.Compliance within 30 days.
6286 | ALL MAG LOCKS SHALL HAVE A CITY OF HOUSTON TAG ATTACHED. PLANS SHALL BE SUBMITTED TO THE CITY FOR REVIEW AND APPROVAL FOR THESE MAG LOCKS.COMPLIANCE WITHIN 30 DAYS
6287 | Permit for keybox is required.Compliance within 30 days.
6288 | A copy of the HazMat Management Plan and HazMat Inventory Statement must be onsite at all times.Compliance within 30 days.
6289 | City approved and stamped plans must be onsite at all times. Permitting Office 1002 Washington Ave Houston, TX.Compliance within 30 days.
6290 | Key box must be easily accessible and operational with keys to access the gate and have access to enter the facility.Compliance within 30 days.
6291 | All combustible material must be removed 3ft away from electrical panels.Compliance within 30 days
6292 | All exits signs throughout the facility must be maintained and operational.Compliance within 30 days.
6293 | NoData
6294 | Renew p2, l1 permit at Houston Permitting Center, 1002 Washington (832.394.8811). Failure to renew will render a Re-inspection fee.
6295 | NoData
6296 | NoData
6297 | Provide signage, "Electrical Room", on or above the door where the Electrical Panels are located.
6298 | Have all Fire Extinguishers serviced, and provided with current service tags, annually.
6299 | Provide (2) additional, size 2A:10BC Fire Extinguishers, with service tags for the Patio areas.
6300 | Provide proper work space clearance around the Electrical Panel.
6301 | NoData
6302 | NoData
6303 | Stand by may be required
6304 | reg tag system
6305 | exit sign missing front door
6306 | NoData
6307 | NoData
6308 | The owner/occupant has the responsibility of correcting or abating all fire code violations or hazards that occur in the business.
6309 | Always maintain approved occupancy of a building as stated be the certificate of occupancy. Failure to do so will result with the event to be stopped until such conditions are corrected.
6310 | The kitchen suppression system must be serviced, when completed make sure that it has a current service tag marked acceptable(not yellow or red). The kitchen suppression system should be serviced every 6 months.
6311 | Clean kitchen vent hoods at intervals to prevent the accumulation of grease build up, records shall be kept to provide time and date of cleaning.(every 90 days)
6312 | The portable fire extinguisher needs to be serviced by the office, make sure it is has a current service tag.
6313 | Always renew or apply for permits that are required for the business at the City of Houston Fire Permit Office. All be permits are to be obtained prior to engaging in any activities, operations, practices, or functions regulated by this fire code.(any required permits for the business)
6314 | All issued permits shall be kept on the premises and readily available for inspection by the fire code official.
6315 | NoData
6316 | NoData
6317 | NoData
6318 | NoData
6319 | NoData
6320 | AS PER CODE
6321 | INFORMATION
6322 | INFORMATION
6323 | AS PER CODE, NOTHING ON DOORS
6324 | NoData
6325 | NoData
6326 | NoData
6327 | NoData
6328 | Mount the class K fire extinguisher located on the ground in the kitchen area.
6329 | Correct the yellow tagged sprinkler deficiencies.
6330 | Repair or replace the inoperable emergency illumination.
6331 | Report is including 9606, 9616, 9636 & 9680 Mesa
6332 | Correct yellow tagged Fire Sprinkler System dated 1/5/2021
6333 | NoData
6334 | Correct yellow tagged Fire Sprinkler System dated 1/5/2021
6335 | New and existing buildings and occupancies there under construction shall be provided with approved address numbers or letters. Each character shall be not less than 4 inches in height and not less than 0.5 inch in width. They shall be installed on a contrasting background and be plainly visible from the street or road fronting the property.
6336 | 5 year gas test is required for your place of business. This test must be performed by a licensed plumber of your choosing.
6337 | Before gas test is performed the plumber must pull a permit to perform the test.
6338 | Post occupant load sign near main exit.
6339 | Add sign to entry doors that reads, "These doors to remain unlocked during business hours". This sign shall face the inside of business to be read by employees.
6340 | NoData
6341 | NoData
6342 | Correct yellow tagged Fire Sprinkler System dated 1/5/2021
6343 | NoData
6344 | Correct yellow tagged Fire Sprinkler System dated 1/5/2021
6345 | NoData
6346 | NoData
6347 | NoData
6348 | NoData
6349 | NoData
6350 | NoData
6351 | The exit door in "Classroom B" does not open freely. Make the appropriate adjustments so that the door opens with a force of less than 15 pounds.
6352 | The vent hood in this occupancy is required to be inspected/serviced every 6 months. Have the vent inspected/serviced and ensure a current service tag is attached.
6353 | Throughout the occupancy are many single station battery operated smoke detectors/alarms. Replace the batteries in any smoke detectors that do not go into alarm when tested, or remove the smoke detector from the occupancy as the occupancy is protected by fire alarm system. Repair or replace any CO detectors found to the inoperable.
6354 | NoData
6355 | NoData
6356 | Provide Junction Box Cover for 5th floor equipment room and 1st floor Mechanical room.
6357 | NoData
6358 | Disregard - no violation at this time.
6359 | Reposition FDC Sign for visibility.
6360 | Throughout Equipment Rooms on Property.
6361 | Maintain accessibility to Fire Depository Box at all times.
6362 | Provide current Emergency Contact List and Mobility Impaired List for Fire Depository Box.
6363 | Provide Electrical/Mechanical Room sign for B1 Level.
6364 | 1) Stair "B" Electrical Pane - hole in Sheetrock. 2) Repair (cover) hole in floor in storage rooms on each floor, and repair ceiling sheetrock holes in same rooms.
6365 | Throughout Property.
6366 | Provide "A" and 'B" designation on floors 2 through 5. Reposition Signs adjacent to Elevator Call Button.
6367 | NoData
6368 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
6369 | NoData
6370 | NoData
6371 | NoData
6372 | NoData
6373 | NoData
6374 | P2 permit is expired. Expired on 12/10/2020. Amount owed for permit 266.80 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
6375 | Have all fire extinguishers inspected and tagged by a licensed fire protection equipment company.
6376 | All exit signs shall be illuminated at all times under primary power or by battery backup for 90 minutes if power loss happens.
6377 | Have all emergency illumination lights that are not working properly repaired or replaced.
6378 | Reapply for Certificate of Occupancy due to the expiration of the prior application.
6379 | Renew fire alarm permit. Current permit expired on 4-25-2020.
6380 | NoData
6381 | NoData
6382 | AS PER CODE
6383 | INFORMATION
6384 | INFORMATION
6385 | AS PER CODE, NOTHING ON DOORS
6386 | Have vent hoods cleaned by a professional cleaning service. Ensure date of cleaning sticker is placed on the vent hoods.
6387 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a gas test permit.
6388 | Repair or replace the inoperable emergency illumination on the exit signs.
6389 | Renew the fire prevention assembly permit before the end of 02/2021.
6390 | Ensure the second exit in the dining area is unlocked while the building is occupied.
6391 | The business shall go through the process of completing the automatic fire sprinkler system and ensuring it has been approved and in working order.
6392 | The installation of the fire alarm system is to be completed. The business shall submit plans for their fire alarm system for approval through the building department. The business shall also provide a plan of action including dates of plan submittal, installation, and final completion to the fire code official. The plan of action may be revised as necessary.
6393 | The business shall obtain a Certificate of Occupancy by application through the Building Department.
6394 | The building is not to be occupied or open to the public without a fire watch from HFD inspectors per the Fire Marshal. After plan submittal, installation, and an approved fire alarm system is in working order, the fire watch may be discontinued. At NO time shall the basement level of the building be occupied (even with fire watch) until the building has an approved fire alarm system, approved automatic fire sprinkler system, and the building has been issued a Certificate of Occupancy.
6395 | All fire extinguishers should be serviced and have a current service tag placed on them.
6396 | The fire alarm system should have an emergency lighting test performed on it.
6397 | The public assembly permit must be renewed.
6398 | 12/26/2020 - Blue, OK
6399 | 12/26/2020 - OK
6400 | 9/2020 - OK
6401 | Obstructed drills OK
6402 | Drills conducted and logged monthly - OK
6403 | 6/2019 - Have all portable fire extinguishers inspected.
6404 | Correct all violations within 60 calendar days.
6405 | 7/2/2019 - Have sprinkler system inspected and have any deficiencies corrected.
6406 | 2/4/2015 - Have 5 year hydrostatic test and internal inspection performed, and provide documentation that deficiencies were corrected.
6407 | Have dampers tested, provide report, and provide documentation that deficiencies were corrected.
6408 | Relocate propane cage that is currently placed in exit pathway outside welding class.
6409 | Conduct and document required annual fire safety training.
6410 | Remove all items blocking access to fire alarm panel in IT room.
6411 | 5/16/2019 - OK
6412 | Provide updated EOP for 20-21 school year.
6413 | Provide documentation of sensitivity report performed within the past five years and provide documentation that any deficiencies were corrected.
6414 | Boilers have never been registered with TDLR. Register boilers, have them inspected, and provide boiler certificates.
6415 | Expired 3/31/2020 - Renew elevator permit.
6416 | Have egress lighting tested and provide documentation that deficiencies were corrected.
6417 | NoData
6418 | NoData
6419 | Please keep all debris from inside all riser rooms. Also, check all heaters for proper operations.
6420 | Toggle switch located inside 911 box does not open electric swing gate.
6421 | NoData
6422 | NoData
6423 | NoData
6424 | NoData
6425 | PERMIT HAS EXPIRED AND REQUIRES RENEWING. PERMIT IS TIED TO AN ACCESS GATE. 911 BOX WILL NEED WIRING INTO THE GATE MOTOR FOR RAPPID ACCESS OF EMERGENCY PERSONNEL.
6426 | NoData
6427 | NoData
6428 | 9/28/2020 - Blue, OK
6429 | 6/18/2019 - OK
6430 | 7/11/2019 - Blue, OK
6431 | 6/13/2019 - OK
6432 | Obstructed drills OK
6433 | Drills conducted and logged monthly - OKDo not split fire drills into groups. All occupants must evacuate at the same time upon activation of the fire alarm.
6434 | 5/2019 - Have all portable fire extinguishers inspected.
6435 | Correct all violations within 60 calendar days.
6436 | 7/11/2019 - Have sprinkler system inspected and have deficiencies corrected.
6437 | 5/2020 - Have ANSUL system inspected.
6438 | Conduct and document required annual fire safety training.
6439 | 6/17/2019 - OK
6440 | Original FDC sign faded and illegible. This violation was listed on the last inspection report for this school, but was never corrected. Have new sign made and attached to building. Sign MUST include which portions of the building are served by the main (original) FDC.Recently added portion of building has its own FDC. Install sign that indicates which portions of building are served by new FDC (west end of building).
6441 | Place "Roof Access" sign on door to room 408. Sign must be PERMANENT.
6442 | 2/6/2020 - Multiple fails with not documentation of corrected.Have new egress lighting test performed and provide documentation that deficiencies were corrected.
6443 | Install panic hardware on all courtyard gates.
6444 | Immediately remove chains and padlocks from gates leading from BOTH courtyards.Prohibit future use of chains and padlocks on gates.Install panic hardware on all courtyard gates.
6445 | NoData
6446 | NoData
6447 | NoData
6448 | NoData
6449 | NoData
6450 | NoData
6451 | NoData
6452 | NoData
6453 | Have the existing fire extinguisher inspected by a Licensed Fire Suppression Company and a have a current tag affixed to the extinguisher.
6454 | Owner/Occupant is responsible for Obtaining Certificate of Occupancy, correcting all fire code violations, and purchasing necessary permits listed in this report. Apply for Occupancy by sending the building department the address needing Occupancy(1570 Telephone Rd) at this email address: occupancy.inspections@houstontx.gov
6455 | Place the open breaker in the electrical panel with a metal or plastic spacer and replace the missing switch plates throughout the business.
6456 | Remove all combustibles within 3 feet of the electrical panels.
6457 | Must purchase the Flammable/Combustible Liquid Storage and Use permit at the City of Houston Permitting Center. 1002 Washington Avenue. 2nd Floor
6458 | Must obtain and purchase F7 permit for the 300 gallon waste oil tank in the rear of the business.
6459 | NoData
6460 | NoData
6461 | FLAMMABLE LIQUIDS STORAGE SHALL COMPLY WITH THE ABOVE FIRE CODE
6462 | FLAMMABLE LIQUIDS STORAGE SHALL COMPLY WITH THE ABOVE FIRE CODE
6463 | FLAMMABLE LIQUIDS STORAGE SHALL COMPLY WITH THE ABOVE FIRE CODE
6464 | RELOCATE LP-G STORAGE OUT OF TRAILER TO EITHER OUTSIDE OF BUILDING OR INSIDE IF STORAGE COMPLIES WITH THE FIRE CODE REQUIREMENTS
6465 | GENERAL NOTE REGARDING TOTAL ALLOWED STORAGE QUANTITY OF LP-G STORAGE
6466 | CONTINUE TO STORE ALL EMPTY AND FULL LP-G CONTAINERS PER ABOVE FIRE CODE
6467 | GENERAL NOTE THAT EMPTY CONTAINERS COUNT AS FULL REGARDING STORAGE QUANTITIES
6468 | GENERAL NOTE FOR ANY STORAGE OF FLAM/COMB LIQUIDS IN THESE TYPE OF STORAGE CABINETS
6469 | MAXIMUM ALLOWABLE QUANTITY IS 120GAL FOR CLASS 1B/1C FLAMMABLES. YOU ARE STORING WELL OVER THAT. IF MOVED INSIDE THE WAREHOUSE, NOTE E OF TABLE 5003.1.1(1) APPLIES ALLOWING YOU 240GAL OF STORAGE MAX. REDUCE STORAGE WITHIN 30 DAYS TO BELOW MAQ.
6470 | SEE NOTE 2 - YOUR STORAGE OF FLAMMABLE LIQUIDS REQUIRES A PERMIT.
6471 | No violations at this time.
6472 | Please have American Fire System repair/correct red tag issues within 72 hours.
6473 | Mount all fire extinguishers
6474 | Use fire extinguisher with a minimum rating of 2A 10 BC
6475 | Replace all missing electrical cover plate.
6476 | NoData
6477 | Power strips must adhere to the above fire code.
6478 | Shall only be plugged into a permanent receptacle according to fire code. Cannot plug a power strip into another power strip.
6479 | Cannot use extension cords as a source of permanent wiring. Extension cords can only be used to power one portable appliance. Refer to the fire code above for extension cords.
6480 | Should not have taking occupancy prior to applying for and being issued a Certificate of Occupancy. Must apply for Certificate of Occupancy prior to follow up inspection.
6481 | NoData
6482 | NoData
6483 | Have a licensed fire protection company service and tag the fire extinguisher located in the breaker room.
6484 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a gas test permit.
6485 | Repair or replace the stand alone emergency lighting and the exit sign illumination.
6486 | Clear and maintain space in the breaker room.
6487 | Ensure the gates on the patio are unlocked while the building is occupied.
6488 | INFORMATION ONLY.
6489 | PROVIDE PERMITS: KEY BOX AND ALARM.
6490 | RELOCATE FIRE EXTINGUISHER BY BAR-B-QUE PIT. ADD FIRE EXTINGUISHER TO OTHER PIT.
6491 | MAKE SURE ALL BEDROOMS HAVE A WORKING SMOKE DETECTOR.
6492 | ALARM SHOWS TROUBLE. REPAIR ASAP.
6493 | INFORMATION ONLY.
6494 | INFORMATION ONLY.
6495 | REPAIR ACCESS GATE ON WEST SIDE OF PROPERTY.
6496 | HAVE A GAS TEST PERFORMED BY A LICENCED PLUMBER. All natural gas systems shall be in accordance with the city of HOUSTON BUILDING CODE (PLUMBING CODE). Contact the building code official for any questions regarding this issue and permit requirements.
6497 | CLEAN DAILY.
6498 | NoData
6499 | NoData
6500 | NoData
6501 | NoData
6502 | Sign letter provided.
6503 | Have fire extinguishers in laundry and boiler rooms serviced. Last service date 5/2019.
6504 | Sign letter provided.
6505 | Sign letter provided.
6506 | FYI: Last gas test performed on 11/03/2017. Good until 11/03/2021.
6507 | Sign letter provided.
6508 | This notice includes 1243 and 1239 Bay Area blvd.
6509 | NoData
6510 | No violations found
6511 | NoData
6512 | FIRE PANEL NEED SERVICE 1-8-20 LAST DATE
6513 | NEED SERVICE 8-19 LAST DATE
6514 | NEED TO BE INSPECTED
6515 | NoData
6516 | NoData
6517 | NEED TO BE SERVICE 9-10-19 LAST DATE
6518 | NEED TO BE SERVICE 11-19 LAST DATE
6519 | LAST SERVICE DATE 8-2020 ,DUE IN FEBRUARY
6520 | NoData
6521 | LAST DATE 6-5-2020. IN COMPLIANCE
6522 | LAST DATE 7-2020. IN COMPLIANCE
6523 | LAST DATE 7-2020. IN COMPLIANCE
6524 | LAST DATE 7-2020. IN COMPLIANCE
6525 | NoData
6526 | NoData
6527 | A LP-Gas permit is required for the use of Propane Gas Heaters on the Patio.Apply for Lp-Gas Permit @ COH-Building Dept.1002 Washington Ave. Permit Office.
6528 | Have all Fire Extinguishers serviced, and provided with current service tags.
6529 | Have Kitchen Fire Suppression / Ansul System serviced, and provided with a current service tag, Every 6 months.
6530 | Renew your Public Assembly Permit within 10 Business Days
6531 | Renew Public Assembly Permit within 10 Business days
6532 | NoData
6533 | Marcus Smith NO VIOLATIONS FOUND AT THIS TIME.
6534 | NoData
6535 | NoData
6536 | NoData
6537 | NoData
6538 | NoData
6539 | NoData
6540 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
6541 | NoData
6542 | NoData
6543 | NoData
6544 | NoData
6545 | Please provide the correct key, to be placed in the 911 box for the master lock on the manual gate. (The first gate next to the exit gate facing Westview) Please repair the failsafe pull cable and piping on the exit gate facing Westview. Replace or Repair 911 box the cable is in.
6546 | NoData
6547 | 6-3-2020 LAST TEST DATE. IN COMPLIANCE
6548 | 7-2020 LAST TEST DATE. IN COMPLIANCE
6549 | 7-2020 LAST TEST DATE. IN COMPLIANCE
6550 | 7-2020 LAST TEST DATE. IN COMPLIANCE
6551 | NoData
6552 | NoData
6553 | NoData
6554 | NEED TO BE SERVICE , HAS TROUBLE LIGHT ON. 9-20-20 LAST DATE
6555 | IN COM[PLIANCE. 8-20 LAST DATE
6556 | IN COM[PLIANCE. 7-20 LAST DATE
6557 | IN COM[PLIANCE. 9-20 LAST DATE
6558 | IN COM[PLIANCE. 7-20 LAST DATE
6559 | NoData
6560 | NEED TO BE SERVICE HAS TROUBLE LIGHT ON. HAS NO ANNUAL INSPECTION TAG
6561 | NEED TO BE SERVICE IN NOVEMBER. 10-19 LAST DATE
6562 | NEED TO BE SERVICE . 8-18 LAST DATE
6563 | NoData
6564 | NEED TO BE SERVICE
6565 | FIRE PANEL NEED TO BE SERVICE
6566 | NEED TO BE SERVICE
6567 | NEED TO BE SERVICE
6568 | 4/19 NEED TO BE SERVICE
6569 | 7/19 WAS THE LAST INSPECTION. NEED TO BE SERVICE IN AUGUST
6570 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
6571 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES. KEEP PLANS UPDATED AND TRAIN QUARTERLY.
6572 | see inspection #301169
6573 | NoData
6574 | NoData
6575 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit for test.
6576 | NoData
6577 | APPLY FOR A M3 (FUEL DISPENSING PERMIT) REQUIRED FOR YOUR PLACE OF BUSINESS.
6578 | It is the owner/occupants responsibility to correct all violations listed below:-Contact a licensed fire protection company to have the fire alarm system serviced and ensure a blue acceptable annual service tag is attached. Ensure that an audibility test has been performed within the past 3 years, and a sensitivity test has been performed within the past 2-5 years. Repair or replace damaged smoke detector in the custodial closet.-Wet chemical extinguishing systems in commercial kitchens are required to be serviced every 6 months. Contact a licensed fire protection company to service the ANSUL system and ensure a current service tag is attached.-Commercial kitchen hoods in low-volume cooking operations such as places of religious worshipare required to beinspected and serviced as necessary every 12 months. Contact a licensed professionalto have the vent hood inspected. Ensure a service tag is attached following the completion of the service.-Have all exit signs inspected to ensure they are properly illuminated under regular service power and battery back up power.-Ensure all ceiling tiles that were found to be missing are put back into place and are properly seated. (second floor classroom and custodial closet)-Remove the white tape being used tocover the open space in the breaker boxin the electrical closet in the school roomand replace with a breaker box filler plate.Side NotesGas test performed and finaled on 09/02/20Fire drill logs inspected and found to be complete
6579 | NoData
6580 | NoData
6581 | NoData
6582 | NoData
6583 | NoData
6584 | The fire extinguishers are required to have annual inspection tags.
6585 | Provide filler plates for the openings in the breaker panel.
6586 | NoData
6587 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualFire Extinguishers- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
6588 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice.COMPLIANCE WITHIN 60 CALENDAR DAYS.
6589 | NoData
6590 | NoData
6591 | UPDATE FIRE MARSHAL BINDER
6592 | CHECK ALL EMERGENCY LIGHTS
6593 | INFORMATION
6594 | AS PER CODE
6595 | INFORMATION
6596 | INFORMATION
6597 | NoData
6598 | NoData
6599 | Maintain clean filters in paint booth.
6600 | Information
6601 | NoData
6602 | Provide a sign on the Doors of the Fire Alarm Room that says "FIRE ALARM"
6603 | Have any out of date FEX inspected and tagged.Shop
6604 | Have any out of date FEX inspected and tagged.Shop
6605 | Some Stand Pipe Tags are MissingFire Tank is not taggedFire Pump Controller is not Tagged.
6606 | Provide an appointment for the initial cleaning of the kitchen hood systems.
6607 | Garage
6608 | Fire Rated Walls required rating shall be maintained.Mechanical rooms walls are penetrated.
6609 | Obtain a Key Box Permit from the Houston Permitting Center
6610 | Place a durable sign on the Fire Alarm Room Door stating "FIRE ALARM"
6611 | Obtain a P2 Assembly Permit.
6612 | Post occupant load signs in all places of assembly.
6613 | NoData
6614 | NoData
6615 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
6616 | INFORMATION
6617 | INFORMATION
6618 | INFORMATION
6619 | NoData
6620 | NoData
6621 | NoData
6622 | Approved, no violations noted.
6623 | NoData
6624 | NoData
6625 | NoData
6626 | NoData
6627 | Event meets the requirements for the George R Browns assembly permit#5026247.
6628 | NoData
6629 | NoData
6630 | NoData
6631 | This is an urgent repair issue. Fire alarm panel must be functional.
6632 | NoData
6633 | Compliance letters from the fire protection company are needed, stating that each system is operating correctly, as designed.
6634 | Notification must be sent immediately when an impairment is encountered.
6635 | Compliance letter is needed stating that these systems are all functioning correctly.
6636 | Ensure the fire protection company completes all necessary tests, then obtain the compliance letters.
6637 | Red tag on fire hose in stairwells stating that a hydro test is due needs to be addressed.
6638 | Oily rag cans need to be emptied regularly and shouldn't contain regular trash.
6639 | Unnecessary combustible clutter needs to be removed.
6640 | Signage is also needed below the sign for Building A that says FCC and gives the direction where they can find the room, which in this case is through the pool gate with a code.
6641 | K1 - Key box permit needs to be renewed annually through the permit office.
6642 | This is a high priority. Signage showing where the FCC is, access to get in the gate is needed in the keybox, a key from the keybox should allow access to the FCC. The FCC needs to be cleaned up. Alarm panel and fire depository box need to be functional and in order.
6643 | The room itself needs to be cleared of debris. The box needs to be repaired so that the 911 lock and a lock of your choice secure the contents. The box is missing 4 keysets, 2 elevator drop keys, and the binder needs to be updated. Refer to LSB 6 in the attachments that were originally sent.
6644 | This is the overview of what the contents of the binder should have in it. For more detailed info, refer to LSB 6.
6645 | Ensure that the legend card is accurate when specifying what each key is for.
6646 | 4 key sets are missing.
6647 | 2 elevator hoistway door keys/tools are needed.
6648 | 2 Independent service keys are needed in the FCC. They should be labeled and placed in a visible area near the Fire Depository Box.
6649 | The key box also needs the door combination so that fire department personnel can access the pool area where the entrance to the FCC is.
6650 | NoData
6651 | Will need a fire watch if the alarm panel red tag issue is not resolved soon.
6652 | NoData
6653 | Portable Fire Extinguisher(s) annual maintenance Dt: 10/20
6654 | Keep all exit door(s) and pathways clear. Please remove product cart in front of exit
6655 | NoData
6656 | 24" clearance must be maintained between ceiling and combustible materials (Non-sprinkled building)
6657 | Extension cords not allowed for permanent wiring, please remove extension cord run into ceiling
6658 | 36" Working clearance must be maintained in front of electrical panels
6659 | Obtain and post Certificate of Occupancy [104.1(9)]. Current yellow application receipt also acceptable
6660 | Lower all plastics (high hazard commodities) to 6 ft. or less and maintain these products at this height until approved for high piled storage.Compliance by 3-12-2021
6661 | Lower all plastic pails, totes, and bottles to 6 ft. or lower in the warehouse and maintain storage at this height until approved for high piled storage.Compliance by 3-12-2021
6662 | Provide stickers showing the direction and color coded product flowing through your outside piping coming form the tank farm.Compliance by 3-12-2021
6663 | Replace the faded 704 placards on your outside above ground storage tanks.Compliance by 3-12-2021
6664 | Submit a Hazardous Materials Inventory Statement using the guidelines provided.Compliance by 3-12-2021
6665 | Repair or replace all emergency lights in your facility that are not working and provide documentation that they have been tested and repaired if not working.Compliance by 3-12-2021
6666 | Have two knox box's installed on the side access gate and outside the far warehouse door with access keys to be placed inside during my follow up inspection. Information on the knox box will be provided.Compliance by 3-12-2021
6667 | Apply for a LP-Gas permit on the City of Houston web site under fire permit.Compliance by 3-12-2021
6668 | APPLY FOR A CERTIFICATE OF OCCUPANCY AT 1002 WASHINGTON AVE. ALL COMPANIES INSIDE THE CITY LIMITS OF HOUSTON SHALL HAVE A OCCUPANCY PERMIT BEFORE OCCUPYING THE BUILDING. COMPLIANCE BY 4-4-2019
6669 | Permit Expired 1/14/2021; Unpaid Fees $177.87
6670 | Exits are required to be unlocked while the building is occupied.
6671 | NoData
6672 | Make all code violation corrections prior to the re-inspection date noted on page 1.
6673 | The annual fire alarm system inspection is expired. Provide for an annual inspection of the FAS by a state certified company. Provide a current fire alarm annual inspection report for review by the inspecting fire code official. The most current annual fire alarm inspection report shall be kept in the Fire Marshal’s Binder. The fire alarm panel shall also have an annual blue inspection tag that is current placed on the panel.
6674 | The audibility test shows to have been done on 3/15/19. Provide test documentation for the noted audibility test date.Must have one of two things to be acceptable and the Documentation should contain Company’s ACR#, Tester’s FAL#, and date. A) Must show each audibility device’s ambient decibel level and the decibel level when the device is active. The difference in DB level must fall within NFPA 72’s acceptable range for the device to pass the test. OR B) A document from their company on company’s letter head that has the following information – 1) Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all audibility devices passed the audibility test as required by NFPA 72.
6675 | The invoice shows an egress light test performed around 10/15/20. Provide the test documentation for a current emergency egress light annual test.An approved licensed master electrician or licensed electrical service company shall test all emergency lighting systems annually. The battery units, whether of the acid or alkali type, shall be tested continuously for a minimum of 90 minutes.Failed devices shall be corrected prior to the re-inspection.Provide dated documentation stating the master electrician and/or company's certification number, and that all devices passed the 90-minute test.
6676 | Provide for annual fire extinguisher inspection. All extinguishers should have a current annual inspection tag.
6677 | Provide documentation for the last sensitivity test. Consult with your fire alarm system inspection company to determine the type of system. If the system is an addressable / Intelligent system - provide the digital diagnostic reading showing the detectors status. If the system is conventional - test each device with synthetic smoke and provide documentation. The documentation is required to show: 1)Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all smoke detector devices passed the sensitivity test as required by NFPA 72.
6678 | NoData
6679 | NoData
6680 | System due for audibility test.
6681 | Fire alarm panel due for annual inspection.
6682 | Sprinkler due for 5th year test.
6683 | Sensitivity test required every 2 years.
6684 | NoData
6685 | Owners responsiblity
6686 | Provide documentation showing compliance of emergency firefighting operation in every elevator located throughout condo community.
6687 | Provide documentation of compliant annual elevator inspections for all buildings in the condo community.
6688 | NoData
6689 | Ventilation system for spray booth shall have an annual inspection performed.Compliance: 30 calendar days.
6690 | NoData
6691 | The configuration of the solid shelving within the racking system shall not be so that water is unable to penetrate the bottom racks. A minimum of 3inch spacing shall be maintained between solid shelving.Compliance: 30 calendar days.
6692 | Extension cords are not allowed to be used for permanent wiring. All extension cords shall be unplugged at the end of each work day to avoid electrical arcing.
6693 | Compliance: 30 calendar days.
6694 | All exits shall have a clear path and be clear from any obstruction.Compliance: Immediately.
6695 | All access door leading into warehouse shall be marked with HFD lettering in red and also be keyed alike. A total of two access doors were inoperable with the 911 key that was provided from the 911 key box.Compliance: 30 calendar days.
6696 | All required permits shall be posted at all times.Compliance: 30 calendar days.
6697 | Renew the P2 - Assembly Permit. (FP-04068922)Report #306489
6698 | Needs Annual Inspection
6699 | All fire systems tags that are expired need to be tested and tags dates updated to current dates.
6700 | Damper test results need to be added to FMB.
6701 | Fire Extinguishers need to be serviced, inspected and tags updated to correct inspection date.
6702 | There are three boxes at differ entrances that need to be updated with new type of 911 box,(Knox 3200 hinged series). Spoke with Mr. A. Garcia on location and explained where these new boxes should be installed. I will attach a photo of what needs to be installed.
6703 | There are several rooms showing Fire Command Room but there is nothing inside the room. The alarm room as well as the riser room do not have correct signage. Please correct the signs to what the use of the room.
6704 | A mechanical room was found not finished and has no ceiling after construction. All electrical and mechanical rooms need to be checked for proper fire stop.
6705 | A mechanical room was found not finished and has no ceiling after construction. All electrical and mechanical rooms need to be checked for proper fire stop. Proper fire rated calking needed.
6706 | Each placard should I.D the class room. Give two different location to the Exit. Exp. Room 102 has a primary line leading to the closes exit. Secondary line leading to a different exit, all coming from room 102. Each placard should coincide with each room. Not the same placard for every class room.
6707 | NoData
6708 | Permit for elevator needs to be added to FMB
6709 | Proper signage outside door to ID alarm panel.
6710 | System and service tags need to be tested and updated according to fire code standards.
6711 | All updated permits need to be added to FMB
6712 | Provide documentation of a gas test within the last 5 years or have a gas test done.
6713 | Bring all fire exstiguishers up to current standard compliance.
6714 | Comply with IFC 2012 506.3 Install an Fire Depository Box
6715 | NoData
6716 | NoData
6717 | NoData
6718 | NoData
6719 | NoData
6720 | NoData
6721 | NoData
6722 | NoData
6723 | -It is the owner/occupants responsibility to correct all violations found.-Reinspection fees will be issued if the violations are not corrected prior to the follow up date.-Citations will be issued if compliance is not obtained.-All exit doors must be able to be opened from the egress side without the use of a key. Replace the double keyed cylinder locks on each door.-Once power is restored to the building, ensure all exits signs are illuminated under regular power and battery backup power.-Replace the missing extinguisher near the exit dooron thewestern end of the building. Mounting a second extinguisher is the kitchen is acceptable and encouraged. Minimum size - 2:A 10:BC-Ensure all extinguishers have been serviced by a licensed fire protection company and have a service tag attached.-At least one fire extinguisher with a minimum rating of 2:A 10:BC is required to the tagged and mounted in the ambulance service shop while being used as a service area.-Ensure all electrical wires are secured and junction boxes/breaker boxeshave appropriate covers.-Install breaker box filler plates in the small breaker box in the office.-Properly secure all compress gas cylinders-Apply for a "Hot Works" permit or remove the cutting torch from the premises.Disable the chain from the access gate. If the decision is made in the future to use the access gate, ensure the Houston Fire Department Life Safety Bureau Standard #4 is followed.Ensure the sensor for the mag lock on the front door is not covered.It appears Acute Medical Services does not have a Certificate of Occupancy on file. Please contact the Houston Permitting Center Occupancy Division. (832)394-8880
6724 | The chain on the access gate was disabled. This is no longer an electronic access gate. Fail safe no longer required.
6725 | The chain on the access gate was disabled. This is no longer an electronic access gate. Toggle switch no longer required.
6726 | NoData
6727 | NoData
6728 | NoData
6729 | NoData
6730 | NoData
6731 | Audibility test required every 3 years.
6732 | Sensitivity test required every 2 years.
6733 | Place sign on doors leading into mechanical, fire alarm panel and electrical rooms.
6734 | Have qualified gate company provide a manual pull switch on the access gate in the event of a power failure the gate can be manually opened.Compliance by 3-12-2021
6735 | Lower all plastic pails, totes, and bottles to 6 ft. or lower in the warehouse and maintain storage at this height until approved for high piled storage.Compliance by 3-12-2021
6736 | Provide stickers showing the direction and color coded product flowing through your outside piping coming form the tank farm.Compliance by 3-12-2021
6737 | Replace the faded 704 placards on your outside above ground storage tanks.Compliance by 3-12-2021
6738 | Submit a Hazardous Materials Inventory Statement using the guidelines provided.Compliance by 3-12-2021
6739 | Repair or replace all emergency lights in your facility that are not working and provide documentation that they have been tested and repaired if not working.Compliance by 3-12-2021
6740 | Have two knox box's installed on the side access gate and outside the far warehouse door with access keys to be placed inside during my follow up inspection. Information on the knox box will be provided.Compliance by 3-12-2021
6741 | Apply for a LP-Gas permit on the City of Houston web site under fire permit.Compliance by 3-12-2021
6742 | NoData
6743 | YELLOW TAG ISSUES MUST BE CORRECTED
6744 | Fire Alarm Panel inoperable red tag attached.3 Day notice to restore panel to full function.Provide Temporary Fire Watch/Sign Form.Fire Alarm Stem Inoperable stickers attached to building and Alarm Room.Fire Protection company provide Technical report on repairs and a Timeline for completion.Notify HFD Dispatch 3 of Inoperability and when system is repaired.713-884-3143HFD.DISPATCH3@houstontx.govFollow LSB # 2.
6745 | Fire Alarm Panel inoperable red tag attached.3 Day notice to restore panel to full function.Provide Temporary Fire Watch/Sign Form.Fire Alarm Stem Inoperable stickers attached to building and Alarm Room.Fire Protection company provide Technical report on repairs and a Timeline for completion.Notify HFD Dispatch 3 of Inoperability and when system is repaired.713-884-3143HFD.DISPATCH3@houstontx.govFollow LSB # 2.
6746 | Have a licensed fire protection company service and tag the class K fire extinguisher.
6747 | The vent hood suppression system is due for service before the end of 03/2021. Ensure a sticker with the date of vent hood cleaning is placed on the vent hood.
6748 | Remove hanging displays from the ceiling.
6749 | Remove the inoperable vent hood suppression pull station.
6750 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a gas test permit.
6751 | Repair or replace the emergency illumination.
6752 | Post the occupant load (125).
6753 | Ensure the side exit is unlocked while the building is occupied. Repair the hardware if necessary.
6754 | NoData
6755 | NoData
6756 | Information for mounting fire extinguishers
6757 | Location requirements for fire extinguishers in E occupancy. Information
6758 | Make all code violation corrections prior to the re-inspection date noted on page 1 of the report.
6759 | Provide documentation for a current emergency egress light annual test.An approved licensed master electrician or licensed electrical service company shall test all emergency lighting systems annually. The battery units, whether of the acid or alkali type, shall be tested continuously for a minimum of 90 minutes.Failed devices shall be corrected prior to the re-inspection.Provide dated documentation stating the master electrician and/or company's certification number, and that all devices passed the 90-minute test.
6760 | All fire extinguisher annual inspections are expired. Provide current annual inspection and tag.
6761 | Check the fire extinguisher Hydrostatic Test LogReplace or test any fire extinguishers with a manufacturers date older than 2009 and update the fire extinguishers hydrostatic test log to reflect any changes.
6762 | Approved Key Boxes noted in the Life Safety Bureau #5.
6763 | 1. The key box on 17th needs the following:- gate key- site map- falcon padlock2. Add a Key Box to the gate post for the sliding Gate on Studewood. The key box must be an approved type listed in accordance with UL 1037 Per the 2012 International Fire Code (506.1) and LSB standard (5.1.2)Approved Key Box is the 3200 series box made by Knox Company that complies with UL 1037
6764 | UL listed power strips / multiplug adapters are allowed when plugged directly into the wall outlet. The use of Multi plug adapters that are not plugged directly into the wall outlet are prohibited and are a fire code violation. Power strips cannot be plugged into each other (also know as daisy chained together). There are several of these daisy chained together (3 or 4) located in Room 122 underneath the aquarium. Also, please notify all employees of this code and remedy any other locations where this is violation is present.
6765 | Cloth material from wall or ceilings must meet NFPA 701 test criteria or be IFR by nature. Provide documentation that the "Lion" picture cloth and the "Chinese" symbol cloth in T-540 meet test requirements of NFPA 701 or remove the material.
6766 | Replace the fire extinguisher in the paint storage building. Add two extinguishers to T-420 by each main exit door. Add one extinguisher in T-540 by the exit door.
6767 | Information for mounting fire extinguishers
6768 | Information for mounting fire extinguishers
6769 | Information for mounting fire extinguishers
6770 | Exit sign near 105 is not lit. Repair the sign.
6771 | Information for Key Box
6772 | Keep fire Marshal’s Binder / Records Orderly. Remove old or expired copies. Remove duplicate copies. Keep old records in an archived binder or another location.
6773 | 1. Renew the Assembly Permit prior to 2/21/21. See Additional Permit renewal form / requirements. 2. Provide current Boiler State Certificate for (TX222086) and place in the Fire Marshal's Binder.
6774 | NoData
6775 | NoData
6776 | NoData
6777 | NoData
6778 | NoData
6779 | NoData
6780 | NoData
6781 | NoData
6782 | NoData
6783 | NoData
6784 | NoData
6785 | NoData
6786 | NoData
6787 | NoData
6788 | NoData
6789 | NoData
6790 | NoData
6791 | NoData
6792 | NoData
6793 | NoData
6794 | NoData
6795 | NoData
6796 | NoData
6797 | Residents must be informed on the proper use of outdoor cooking equipment.
6798 | Please keep all debris from inside all riser rooms. Also, check all heaters for proper operations.
6799 | Toggle switch located inside 911 box does not open electric swing gate.
6800 | Please repair the toggle switch located inside 911 box and add master lock key that secures the Fail Safe pull cord.
6801 | Please label all shutoff with correct unit numbers
6802 | Visually inspect all draft stops located in the attic space.
6803 | verify all sleeping units are supplies with working smoke alarms.
6804 | Please provide last Gas Test date. Gas test shall be done every 5 years.
6805 | Please verify updated Key box permit. My records show permit expired in 2020.
6806 | NoData
6807 | NoData
6808 | NoData
6809 | NoData
6810 | NoData
6811 | NoData
6812 | NoData
6813 | NoData
6814 | NoData
6815 | NoData
6816 | PUBLIC ASSEMBLY PERMIT EXPIRED
6817 | NoData
6818 | NoData
6819 | NoData
6820 | NoData
6821 | NoData
6822 | NoData
6823 | NoData
6824 | NoData
6825 | NoData
6826 | NoData
6827 | NoData
6828 | NoData
6829 | NoData
6830 | NoData
6831 | NoData
6832 | NoData
6833 | NoData
6834 | NoData
6835 | NoData
6836 | NoData
6837 | NoData
6838 | NoData
6839 | NoData
6840 | NoData
6841 | NoData
6842 | NoData
6843 | NoData
6844 | NoData
6845 | NoData
6846 | NoData
6847 | Last fire extinguisher inspection was October 2018 .Bring up to code
6848 | Last test for Emergency Lighting found in Fire Marshal Binder was 7-1-16
6849 | Last riser inspection March 2018Bring up to code
6850 | Last Hydro Test October 2014Bring up to code
6851 | P2 permit expired1-13-20.A4 permit expired 2-18-20
6852 | NoData
6853 | NoData
6854 | NoData
6855 | NoData
6856 | NoData
6857 | NoData
6858 | NoData
6859 | NoData
6860 | NoData
6861 | NoData
6862 | NoData
6863 | All automatic access gates shall have a manual pull in the case of power outage for emergency operations per Life Safety Bureau Standard 4.Compliance by 1-4-2021
6864 | An operational permit is required when a automatic access gate is in use. Apply for an access gate permit on the City of Houston website under fire department permits.Compliance by 1-4-2021
6865 | NoData
6866 | NoData
6867 | NoData
6868 | NoData
6869 | NoData
6870 | NoData
6871 | NoData
6872 | NoData
6873 | NoData
6874 | NoData
6875 | The Falcon Lock on the 911 key box has rusted in the closed position. The lock must be removed with bolt cutters and replaced - OR - a new 911 key box with the hinged lid protecting the key lock may be used. Should you decide to use the key box with the hinged lid (which will not require a falcon lock being replaced periodically), the existing key box must be removed.
6876 | NoData
6877 | NoData
6878 | Both entrance/exit access gates.
6879 | Either a "micro switch" or "toggle switch" shall be located inside both 911 boxes.
6880 | Please repair the fold down hinged arm that secures the manual swing gate in the closed position via master lock. Key to this padlock will be kept inside the 911 box for HFD emergency use.
6881 | A pin lock shall be required on all electric swing gate arm providing HFD with emergency access.
6882 | unit numbers shall be located on outside electrical panels.
6883 | All building with a pitched roof shall be visually inspected for solid draft stop construction. No draft stop penetration shall be allow.
6884 | Please provide an all weather 18" x 18" sign that reads "HFD 3".
6885 | every bedrooms and exit pathway shall be provided with a working smoke alarm.
6886 | 5 year gas test is required for all gas meters located on property.
6887 | Access gate (a4) permit expired on 12/9/2020. Please Call HPC at 832-394-8811 for information concerning on-line permit renewal.
6888 | multiple units have windows with broken glass. Please repair all windows with broken glass on property.
6889 | Please make sure no debris, furniture, mattresses are located beside dumpster. All trash shall be placed inside dumpster for removal.
6890 | Please trim both trees that are located near fire hydrants at the back of property to 13'-6".
6891 | NoData
6892 | Renew the access gate permit.
6893 | NoData
6894 | NoData
6895 | NoData
6896 | NoData
6897 | NoData
6898 | NoData
6899 | NoData
6900 | NoData
6901 | NoData
6902 | NoData
6903 | NoData
6904 | NoData
6905 | NoData
6906 | NoData
6907 | NoData
6908 | NoData
6909 | NoData
6910 | NoData
6911 | NoData
6912 | NoData
6913 | NoData
6914 | NoData
6915 | NoData
6916 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAETY AND CODE VIOLATIONS AT ALL TIMES.
6917 | NoData
6918 | NoData
6919 | NoData
6920 | NoData
6921 | NoData
6922 | NoData
6923 | NoData
6924 | NoData
6925 | NoData
6926 | NoData
6927 | NoData
6928 | NoData
6929 | NoData
6930 | NoData
6931 | NoData
6932 | The event manager has submitted the site plan for the event. The plan has been approved.
6933 | Permit inspection with event manager. The site meets the requirements for Minute Maid Park's assembly permit.
6934 | The event manager has been notified that if they want to place the alarm system on bypass during the event they would need to obtain a standby permit. The proper paperwork has been submitted and forward to the LSB-Coordinator for the assignment of inspectors.
6935 | NoData
6936 | NoData
6937 | NoData
6938 | NoData
6939 | NoData
6940 | NoData
6941 | NoData
6942 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
6943 | THE FDC MUST BE PRESSURE TESTED EVERY 5 YEARS.
6944 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY ALL TIMES. KEEP PLANS UPDATED AND TRAIN QUARTERLY.
6945 | Upon inspection, no fire code violations were discovered at this time.
6946 | Fire Alarm Permit Issued August 11, 2020 and expires September 19, 2021.
6947 | NoData
6948 | Portable Fire Extinguisher(s) annual maintenance Dt: 11/20
6949 | Annual Fire alarm test Dt: 6/3/20 FACP for sprinkler system only.
6950 | Annual Sprinkler system (wet) test Dt: 6/3/20
6951 | 5-year hydro/flow test Dt: 10/26/16
6952 | 18" clearance must be maintained between sprinkler head deflectors and combustible materials (Sprinkled building). Be aware of combustible storage height on top shelf
6953 | Extension cords are plugged in correctly, however are used as illegal wiring. See also 605.5
6954 | NoData
6955 | Emergency lighting must be tested and any deficiencies corrected
6956 | Gas cylinders must be secured. Attach chain to non-movable object in order to keep cylinders upright. Helium cylinder in store room must be secured
6957 | Gas cylinder caps must be in place when not in use. One tank, secured against the wall, is missing a cap
6958 | 3-way plugs, multiple outlet adapters and multi-outlet cords are not allowed unless they are "resettable" type (overcurrent protected). See also 605.4.1
6959 | 3-way plugs, multiple outlet adapters and multi-outlet cords are not allowed unless they are "resettable" type (overcurrent protected). Please remove all multi-outlet extension cords
6960 | Approved multi-outlet power taps must be plugged directly into an outlet. No daisy-chaining of power taps allowed. Remove multi-outlet taps that are currently plugged into another multi-outlet power tap
6961 | Extension cords not allowed as a replacement for permanent wiring. Remove all extension cords running into drop ceiling
6962 | No missing spacers allowed in electrical panels
6963 | Obtain and post Certificate of Occupancy [104.1(9)]. Current yellow application receipt also acceptable
6964 | Directional arrows showing incorrect direction to exit. No arrows showing direction of exit door
6965 | NoData
6966 | NoData
6967 | NoData
6968 | NoData
6969 | NoData
6970 | NoData
6971 | NoData
6972 | NoData
6973 | After a meeting with the event manager it was decided the event would be cancelled due to the possibility of inclement weather.
6974 | The plan has been approved.
6975 | No violations found at this time.
6976 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFE AND CODE VIOLATIONS AT ALL TIMES.
6977 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES. KEEP PLANS UPDATED AND TRAIN QUARTERLY.
6978 | NoData
6979 | NoData
6980 | NoData
6981 | NoData
6982 | NoData
6983 | Repair exit signs in pool area x2
6984 | Maintain clearance space around electrical panels and equipment. A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. C-124
6985 | Remove curtains that do not meet NFPA 701 - C122
6986 | The Fire alarm panel display is showing trouble but no trouble light is lit up. Repair the fire alarm panel.
6987 | Keep fire Marshal's Binder / Records Orderly. Remove old or expired copies. Remove duplicate copies. Keep old records in an archived binder or another location. Provide the annual standpipe hose report and the 3yr report in the fire marshal's binder
6988 | Boiler TX Cert of Operation is expired for #246461
6989 | Current annual inspection tag is needed
6990 | Documentation required for the last intercom test. Performed within the last year. "Fire alarm systems shall be tested, and service tagged at the main alarm panel, not less than annually." "voice/alarm communications systems and other devices that may be part of the fire alarm system."
6991 | Make all code violation corrections prior to the compliance date noted on page 1 of the report.
6992 | Lower combustible storage. - C124 - E107 - Kitchen
6993 | Provide training sign in sheet for 2019-2020 school year
6994 | There is water leaking above the smoke detector in the A100 Hallway. Repair the leak to prevent malfunction of the smoke detector. Exposed junction box wires need cover plate.
6995 | Remove hanging displays T-28
6996 | Test and tag the ansul system
6997 | Provide documentation for a current emergency egress light annual test. An approved licensed master electrician or licensed electrical service company shall test all emergency lighting systems annually. The battery units, whether of the acid or alkali type, shall be tested continuously for a minimum of 90 minutes. Failed devices shall be corrected prior to the re-inspection.
6998 | There is water leaking above the smoke detector in the A100 Hallway. Repair the leak to prevent malfunction of the smoke detector. Exposed junction box wires need cover plate.
6999 | Clear out trash, combustibles, pipes, metal, etc. in the swimming pool basement area and the Boiler Room.
7000 | Remove curtains that do not meet NFPA 701 - C122 T-1
7001 | The following permits are expired and must be renewed: - Burglar Alarm - Combustible Waste - Fire Alarm Permit Provide documentation in the fire marshal's binder
7002 | Do not storyany combustibles within 3 feet of the battery charging station.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
7003 | HIGH-PILEDCOMBUSTIBLE STORAGE. Storage of combustible materials in closelypacked piles or combustible materials on pallets, in racks or on shelves wherethe top of storage is greater than 12 feet (3658 mm) in height. When requiredby the fire code official, high-piled combustible storage alsoincludes certain high-hazard commodities, such as rubber tires. Group Aplastics, flammable liquids, idle pallets and similar commodities, where thetop of storage is greater than 6 feet (1829 mm) in height.This facility was never approved forhigh-piled storage. Plans were neversubmitted to the building department or the fire marshal’s office for approvalof rack storage of high-piled operation.Lower all class I-IV commodities to a maximumof 12 feet and high-hazard commodities to 6 feet, as required by table 3206.2,for non-sprinklered buildings and maintain commodities at this height. AN OWNER'S STATEMENT MUST BE SIGNED If you choose to become high-piled submit plans to the building department andthe hazmat/high-piled storage team for review and approval for high-piledcombustible storage. Acquiring the expertise of a certified fireprotection engineer for this process is highly advisable.SEE ATTACHED COPY OF HIGH-PILED STORAGE PLANSUBMITTAL GUIDELINE.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
7004 | All fireextinguishers shall have a current annual inspection tag by an approvedlicensed fire protection equipment company.All servicing, testing, maintenance and tagging of listed portable fireextinguishers shall be conducted annually by qualified personnel in accordancewith LSB standard 01, "installation and maintenance of portable fireextinguishers"COMPLIANCE:WITHIN 30 CALENDAR DAYS.
7005 | Exits and exit pathways are to remain clear of obstructions at all times. Do not allow anything to be placed in front of the emergency exits at any time.IMMEDIATE COMPLIANCE REQUIRED
7006 | The owner/occupant shall be heldresponsible for the correction and abatement of all violations listed in thisnotice of violations report. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
7007 | Aisles in the rack storage must be kept according tothe code paying special attention to keeping aisles clear of storage. Aislescannot be used for storage. Half of the aisle is always to remain clear.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
7008 | A 4-A/20-B:C fire extinguisher must be properly mounted within 20 feet of the battery charging station.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
7009 | Mark the posts of your rack storage at 12 feet from the ground and ensure that your storage stays below the 12 foot mark.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
7010 | A workingspace (cleared of all combustible material) of not less than 30 inches inwidth, 36 inches in depth and 78 inches in height shall be provided in front ofelectrical service equipment.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
7011 | NoData
7012 | NoData
7013 | Coverage inspection passed for the basement and sprinkler permit#20041394 is final. Coverage inspection for level#1 passed and the trip tests for both the dry system and the pre-action passed. permit#20040198 is final. the hydro test and the pipe-size inspections passed for the standpipe system in the building. Tampers for pump room passed also. The fire pump final passed and the pump run, power fail and phase reversal also passed the standpipe permit#19015982 is final. inspections are complete.
7014 | Repair the front access gate manual pull so that access is available in the event of a power outage.Compliance by 2-19-2021
7015 | Provide a cover plate over the electrical outlet behind the vending machines.Compliance by 2-19-2021
7016 | Provide documentation that the fire alarm sensitivity test as been done in the time frame listed in this section. Women side appears do have been done in 2017 but did not see date tested on mens side.Compliance by 2-19-2021
7017 | Provide documentation that gas test has been conducted in the manufacturers time frame.Compliance by 2-19-2021
7018 | Repair or replace the emergency exit light ex. 9.Compliance by 2-19-2021
7019 | NoData
7020 | NoData
7021 | NoData
7022 | NoData
7023 | NoData
7024 | NoData
7025 | NoData
7026 | NoData
7027 | NoData
7028 | NoData
7029 | NoData
7030 | NoData
7031 | NoData
7032 | NoData
7033 | NoData
7034 | NoData
7035 | NoData
7036 | NoData
7037 | NoData
7038 | NoData
7039 | Label the electrical room door (Electrical Panel Inside)
7040 | Add at least one Portable Fire Extinguisher inside of the business
7041 | Remove the portable Fire Extinguisher from between the beverage coolers
7042 | Apply for and post the (M3) Fuel Dispenserpermit at 1002 Washington Ave. 832-394-8811 Apply for and post the (L1) Propane Storag permit at 1002 Washington Ave. 832-394-8811
7043 | Make sure both the left and right side entrance/exit door remain unlocked during business hours
7044 | NoData
7045 | NoData
7046 | NoData
7047 | NoData
7048 | NoData
7049 | MAKE SURE ALL PORTABLE FIRE EXTINGUISHERS HAVE A CURRENT INSPECTION TAG OF THEM
7050 | CLEAR ALL THE OBSTRUCTIONS FROM IN FRONT OF THE EXIT DOOR
7051 | LABEL THE ELECTRICAL ROOM DOOR WITH A SIGN THAT READS "ELECTRICAL PANELS INSIDE
7052 | CLEAR ALL COMBUSTIBLES FROM IN FRONT OF AND AROUND THE ELECTRICAL PANEL BOXES
7053 | RENEW THE M3(FUEL DISPENSER) PERMIT AT 1002 WASHINGTON AVE. 832-394-8811
7054 | An approved automatic extinguishing system is required on the spray booth.
7055 | NoData
7056 | NoData
7057 | Plans are required to be submitted to the building department.
7058 | Submit plans to the building department.
7059 | Submit plans to the building department.
7060 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
7061 | Have a licensed fire protection company perform an annual fire sprinkler inspection and correct any deficiencies.
7062 | Have a licensed fire protection company perform a 5 year FDC test and correct any deficiencies.
7063 | NoData
7064 | NoData
7065 | NoData
7066 | NoData
7067 | NoData
7068 | NoData
7069 | NoData
7070 | CERTIFICATE OF OCCUPANCY IS VISIBLY POSTED ON SITE EMERGENCY EGRESS AND EXIT LIGHTS OPERATIONAL - TESTED OCT 2020 P2 PERMIT POSTED - EXPIRES 5/9/21 FIRE ALARM PERMIT IS POSTED ON SITE - VALID UNTIL 11/17/21 FIRE ALARM PANEL IS BLUE TAGGED - 10/09/20 FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - OCT 2020 EMERGENCY ESCAPE MAPS ARE ALL POSTED IN PLACE IN EACH CLASSROOM K EXTINGUISHER BLUE TAGGED AND INSPECTED OCT 2020 ANSUL SYSTEM IS BLUE TAGGED - OCT 2020 GAS TEST CONDUCTED AND PASSED 1/8/20
7071 | CERTIFICATE OF OCCUPANCY IS VISIBLY POSTED ON SITE EMERGENCY EGRESS AND EXIT LIGHTS OPERATIONAL - TESTED OCT 2020 P2 PERMIT POSTED - EXPIRES 5/9/21 FIRE ALARM PERMIT IS POSTED ON SITE - VALID UNTIL 11/17/21 FIRE ALARM PANEL IS BLUE TAGGED - 10/09/20 FIRE EXTINGUISHERS ARE OPERATIONAL, IN PLACE AND TAGGED - OCT 2020 EMERGENCY ESCAPE MAPS ARE ALL POSTED IN PLACE IN EACH CLASSROOM K EXTINGUISHER BLUE TAGGED AND INSPECTED OCT 2020 ANSUL SYSTEM IS BLUE TAGGED - OCT 2020 GAS TEST CONDUCTED AND PASSED 1/8/20
7072 | VENT HOODS MUST BE CLEANED AT TIMELY INTERVALS - ALL CLEANINGS MUST BE RECORDED AND DOCUMENTS KEPT ON SITE
7073 | VENT HOODS MUST BE CLEANED AT TIMELY INTERVALS - ALL CLEANINGS MUST BE RECORDED AND DOCUMENTS KEPT ON SITE
7074 | FIRE DRILLS MUST BE CONDUCTED MONTHLY IN COMPLIANCE WITH MONTHLY FIRE DRILLS - LAST CONDUCTED 01/2020; THE BUILDING HAS ONLY EMPLOYEES AND NO STUDENTS AFTER THIS DATE DUE TO COVID-19 RESTRICTIONS IT IS SUGGESTED THAT MONTHLY FIRE DRILLS RESUME (TO PREPARE FOR THE RETURN OF STUDENTS) AND TO CONTINUE THE PRACTICE - PRACTICE MAKES PERFECT!
7075 | FIRE DRILLS MUST BE CONDUCTED MONTHLY IN COMPLIANCE WITH MONTHLY FIRE DRILLS - LAST CONDUCTED 01/2020; THE BUILDING HAS ONLY EMPLOYEES AND NO STUDENTS AFTER THIS DATE DUE TO COVID-19 RESTRICTIONS IT IS SUGGESTED THAT MONTHLY FIRE DRILLS RESUME (TO PREPARE FOR THE RETURN OF STUDENTS) AND TO CONTINUE THE PRACTICE - PRACTICE MAKES PERFECT!
7076 | NoData
7077 | NoData
7078 | PROVIDEEVIDENCE OF MONTHLY FIRE DRILLS – KEEP THESE RECORDS ON SITE FOR AT LEAST 3YEARS ENSURE FIRE DRILLS ARE CONDUCTED MONTHLY, WITHOUTFAIL
7079 | PROVIDEEVIDENCE OF MONTHLY FIRE DRILLS – KEEP THESE RECORDS ON SITE FOR AT LEAST 3YEARS ENSURE FIRE DRILLS ARE CONDUCTED MONTHLY, WITHOUTFAIL
7080 | VENT HOODS MUST BECLEANED AT TIMELY INTERVALS - ALL CLEANINGS MUST BE RECORDED AND DOCUMENTS KEPTON SITE
7081 | VENT HOODS MUST BECLEANED AT TIMELY INTERVALS - ALL CLEANINGS MUST BE RECORDED AND DOCUMENTS KEPTON SITE
7082 | NoData
7083 | NoData
7084 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
7085 | YOUR ATTENTION IS RESPECTFULLY CALLED TO THE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATED HEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORT MAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BE DISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORT IS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHER ENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FOR FIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
7086 | NoData
7087 | NoData
7088 | CITATIONS WILL BE ISSUED IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 30 DAYS
7089 | CITATIONS WILL BE ISSUED IF COMPLIANCE ISDISREGARDED OR NOT MET WITHIN 30 DAYS
7090 | NoData
7091 | NoData
7092 | NoData
7093 | NoData
7094 | NoData
7095 | NoData
7096 | NoData
7097 | NoData
7098 | NoData
7099 | NoData
7100 | NoData
7101 | NoData
7102 | NoData
7103 | NEE TO DO THE ANNUAL FIRE ALARM TESTING
7104 | P2 permit is expired. Expired on 2/1/2021. Amount owed 385.38 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
7105 | NoData
7106 | NoData
7107 | NoData
7108 | ACCEPTANCE TAG WITH MUST BE ATTACHED FOR PROOF OF TESTING
7109 | SYSTEM MUST BE CORRECTED FROM YELLOW TAG
7110 | NoData
7111 | NoData
7112 | NoData
7113 | NoData
7114 | NoData
7115 | NoData
7116 | NoData
7117 | NoData
7118 | NoData
7119 | NoData
7120 | Sprinkler heads busted at the home plate entrance of the diamond lot.2 domestics water lines in Union Station1- hose line at the left field gate.
7121 | Firetron is currently making repairs to the system.
7122 | COMPLY WITH ABOVE CODE
7123 | NEMO TAHIRI
7124 | TAGS AND LABLES SHALL NOT BE REMOVE BY RESTAURANT PERSONNEL.
7125 | COMPLY WITH ABOVE CODE
7126 | COMPLY WITH ABOVE CODE
7127 | COMPLY WITH ABOVE CODE.
7128 | A few ruptured sprinkler heads in the services area of the stadium Firetron is currently in the process of making the repairs.
7129 | I arrived on location to find 6 individual buildings in the apartment community. Three buildings have a red tagged fire alarm system and no water pressure in the sprinkler system. The remaining three buildings have no water pressure in the sprinkler system. I started an intervention form for an standby. I also initiated an in house fire watch agreement form.
7130 | No exits are blocked and aisle spacing is compliant with the fire code.
7131 | NoData
7132 | NoData
7133 | NoData
7134 | NoData
7135 | I arrived on location to find 6 individual buildings in the apartment community. Three buildings have a red tagged fire alarm system and no water pressure in the sprinkler system. The remaining three buildings have no water pressure in the sprinkler system. I started an intervention form for an standby. I also initiated an in house fire watch agreement form.
7136 | NoData
7137 | NoData
7138 | NoData
7139 | NoData
7140 | NoData
7141 | NoData
7142 | Repair ASAP.
7143 | The required permits shall be purchased within 2 weeks and maintained on site to avoid citations.
7144 | Obtain an L1: LPG operational permit and post on site for the storage and use of propane.Permits may be obtained at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811 www.houstonpermittingcenter.org
7145 | Obtain a P2: Public Assembly operational permit. This permit is required due to your facility's A-2 occupancy type with occupant load over 50 persons, as stipulated on the Certificate of Occupancy.Permits may be obtained at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811 www.houstonpermittingcenter.org
7146 | Correct all violations within 60 calendar days.
7147 | Provide documentation of damper test conducted within the last for years. If such documentation is not available, have dampers inspected and provide documentation that deficiencies were corrected.2/3/2021 - Dampers tested 3/11/2019. Repairs maid 2/1/2021 - OK
7148 | Maintain required ceiling clearance.
7149 | Remove all combustible items stored in electrical and mechanical rooms.
7150 | Provide documentation of fire extinguisher and fire code training.Training conducted 12/11/2020 - OK
7151 | Provide documentation of gas piping test conducted within the last five years.Gas test performed and passed 11/24/2020 - OK
7152 | Remove all multi-outlet power adapters that do not have built-in surge protection.
7153 | Provide Emergency Operations Plan for inspector to review.EOP OK
7154 | Some evacuation maps are old and faded. Update maps so that two egress routes are clearly visible.
7155 | Remove all curtains, drapes, fabrics, and combustible 3D decorations that do not have certificates of flame resistance from a certified testing laboratory.2/3/2021 - Certified applicator provided certificate for carpeted walls, decorative tree in theater, and blinds. Cert dated 12/31/2020 - OK.
7156 | Label all doors to electrical and mechanical rooms. If two doors must be opened to access equipment rooms (through laundry, for example) both doors must be labeled.
7157 | Have 90 minute egress lighting test performed and document correction of deficiencies.Repair any non-working exit signs2/3/2021 - Test conducted 12/8/2020. Repairs maid 12/30/2020 - OK
7158 | Remove drop pins from all perimeter gates.
7159 | Remove all items that restrict the width of exit corridors.
7160 | Your magnetic locks have never been approved through the City of Houston. Contact the building department using the information given to get your locks approved.Compliance by 2-19-2021
7161 | Your plastic bottles are considered high hazard commodities and maximum storage height for those products is 6 ft. unless approved for high piled storage. Lower all bottles and other plastic products to 6 ft and maintain that height unless approval occurs.Compliance by 2-19-2021
7162 | All buildings with designated letters per your Certificate of Occupancies shall be posted on the matching buildings.Compliance by 2-19-2021
7163 | Provide 2 Falcon Locks or Knox Boxes to replace the locks that no longer open on your front gates.Compliance by 2-19-2021
7164 | Secure all compressed gas bottles from the options listed above.Compliance by 2-19-2021
7165 | Have qualified door company perform annual drop test on all fire doors in your facility.Compliance by 2-19-2021
7166 | Have qualified sprinkler and alarm company perform annual testing on these systems.Compliance by 2-19-2021
7167 | All forklifts powered by propane or fuel shall have a tagged fire extinguisher mounted on the lift.Compliance by 2-19-2021
7168 | All fire extinguishers shall be mounted to a fixed object and not on floors.Compliance by 2-19-2021
7169 | Repair or replace all emergency lighting throughout your facility and provide documentation that all lights were working at that time.Compliance by 2-19-2021
7170 | Provide at least a 3 ft. clearance around all electrical boxes.Compliance by 2-19-2021
7171 | All exits lights shall be illuminated.Compliance by 2-19-2021
7172 | Remove all objects blocking the direct path to exits in the locations listed.Immediate compliance required.
7173 | Repair ASAP.
7174 | NoData
7175 | The following annual operational permits shall be obtained and posted on site within 2 weeks:-P2: Public Assembly (101-299 occupants)-Fire Alarm PermitPermits are available at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811 www.houstonpermittingcenter.org
7176 | NoData
7177 | NoData
7178 | NoData
7179 | NoData
7180 | NoData
7181 | NoData
7182 | NoData
7183 | No violations to facility at this time. All fire preventive measures are in place and in acceptable working order.
7184 | Expired permits please update permits that have expired.
7185 | Daily inspection of the warming centers in halls C and D. The aisles are being maintained and no exits are blocked.
7186 | NoData
7187 | NoData
7188 | NoData
7189 | NoData
7190 | NoData
7191 | NoData
7192 | NoData
7193 | NoData
7194 | NoData
7195 | NoData
7196 | NoData
7197 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
7198 | NoData
7199 | NoData
7200 | NoData
7201 | NoData
7202 | NoData
7203 | Repair ASAP.
7204 | Repair ASAP.
7205 | NoData
7206 | NoData
7207 | INSTALL A 4A-80BC PORTABLE FIRE EXTINGUISHER NEAR INSIDE OF THE STORE NEAR THE ENTRANCE/EXIT DOOR FOR THE GAS PUMPS
7208 | INSTALL A PORTABLE FIRE EXTINGUISHER INSIDE OF THE STORE FOR THE NORMAL COMBUSTIBLES INSID OF THE STORE
7209 | INSTALL A EXIT SIGN OVER THE ENTRANCE/EXIT DOOR
7210 | KEEP A CLEARANCE OF AT LEAST 30 INCHES FROM AROUND THE ELECTRICAL PANEL BOXES. REMOVE ALL BOXES AND COMBUSTIBLES FROM THE ELECTRCAL PANEL BOX(ES)
7211 | PROVIDE A CURRENT M3(FUEL DISPENSE) PERMIT, 1002 WASHINGTON AVE. 832-394-8811
7212 | POST THE ORIGINAL CERTIFICATE OF OCCUPANCY FROM THE BUILDING DEPT. 1002 WASHINGTON AVE. 832-394-8811
7213 | NoData
7214 | NoData
7215 | NoData
7216 | NoData
7217 | NoData
7218 | MAKE SURE ALL PORTABLE FIRE EXTINGUISHERS HAVE A CURRENT INSPECTION TAG ON THEM
7219 | MAKE SURE BOTH THE LEFT AND RIGHT SIDE MAIN EXIT DOORS REMAIN UNLOCKED DURING BUSINESS HOURS
7220 | REPLACE MISSING CEILING TILES IN THE BACK ROOM
7221 | LABEL THE DOOR WITH THE ELECTRICAL PANEL BOX IN IT "ELECTRICAL PANEL INSIDE"
7222 | APPLY FOR THE M3(FUEL DISPENSER) PERMIT AT 1002 WASHINGTON AVE. 832-394-8811
7223 | APPLY FOR AND POST THE ORIGINAL CERTIFICATE OF OCCUPANCY. APPLY AT 1002 WAHSINGTON AVE. 832-394-8811
7224 | PROVIDE A 3A 80BC PORTABLE FIRE EXTINGUISHER NEAR THE MAIN ENTRANCE OF THE STORE PROVIDE A 2A 10BC PORTABLE FIRE EXTINGUISHER FOR THE INSIDE OF THE STORE
7225 | INSTALL AN EXITI SIGN ABOVE THE MAIN ENTRANC/EXIT DOOR
7226 | REMOVE ALL BOXES FROM AROUND THE ELECTRICAL PANEL, PROVIDE AT LEAST 30 INCH CLEARANCE FROM ELECTRICAL PANELS
7227 | PROVIDE THE ORIGINAL CERTIFICATE OF OCCUPANCY
7228 | PROVIDE A CURRENT M3 (FUEL DISPENSING) PERMIT, 1002 WASHINGTON AVE. 832-394-8811
7229 | NoData
7230 | NoData
7231 | NoData
7232 | NoData
7233 | NoData
7234 | NoData
7235 | NoData
7236 | NoData
7237 | NoData
7238 | NoData
7239 | NoData
7240 | NoData
7241 | NoData
7242 | NoData
7243 | NoData
7244 | NoData
7245 | NoData
7246 | NoData
7247 | No violations found.
7248 | Please renew the K1, key box permit.Expired 1/25/21.
7249 | NoData
7250 | NoData
7251 | NoData
7252 | NoData
7253 | NoData
7254 | NoData
7255 | Compliance: 30 calendar days.
7256 | NoData
7257 | NoData
7258 | NoData
7259 | NoData
7260 | Extinguishers must tested and tagged by licensed company
7261 | Must be updated and readily available
7262 | Must be updated and readily available
7263 | Exit doors and sleeping units must not have key required locks for use.
7264 | Sleeping units must remove the additional window opening constraints
7265 | Extinguishers must tested and tagged by licensed company
7266 | NoData
7267 | NoData
7268 | NoData
7269 | A Fire Department stand-by may be required if red-tagged system is not serviced in a timely manner.
7270 | Fire alarm system is red tagged and must be serviced within 72 hours
7271 | Failure to service red tagged systems will be subject to citations and re-inspection fees.
7272 | A Fire Department stand-by may be required if red-tagged system is not serviced in a timely manner.
7273 | Fire alarm system is red tagged and must be serviced within 72 hours
7274 | Failure to service red tagged systems will be subject to citations and re-inspection fees.
7275 | NoData
7276 | NoData
7277 | NoData
7278 | NoData
7279 | NoData
7280 | All fire extinguishers shall be inspected, tagged, and mounted.
7281 | All fire extinguishers shall be inspected, tagged, and mounted.
7282 | ELEVATOR ROOMS NEED CLEANED
7283 | No storage allowed in FCC ROOM
7284 | All doors shall be self closing and latching
7285 | Need to replace stuck closed lock on garage walk-in gate.
7286 | Binder shall remain in the FDB and updated
7287 | Binder shall remain in the FDB and updated
7288 | Binder shall remain in the FDB and updated
7289 | ALL DOORS SHALL BE SELF CLOSING AND LATCHING
7290 | ALL DOORS SHALL BE SELF CLOSING AND LATCHING
7291 | Need to pay all required permits
7292 | All doors in high rise should be self closing and latching
7293 | Need to add elevator evacuation sign to 1st floor
7294 | NoData
7295 | NoData
7296 | Where required, an approved box that contains: emergency keys; access door loc or barrier release or deactivation devices; and may in addition contain such information as required by the fire department to affect safe and ready access property, building or structure in event of an emergency
7297 | A Fire Marshal Approval permit is required to install and maintain access co gates and barriers on private drive, street, or road.
7298 | NoData
7299 | The gate shall be twenty (20) feet in width. A 9-1-1 Box and a Fail- safe shall be installed on the gatepost at a height not to exceed five (5) feet. W approved by the code official, the 9-1-1 Box and the Fail-safe Box may be
7300 | Construction documents for proposed fire apparatus access and access control gate/barriers shall be submitted. Gates/barriers must remain open at all times until a fire prevention inspector a final on- site inspection and approval.
7301 | A manual operation of electronic slide or swing gates that can be used in the power failure or equipment malfunction
7302 | An approved 9-1-1 padlock applied to 9-1-1 gate operations.
7303 | NoData
7304 | A gate operation or function such as manual, electronic, swing arm, chain driv devices such as a card reader, key pad, telephone; direction of gate swing, fa methods.
7305 | A permit is required to install and maintain a fire apparatus access-control g barrier on a fire apparatus access road, or a private drive or private street for fire apparatus access. A permit is also required to install and maintain Key Box; this permit shall be renewed annually.
7306 | Unapproved gates/barriers shall mean those gates/barriers that do not have wr approval from the Fire Marshal,
7307 | The owner/occupant is responsible for correcting all violations listed in this report.
7308 | Have yellow tagged sprinkler system corrected and tagged.
7309 | Post the occupant load.
7310 | Remove obstructions in front of the fire extinguisher.
7311 | NoData
7312 | All emergency lights should function properly. The lights on the device should illuminate when tested or if the power goes out.
7313 | A hydrostatic test must be performed on the fire sprinkler system.
7314 | The ceiling tile in the fire sprinkler room must be put back into place.
7315 | NoData
7316 | NoData
7317 | The vent hood is due for cleaning.
7318 | Secure the compressed gas cylinders.
7319 | Provide filler plates for the openings in the breaker panel. Replace the missing cover on the breaker panel.
7320 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
7321 | NoData
7322 | NoData
7323 | Ensure the side exit is unlocked and free from obstructions while the building is occupied.
7324 | Have a licensed fire protection company perform an annual fire alarm inspection before the end of 01/2021.
7325 | NoData
7326 | NoData
7327 | Have a licensed fire protection company perform a 5 year FDC test and correct any deficiencies.
7328 | Secure the compressed gas cylinders.
7329 | Have a licensed fire protection company correct the deficiencies on the yellow tagged sprinkler system.
7330 | NoData
7331 | NoData
7332 | NoData
7333 | NoData
7334 | Fire extinguisher needs to be properly mounted.
7335 | Updated service tags and testing needed.
7336 | All required service tags need to be updated and provide documentation on test results.
7337 | Needs service tag.
7338 | NoData
7339 | All need to be tested and documentation showing pass or fail.
7340 | HVAC need to have dampers tested or if smokes are in the system documentation must be provided.
7341 | Updated services tags required.
7342 | Required service tags needed
7343 | Provide updated P2 permit
7344 | House keeping In storage room removed. Exit door to the public way needs to be corrected and open without problem. All storage under stairway needs to be removed.
7345 | Fire extinguisher needs to be properly mounted.
7346 | Updated service tags and testing needed.
7347 | All required service tags need to be updated and provide documentation on test results.
7348 | Needs service tag.
7349 | NoData
7350 | All need to be tested and documentation showing pass or fail.
7351 | HVAC need to have dampers tested or if smokes are in the system documentation must be provided.
7352 | Updated services tags required.
7353 | Required service tags needed
7354 | Provide updated P2 permit
7355 | House keeping In storage room removed. Exit door to the public way needs to be corrected and open without problem. All storage under stairway needs to be removed.
7356 | NoData
7357 | NoData
7358 | NoData
7359 | All commercial kitchen vent hoods, exhaust ducts, exhaust fans and appurtenances shall be cleaned and inspected by approved personnel and in accordance with manufacturer s guideline, as often as necessary to insure against excess grease accumulations. Have hood retagged or provide proof of cleaning.
7360 | All fire extinguishers shall have a current annual inspection tag by an approved licensed fire protection equipment company.
7361 | Comply with the above code.
7362 | Comply with the above code.
7363 | Check all EXIT/Emergency lights. Fix or replace any inoperable lights.
7364 | Comply with the above code.
7365 | Portable fire extinguishers having a gross weight not exceeding 40 pounds shall be installed so that the top of the extinguisher is not more than 5 feet above the floor. In no case shall the clearance between the bottom of the extinguisher and the floor be less than 4 inches.
7366 | All Assembly, Educational, Institutional and Residential R-1, R-2 and R-4, occupancies (as defined in the Building Code, 2000 edition International Building Code as amended) shall have a test of the building s natural gas system(s), to check for leakage, at least every 5 years. The last gas test had been completed 5-18-15.
7367 | Citations shall be issued on the third re-inspection if all violations are not corrected.
7368 | Check all EXIT/Emergency lights. Fix or replace any inoperable lights.
7369 | NoData
7370 | F-7 Fuel storage permit is required for a tank of used cooking oil storage greater than 60 gallons.
7371 | Provide light covers in compliance with the above code.
7372 | All Assembly, Educational, Institutional and Residential R-1, R-2 and R-4, occupancies (as defined in the Building Code, 2000 edition International Building Code as amended) shall have a test of the building s natural gas system(s), to check for leakage, at least every 5 years. The last gas test had been completed 5-18-15.
7373 | Re-inspection fees shall be issued on the second re-inspeciton if all violations are not corrected.
7374 | NoData
7375 | Fire extinguishers annual inspection due at the end of this month
7376 | Sprinkler riser last inspection November 2017Bring up to code
7377 | NoData
7378 | NoData
7379 | NoData
7380 | Fire alarm panel YELLOW TAGGED System in trouble mode and silenced72 hrs to bring up to code
7381 | Ansul system due at the end of this month
7382 | Remove pallets from electrical room.Can not be stored inside school
7383 | NoData
7384 | K1-911 box permit expired 3-24-2020
7385 | NoData
7386 | P2-Place of Assembly permit expired March 24-2020
7387 | NoData
7388 | INFORMATION
7389 | INFORMATION
7390 | INFORMATION
7391 | NEED ANNUAL INSPECTION ON FIRE EXTINGUISHERS.9-19-19
7392 | LAST EMERGENCY LIGHTING TEST 1-15-2020BRING UP TO CODE
7393 | SPRINKLER RISER LAST INSPECTION 9-4-2017BRING UP TO CODE
7394 | AS PER CODE
7395 | NoData
7396 | Please renew your Access Gate (a4) permit that expired on 01/30/2021.All questions concerning invoice and payment shall be answered by the HPC office at 832-394-8811 (dial "0") when you hear the recording.
7397 | NoData
7398 | NoData
7399 | Please renew your key box (k1) permit that expired on 02/06/2021. Any questions you may have regarding invoice and/or payment can be answered by the HPC office at 832-394-8811 (then dial "0").
7400 | Repair ASAP.
7401 | Repair ASAP.
7402 | Inspect and Service tag commercial kitchen hood system. Correct all red tag impairments immediately.
7403 | NoData
7404 | NoData
7405 | NoData
7406 | The 911 key has been repaired.
7407 | replace missing spacer
7408 | Label sprinkler room
7409 | Repair missing sheetroom
7410 | Service yellow tag
7411 | NoData
7412 | NoData
7413 | NoData
7414 | NoData
7415 | ADD ELEVATOR CAR NUMBERS AS SPECIFIED
7416 | NoData
7417 | NoData
7418 | NoData
7419 | ADD SIGNAGE FOR FIRE EXTINGUISHERS
7420 | UPDATE FDC SIGN AT STREET
7421 | PLACE RED OILY RAG CAN IN ELEVATOR CONTROL ROOM
7422 | MAINTAIN PERMIT ON HAND
7423 | NoData
7424 | ADD REQUIRED SURVEYS, ADD SUPPLEMENTAL INFORMATION, UPDATE ELEVATOR MATRIX
7425 | UPDATE KEY SETS
7426 | INSTALL SIGN FOR ROOF TOP TEST CONNECTIONS
7427 | NoData
7428 | ADD ELEVATOR LOCKOUT/TAG OUT KITS
7429 | CORRECT "ROOF ACCESS" INDICATION ON STAIR WELL SIGNS
7430 | NoData
7431 | MAINTAIN PERMIT ON HAND
7432 | EVACUATION MAP GROUND LEVEL ELEVATOR LOBBY
7433 | NoData
7434 | Please renew expired key box (k1) permit that expired on 04/01/2018. Also, contact the HPC office at 832-394-8811 (dial "0" upon hearing recording) and acquire what years are expired. You may have to pay for expired (k1) permits for years 2018 thru 2021. Also, this would be a good time to check on your Access Gate permit as well.
7435 | NoData
7436 | NoData
7437 | NoData
7438 | provide and install an official spray booth for spraying of flammable or combustible liquids with out a permit
7439 | provide and install one 2a 10bc fire extinguisher and mount in front office
7440 | provide an extra key from your gate lock and falcon lock for 911 emergency key box
7441 | NoData
7442 | inside of opening door
7443 | 2nd Notice Permit Expired 12/20/2020; Unpaid Fees $266.80. Payment must be made within 10 days or a citation will be issued for failure to maintain a required operational permit.
7444 | NoData
7445 | Your firefighter access road has faded in the rear of the building. Paint over the lines so that they are visible and maintain a clear path inside these lines.Compliance by 2-12-2021
7446 | Secure all argon and propane bottles in one of the ways listed.Compliance by 2-12-2021
7447 | Provide an approved cover plate over the open electrical near the chiller room.Compliance by 2-12-2021
7448 | Have qualified door company perform annual drop test on all fire doors.Compliance by 2-12-2021
7449 | Have qualified fire extinguisher company place a tagged extinguisher on all forklifts powered by propane or fuel.Compliance by 2-12-2021
7450 | Provide aisles around the warehouse so that making it to exits is not blocked.Aisles between racks shall not be blocked unless restocking is going on. At this time at least half the aisle shall remain clear.Compliance by 2-12-2021
7451 | Provide documentation that all emergency lights have been tested and are working at that time.Compliance by 2-12-2021
7452 | Remove the lock on the exit at the front of the building a maintain that door unlocked while the building is occupied.Immediate compliance required.
7453 | Remove the letters HFD on all doors that don't lead into the high piled area.Compliance by 2-12-2021
7454 | Remove all pallets and other objects blocking the width of your firefighter access road in the rear of the building.Compliance by 2-12-2021
7455 | Remove all objects blocking a clear means of egress to all exits and on the outside of all exits so that a clear path away from the building is provided.Immediate compliance required.
7456 | For the failure to abate the following violations: Obtaining a 911 key box permit, the removal of all drop bars and installation of approved locks/latches
7457 | APPLY FOR AND OBTAIN A HFD KEY BOX PERMIT (K1) FROM THE CITY OFHOUSTON PERMIT CENTER LOCATED AT 1002 WASHINGTON AVE. (832)394-9000. COMPLIANCE WITHIN 30 DAYS
7458 | FOLLOW CODE REFERRED TO ABOVE CONCERNINGLOCKS OR LOCKING MAIN ENTRANCE.COMPLIANCE WITHIN 30 DAYS
7459 | NoData
7460 | NoData
7461 | NoData
7462 | NO VIOLATIONS FOUND AT THIS TIME
7463 | NoData
7464 | NoData
7465 | NoData
7466 | Annual Fire Alarm Test was done January 2020. Recent one is requiredtest date 2-3-2021 by Constant Security
7467 | COMPLIANCE DATE 15 CALENDAR DAYS
7468 | (H3) fire prevention permit is expired at this time.
7469 | NoData
7470 | ALL YELLOW AND RED TAG ISSUES MUST BE CORRECTED
7471 | NoData
7472 | NoData
7473 | NoData
7474 | A few ruptured sprinkler heads in the services area of the stadium Firetron is currently in the process of making the repairs. The sprinkler heads are been fixed(2/23/21)
7475 | The fire alarm panel must have an annual inspection performed on it.
7476 | An audibility test must be performed on the fire alarm system.
7477 | A sensitivity test must be performed on the fire alarm system.
7478 | The fire alarm permit must be renewed.
7479 | Please renew the A4, access gate permit.Expired 2/3/21.
7480 | NoData
7481 | apply for a certificate at 1002 washinton and post
7482 | apply for a flammable and comustible liguid permit type f-7
7483 | All spare propane bottles shall be stored outside of building in cages 10 ft. away from buildingCompliance: 30 calendar days.
7484 | Move all dumpsters at least 10 ft. away from building.Compliance: 30 calendar days.
7485 | Compliance: 30 calendar days.
7486 | Have a licensed fire protection company perform an annual inspection on the sprinkler system and correct any deficiencies.
7487 | Have a licensed fire protection company perform a 5 year FDC test and correct any deficiencies.
7488 | Vent hoods are due for cleaning.
7489 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
7490 | Repair the front exit doors to ensure they swing in the direction of egress.
7491 | Repair or replace inoperable emergency illumination.
7492 | Remove bolt locks from the front exit doors.
7493 | NoData
7494 | NoData
7495 | NoData
7496 | NoData
7497 | NoData
7498 | NoData
7499 | NEED TO BE SERVICE 5-16-2019 LAST DATE
7500 | NEED TO BE SERVICE 1-2020 LAST DATE
7501 | NEED TO BE SERVICE 2-2020 LAST DATE
7502 | NEED TO BE SERVICE 2-2020 LAST DATE
7503 | NEED TO GET A GAS TEST DONE. SMELL OF GAS IN THE BUILDING
7504 | Please clear out anything blocking the rear exits, including boxes, shelving, and other obstructions. Make sure all marked exits are clear of obstructions.
7505 | It is the owner/occupants responsibility to correct all fire code violations.
7506 | Must secure compressed gas containers to a fixed object with chain, rope, or other material to prevent containers from falling.
7507 | Have someone inspect, test, and repair all exit signs and make sure they are illuminated correctly and the backup batteries will illuminate the signs during a power outage.
7508 | Fire Alarm Is Red Tagged.72 Hour Notice Issued Self Fire Watch inplace
7509 | NoData
7510 | NoData
7511 | NoData
7512 | THE SCHOOL BEEN CLOSED DOWN SENSE MAY OF 2019. SANDRA JOLIVET 713-747-7800. EMAIL STPETERCC@SBCGLOBAL.NET
7513 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
7514 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
7515 | Provide documentation/report for fire damper testing and any necessary repairs.
7516 | Correct Monitor alert on Fire Alarm Panel
7517 | Provide Boiler permits: 268216, 186202
7518 | Provide "Exit Sign" on stage and back door
7519 | Fire Alarm Red Tagged Impaired72 Hour Notice IssuedSelf Fire Watch initiated 2-22-21
7520 | Fire Alarm Red TagMaintain Self Fire Watch until fire protection systems are back in normal service.
7521 | NoData
7522 | P2 permit is expired. Expired on 1/24/2021. Amount owed for permit 385.38 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
7523 | Fire Alarm is Red Tagged ImpairedFire Sprinkler System is out of service and out of date.Maintain Self Fire-watch until systems are back in regular service.
7524 | NoData
7525 | NoData
7526 | NoData
7527 | NoData
7528 | NoData
7529 | NoData
7530 | NoData
7531 | NoData
7532 | NoData
7533 | NoData
7534 | NoData
7535 | Have all fire extinguishers inspected annually.
7536 | Exits must be clear of obstructions.
7537 | Reposition or remove desk in front of warehouse exit.
7538 | Store propane outside of building.
7539 | NoData
7540 | The occupant/owner of the business is responsible for correcting all fire code violations.
7541 | Must clean up the trash and rubbish accumulation inside and outside the business. Wood, plastic, paper products, and clutter.
7542 | Must correct the hanging light in the bathroom. Fixture must be correctly connected to the ceiling and no wiring exposed.
7543 | Must replace missing or damaged sheetrock in the office area hallway and bathroom.
7544 | Must repair exit sign in the office that is not illuminated correctly.
7545 | Permit Expired 1/24/2021; Unpaid Fees $266.80
7546 | NoData
7547 | NoData
7548 | NoData
7549 | NoData
7550 | NoData
7551 | NoData
7552 | NoData
7553 | NoData
7554 | NoData
7555 | Site plan has been submitted and approved for the city of Houston event in Ballrooms A and B.
7556 | The George R Brown has an annual assembly permit
7557 | Event manager has submitted site plan for the event and the plan has been approved
7558 | The GRB has an annual Assembly permit.
7559 | NoData
7560 | NoData
7561 | NoData
7562 | The vent hood suppression system is due for service before the end of 03/2021.
7563 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
7564 | Repair the broken emergency illumination in the dining area.
7565 | Remove bolt latch from the rear exit door. Repair panic hardware if necessary.
7566 | NoData
7567 | NoData
7568 | NoData
7569 | NoData
7570 | NoData
7571 | NoData
7572 | NoData
7573 | NoData
7574 | NoData
7575 | Have the required annual inspection/service performed on all extinguishers in the facility by a certified fire protection company, nd ensure that new hang tags are put in place.
7576 | NoData
7577 | Proof of gas test needed.
7578 | NoData
7579 | NoData
7580 | NoData
7581 | the installed fire lane requires approval;fire lane plans required and fire lane signs required for the fire lane
7582 | label the main electrical room on the outside near generator and label door#b215 that leads to the electrical room
7583 | floor plans required for all classroms
7584 | NoData
7585 | NoData
7586 | a4 access gate permit; k1 key box permit; 15 firelane permit
7587 | remove obstructions in the exit path near kindergarten area
7588 | NoData
7589 | NoData
7590 | re-inspection fee for expired Kitchen hood systemlast inspected 12/2018
7591 | last annual 1/2019
7592 | last semi-annual 12/2018
7593 | NoData
7594 | NoData
7595 | NoData
7596 | Obtain a flammable combustible liquids permit from the Houston Permitting Center.
7597 | NoData
7598 | The MAQ for 1B and 1C liquids is 120 gallons (MAQ can increase to 240 gallons if stored in approved storage cabinets).The MAQ for class 2 liquids is 240 gallons (MAQ can increase to 480 if stored in approved storage cabinets). Amounts greater than the MAQ are to be removed from the building.
7599 | NoData
7600 | Outdoor storage for flammable liquids.
7601 | Required to increase MAQ.
7602 | NoData
7603 | NoData
7604 | NoData
7605 | NoData
7606 | MAQ for outdoor storage is 1100 gallons. Minimum distance to lot line is 50 ft.. Minimum distance to street is 10 ft..
7607 | Required for outdoor storage.
7608 | Required for outdoor storage.
7609 | Required for outdoor storage.
7610 | Required for outdoor storage.
7611 | Class 1A liquid containers are required to be less than a 5.3 gallon capacity for gravity dispensing.
7612 | NoData
7613 | Provide a "fail safe" for the access gate.
7614 | A key box is required near the keypad that will open the access gate.
7615 | Obtain a key box and access gate permit from the Houston Permitting Center.
7616 | Have SDS forms readily available on site.
7617 | Continue the process of obtaining your Certificate of Occupancy.
7618 | NoData
7619 | NoData
7620 | NoData
7621 | NoData
7622 | NoData
7623 | NoData
7624 | NoData
7625 | NoData
7626 | ENSURE ALL OPEN ELECTRIC COTROL PANELS AND JUNCTION BOXES ARE CLOSED/COVERED
7627 | RED OILY RAG CAN SHOULD BE EMPTYIED DAILY (AFTER USE)
7628 | ARRANGE KEY SETS IN ACCORDANCE WITH LSB 6 IN RESOURCES PROVIDED
7629 | SEAL ALL PENETRATIONS IN ELECTRIC AND MECHANICAL ROOMS
7630 | ENSURE ROOF RISER TEST CONNECTION HAS PROPER SIGNAGE
7631 | NoData
7632 | LOCKOUT TAG OUT IN GARAGE
7633 | ENSURE PROPER OPERATION OF MAGLOCKS DURING EMERGENCY AND HAVE CERT/STICKER PLACED
7634 | INSTALL APPROVED STAIRWAY SIGNS IN ACCORDANCE WITH APPENDIX H IN THE RESOURCES PROVIDED
7635 | Inspect and Service tag commercial kitchen hood system. Correct all red tag impairments immediately.
7636 | NoData
7637 | NoData
7638 | NoData
7639 | NoData
7640 | INFORMATION ONLY.
7641 | REPAIR ALARM SYSTEM ASAP.
7642 | INFORMATION ONLY.
7643 | INFORMATION ONLY.
7644 | NoData
7645 | NoData
7646 | COMPLIANCE DATE: 15 CALENDAR DAYS
7647 | a4 and k1 fire prevention permit is expired at this time.
7648 | NoData
7649 | NoData
7650 | NoData
7651 | NoData
7652 | NoData
7653 | RESTAURANT IS DUE FOR ITS 5 YEAR NATURAL GAS LEAK TEST.
7654 | BEFORE GAS TEST IS PERFORMED, A PERMIT MUST BE OBTAINED FROM THE HOUSTON PERMITTING OFFICE.
7655 | HAVE ALL EMERGENCY ILLUMINATION LIGHTS THAT ARE NOT IN WORKING ORDER REPAIRED OR REPLACED.
7656 | OBTAIN COPY OF CERTIFICATE OF OCCUPANCY AND POST ON IN A LOCATION THAT IS READILY AVAILABLE FOR INSPECTION.
7657 | NoData
7658 | Post the occupant load.
7659 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
7660 | NoData
7661 | NoData
7662 | NoData
7663 | NoData
7664 | The fire alarm control unit was found to have a yellow tag attached. Contact a licensed fire protection to correct the violations and ensure a current service tag reflecting the corrections made is attached.
7665 | 2nd Notice Permit Expired 12/4/2020; Unpaid Fees $385.38
7666 | NoData
7667 | NoData
7668 | THERE ARE NO KEYS IN THE KEY BOX AT MAIN ENTRANCE
7669 | re-inspection fee for expired fire sprinkler system
7670 | ANNUAL FIRE SPRINKLER REQUIRED LAST INSPECTION 7/2017 NOTED ON 2018 REPORT
7671 | NoData
7672 | K-1 permit is expired. Renew permit per code.
7673 | NoData
7674 | NoData
7675 | NoData
7676 | NoData
7677 | NoData
7678 | NoData
7679 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
7680 | MAINTAIN FIRE ALARM SYSTEM AT ALL TIMES. REPAIR ALL TROUBLE/SUPERVISORY ALARMS.
7681 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES. KEEP PLANS UPDATED AND TRAIN QUARTERLY.
7682 | Have a licensed fire protection company service and tag the fire extinguishers.
7683 | Ensure the swinging door isn't propped open blocking the fire extinguisher. Move the fire extinguisher if necessary.
7684 | Remove locking bars from exits while the building is occupied. Repair door hardware if necessary.
7685 | Mount the fire extinguisher that's been placed on the ground.
7686 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
7687 | Clear and maintain space in front of the breaker panels.
7688 | Post the occupant load.
7689 | Fire Alarm Is Impaired Fire Sprinklers are out of serviceSelf Fire Watch established, Maintain self fire watch until all FP systems are in regular service.
7690 | NoData
7691 | NoData
7692 | Replace missing light covers.
7693 | Fire extinguishers must be inspected and tagged annually.
7694 | Place fire extinguisher on bracket.
7695 | Replace missing cover plate.
7696 | NoData
7697 | NoData
7698 | Provide current K1 keybox permit
7699 | Replace missing 911 falcon lock, repair toggle switch in 911 key box.
7700 | Repair ASAP.
7701 | Repair ASAP.
7702 | Renew oil storage permit
7703 | Replace missing cover plate
7704 | All fire extinguishers must be inspected annually
7705 | Propane tanks must be stored outside.
7706 | Fire Sprinkler System is out of service.Maintain the prior established self fire watch until all fire protection systems are in regular service.
7707 | NoData
7708 | NoData
7709 | Correct the deficiencies on the yellow tagged fire alarm panel and fire sprinkler system.
7710 | NoData
7711 | Yearly flow test is required on both F/H's.
7712 | Visually inspect the attic space for solid draft stop construction.
7713 | Three "HFD 2" all weather signs are required on the outside of all emergency gates.
7714 | See Fire Marshal's Statement of Compliance form
7715 | Please Purchase a Access Gate (a4) permit at 1002 Washington Avenue, Houston Tx. 77002 or call 832-394-8811.
7716 | Please Purchase a Key Box (k1) permit at 1002 Washington Avenue, Houston Tx. 77002 or call 832-394-8811.
7717 | Please add a 911 Falcon lock on back gate for HFD access
7718 | NoData
7719 | Have vent hood professionally inspected and cleaned. Ensure inspection sticker is placed on the hood.
7720 | Clear and maintain clearance in front of the breaker panels.
7721 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit prior to test.
7722 | NoData
7723 | All sprinkler heads shall be free from all obstructions.
7724 | Compliance: 30 calendar days.
7725 | Issued permits shall be kept on the premises designated therein at all times and shall be readily available for inspection.Compliance: 30 calendar days.
7726 | NoData
7727 | NoData
7728 | NoData
7729 | all fire extinguishers
7730 | post numbers
7731 | post a copy of the certificate of occupancy at main office bldg.
7732 | Event manager has submitted a site plan for the location of the L.P. Heaters for the Event.
7733 | Minute Maid Park holds an annual L.P Gas Permit for the use of L.P. Gas appliances at the stadium. The permit is valid until January of 2022.
7734 | Informed the event manager that fire extinguishers will need to be placed at various locations on the field and the main concourse for the use of the L.P. Gas appliances.
7735 | Met with the event manager to inform her of the need for and Inspector standby permit for the use of the L.P. Gas appliances inside the stadium.
7736 | NEED TO ADD INSTALLATION TAG TO FIRE ALARM SYSTEM
7737 | NEED TO ADD INSTALLATION TAG TO FIRE PUMP AND SPRINKLER SYSTEM
7738 | NEED TO ADD 911 BOX TO STAIRWELL B AND COMMERCIAL SUITS
7739 | NEED TO ADD A 911 BOX TO STAIRWELL C AND NEED TO ADD A SIGN LABELING STAIRWELL C (EXTERIOR)
7740 | NEED TO ORGANIZE THE BINDER IN THE FDB AS PER (LSB STANDARD 6)
7741 | NEED TO ADD A LOCK OUT/TAG OUT KIT TO ELEVATOR ROOM
7742 | NEED TO PAY FOR ALL PERMITS REQUIRED, INCLUDING FLAMMABLE LIQUID (F7)
7743 | NEED TO ADD EVACUATION SIGNS (EVERY FLOOR AND ELEVATOR)
7744 | NEED TO LABEL STAIRWAY (C) ON EXTERIOR SIDE
7745 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
7746 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
7747 | Provide documentation/report for fire damper testing and any necessary repairs.
7748 | NoData
7749 | 1st floor Mech Room Fire Extinguisher obstructed by PVC Pipe.
7750 | NoData
7751 | Provide Current Inspection Tag for all Red Tag Fire Extinguishers.
7752 | 3rd Floor East Mechanical Room.
7753 | Provide updated Emergency Contact List and Mobility Impaired List.
7754 | 1st Floor Electrical Room/Mechanical Room.
7755 | 4th floor west mechanical room. two holes in sheetrock. Reposition Ceiling Tile (Stair 3-B).
7756 | Replace or Repair existing Fire Pump Room Sign.
7757 | 1st floor mechanical room (PVC Pipe).
7758 | NoData
7759 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
7760 | THE ALARM SYSTEM MUST BE TESTED AND MAINTAINED AT ALL TIMES. REPAIR ALL SUPERVISORY/TROUBLE ALARMS.
7761 | KEEP FIRE DRILL RECORDS ON PROPERTY AT ALL TIMES.
7762 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES. KEEP PLANS UPDATED PER THE CODE AND TRAIN QUARTERLY.
7763 | Your high piled storage (h2) permit expired on 2-9-2021. Renew this permit by following the directions on the expired permit renewal form by the date listed on the form.
7764 | Provide a approved electrical cover plate over the outlet near the restrooms in the warehouse.Compliance by 3-24-2021
7765 | All forklifts powered by propane shall have a tagged mounted fire extinguisher.Compliance by 3-24-2021
7766 | All firefighter access doors leading into the high piled area shall be keyed alike and access to these doors required.Compliance by 3-24-2021
7767 | Have qualified sprinkler company address the yellow tag issues on the riser and bring system back into compliance.Immediate compliance required.
7768 | Have qualified alarm company perform annual inspection on the fire alarm panel.Immediate compliance required.
7769 | Provide a FDC sign above the connection using the guidelines in this section.Compliance by 3-24-2021
7770 | All firefighter access doors leading into the high piled area shall have the letters HFD in the upper left hand corner on the outside of the doors.Compliance by 3-24-2021
7771 | Must have a licensed fire equipment inspection company inspect and tag all portable fire extinguishers.
7772 | Must have a current tagged portable fire extinguisher mounted on all fork lifts in use with a 10 B:C rating.
7773 | It is the owner's/occupant responsibility to correct all fire code violations prior to permit approval.
7774 | Must secure and cap all cylinders not currently secured or capped.
7775 | NoData
7776 | NoData
7777 | Permit Expired 1/24/2021; Unpaid Fees $266.80
7778 | NoData
7779 | Cover all open electrical boxes with approved cover plates.Compliance by 9-14-2020
7780 | Have qualified alarm/sprinkler company address your alarm panel that is red tagged and your sprinkler system that is yellow tagged and bring both into compliance.Submit a plan of action by 8-17-2020
7781 | All fire extinguishers shall be mounted on the hardware provided to a fixed object.Compliance by 9-14-2020
7782 | 6811 Silsbee has never been approved for high piled storage. Lower all product in the warehouse to 12 feet or below and maintain products at this height until this building has been upgraded and approved for high piled storage. Compliance by 9-14-2020
7783 | NoData
7784 | NoData
7785 | NoData
7786 | NoData
7787 | NoData
7788 | NoData
7789 | NoData
7790 | NoData
7791 | NoData
7792 | NoData
7793 | NoData
7794 | NoData
7795 | NoData
7796 | NoData
7797 | NoData
7798 | NoData
7799 | NoData
7800 | NoData
7801 | NoData
7802 | NoData
7803 | NoData
7804 | LAST INSPECTED 10/2019 - NEED CURRENT ANNUAL INSPECTION, AND 5YR IS DUE
7805 | PROVIDE COPY OF APPROVED HIGH PILE STORAGE PLANS, WHICH SHOULD BE MAINTAINED ON SITE PER ABOVE FIRE CODE
7806 | REMOVE BOLT LOCK - REPLACE WITH PANIC HARDWARE/APPROVED LOCKING/OPENING DEVICE PER ABOVE FIRE CODE
7807 | PER ABOVE FIRE CODE, MAINTAIN FIRE PROTECTION INSPECTION RECORDS FOR CODE OFFICIAL REVIEW
7808 | KEEP STORAGE CLEAR OF ELECTRICAL EQUIPMENT PER ABOVE FIRE CODE
7809 | It is the responsibility of the owner/management to correct these violations.
7810 | Red tags must be reported immediately. A non-functioning alarm panel can cause serious injury and high loss of life in an emergency scenario. This needs to be corrected immediately.
7811 | Protocol for reporting times when systems go out of service.
7812 | Fire alarm panel - annual inspection is required, and needs to pass. Red tags are not acceptable.
7813 | Alarm panel - Audibility test is needed. If one has been performed and has passed, we just need the compliance letter stating that.
7814 | Key-box needs correct keys to access building and info specifying location of FCC.
7815 | Fire depository box is the next priority after getting the red tag issue on the alarm panel addressed.
7816 | This is the basic guide for the binder in the Fire Depository Box. For a more in depth explanation, refer to LSB 6 in the original email attachments that were sent to you.
7817 | Place in the Fire depository box.
7818 | Key sets need to have the correct keys on them and need the required 5 sets.
7819 | 2 elevator hoistway door keys/tools are needed.
7820 | 2 independent service keys are needed.
7821 | Must be operational.
7822 | Keep all inspection and testing records for a minimum of 3 years.
7823 | Needs to function as it was intended to.
7824 | Upon completion of getting violations corrected, compliance letters are needed from the fire protection company that services the systems. Any active permits are also needed.
7825 | Fire alarm panel. If not corrected soon, approval through the fire department chain of command for a fire watch will be requested.
7826 | Provide a approved electrical cover plate over the outlet near the restrooms in the warehouse.Compliance by 3-24-2021
7827 | All forklifts powered by propane shall have a tagged mounted fire extinguisher.Compliance by 3-24-2021
7828 | All firefighter access doors leading into the high piled area shall be keyed alike and access to these doors required.Compliance by 3-24-2021
7829 | Have qualified sprinkler company address the yellow tag issues on the riser and bring system back into compliance.Immediate compliance required.
7830 | Have qualified alarm company perform annual inspection on the fire alarm panel.Immediate compliance required.
7831 | Provide a FDC sign above the connection using the guidelines in this section.Compliance by 3-24-2021
7832 | All firefighter access doors leading into the high piled area shall have the letters HFD in the upper left hand corner on the outside of the doors.Compliance by 3-24-2021
7833 | Provide a approved electrical cover plate over the outlet near the restrooms in the warehouse.Compliance by 3-24-2021
7834 | All forklifts powered by propane shall have a tagged mounted fire extinguisher.Compliance by 3-24-2021
7835 | All firefighter access doors leading into the high piled area shall be keyed alike and access to these doors required.Compliance by 3-24-2021
7836 | Have qualified sprinkler company address the yellow tag issues on the riser and bring system back into compliance.Immediate compliance required.
7837 | Have qualified alarm company perform annual inspection on the fire alarm panel.Immediate compliance required.
7838 | Provide a FDC sign above the connection using the guidelines in this section.Compliance by 3-24-2021
7839 | All firefighter access doors leading into the high piled area shall have the letters HFD in the upper left hand corner on the outside of the doors.Compliance by 3-24-2021
7840 | Repair the inoperable emergency illumination on the exit sign located at the side exit.
7841 | The fire extinguisher located under the bar is past due for service.
7842 | NoData
7843 | NoData
7844 | The assembly permit is due for renewal before the end of 03/2021.
7845 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
7846 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES. KEEP PLANS UPDATED PER CODE AND TRAIN QUARTERLY.
7847 | Permit Expired 1/5/2021; Unpaid Fees $266.80
7848 | NoData
7849 | Remove propane cage with spare containers outside 10 ft. away from building.Compliance: Immediately.
7850 | Fire protection systems shall be inspected, tested and maintained in accordance with the referenced standards listed in Table 901.6.1 and in accordance with Houston Fire Department LSB Standard No. 02, “Inspection and Testing of Fire Protection and Life-Safety Equipment” and LSB Standard No. 01, “Installation and Maintenance of Portable Fire Extinguishers.”Compliance: 30 calendar days.
7851 | Repair or replace all non working exit lights throughout warehouse.Compliance: 30 calendar days.
7852 | NoData
7853 | NoData
7854 | NoData
7855 | NoData
7856 | NoData
7857 | No violations at this time.
7858 | The owner/occupant is responsible for correcting all fire code violations.
7859 | Need to have an audibility test performed.
7860 | Need to have sensitivity test done every 2 years.
7861 | NoData
7862 | NoData
7863 | NoData
7864 | debris and old mattresses located beside dumpsters must be removed from property.
7865 | Fail safe" operation shall be installed on both electric slide gates
7866 | NoData
7867 | NoData
7868 | NoData
7869 | attic space shall be visually inspected for draft stop damage/integrity.
7870 | HFD 1" all weather 18"x18" sign installed on both access gtes
7871 | Please mark fire hydrant with a blue reflector
7872 | working smoke alarms located inside all bedrooms
7873 | exit gate requires a 'knox box" with toggle switch and secondary "fail safe" installed for emergency access.
7874 | Please have a "flow test" done on private fire hydrant that's located at Northeast corner of parking lot near Bldg. #2.
7875 | NoData
7876 | NoData
7877 | NoData
7878 | NoData
7879 | INFORMATION
7880 | INFORMATION
7881 | INFORMATION
7882 | LAST INSPECTION ON FIRE ALARM PANEL2-11-2020
7883 | LAST SPRINKLER RISER INSPECTION2-01-2020
7884 | NoData
7885 | NoData
7886 | NoData
7887 | NoData
7888 | NoData
7889 | NoData
7890 | NoData
7891 | NoData
7892 | Current inspection is January 2020. Fire extinguishers will need to be inspected and tagged in January 2021.
7893 | Must add two new 2A, 10:BC portable fire extinguishers. One in the office and another in the warehouse area as discussed.
7894 | Please make sure all exits are free from obstructions.
7895 | It is the owner/occupants responsibility to correct all fire code violations prior to follow up inspection.
7896 | Make sure the stacks of materials inside the warehouse are orderly and stable and maintain the 12' height inside the warehouse.
7897 | Make sure the materials in the attic are not within two feet of the ceiling and other storage materials that are within two feet of the ceiling as well.
7898 | All portable fire extinguishers must be in a well traveled and visible location.
7899 | Make sure all fire extinguishers are not obstructed and please make sure employees can identify where the fire extinguishers are with signs.
7900 | Make sure all exit signs are working properly and the battery back ups will keep exit signs illuminated during a power outage.
7901 | Please remove all combustibles from around electrical components listed above and provide the space around the components listed in the above fire code.
7902 | NO VIOLATIONS FOUND AT THIS TIME.
7903 | NoData
7904 | K1 permit expired
7905 | NoData
7906 | FIRE ALARM SYSTEM MUST BE SERVICE AND OPERATING IN AN ACCEPTABLE CONDITION.
7907 | Met with Mrs. Maria Alam 02/22/21 on location for a complain on this location. While performing an Site Inspection with Mrs. Alam she informed me that she do have a plumbing Company on this location repairing their busted pipes due to the Winter Storm. While on location I called Mrs. Rosenna Alaniz @ 832-553-2159 the Originator of this complaint to get a clear understanding of this complaint, Mrs. Rosenna Informed me that this yellow/red tags is due to busted pipes from the Winter Storm once the ice melted the water entered the Alarm Panel shorting out the Panel and that Panel now need to be replaced. Mrs. Rosenna Informed me that her Company have present communicated with Mrs. Alam for bids to correct the Yellow/Red Tag by replacing the Alarm Panel.
7908 | Portable Fire Extinguisher(s) annual maintenance Dt: 10/20
7909 | Annual Fire alarm test Dt: 10/29/20
7910 | Annual Sprinkler system (wet) test Dt: 10/29/20
7911 | 5-year hydro/flow test Dt: 10/23/19
7912 | NoData
7913 | Emergency lighting must be tested and any deficiencies corrected
7914 | 3-way plugs, multiple outlet adapters and multi-outlet cords are not allowed unless they are "resettable" type (overcurrent protected)
7915 | Extension cords not allowed as a replacement for permanent wiring
7916 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs
7917 | 36" Working clearance must be maintained in front of electrical panels
7918 | Obtain and post Certificate of Occupancy [104.1(9)]. Current yellow application receipt also acceptable
7919 | NoData
7920 | NoData
7921 | Met with Mr. Pidel Lazona the new Property Manager and he Informed me that he have American Fire Protecting System on the site at the present time performing repairs on the Alarm System. I schedule a (G.I.) on this location for 02/18/2021 @ 10:00 am.
7922 | INSTALL AN ILLUMINATED EXIT SIGN OVER THE EXIT DOOR
7923 | PROVIDE AND POST THE M3(FUEL DISPENSING) PERMIT, 1002 WASHINGTON AVE. 832-394-8811
7924 | LABEL THE ROOM DOOR WITH THE BREAKER BOX PANEL IN IT "ELECTRICAL PANEL INSIDE"
7925 | REPLACE ADDRESS NUMBERS WITH NUMBERS THAT ARE AT LEAST 4 INCHES IN HEIGHT AND CONTRASTING COLORS TO THE BUILDING
7926 | INSTALL LIGHT PROTECTION FOR THE FLUORESCENT LIGHT BALLAST IN THE STORAGE ROOM
7927 | NoData
7928 | NoData
7929 | NoData
7930 | NoData
7931 | provide metal lid covers for five(5) gallon cans of waste oil that are been use before pouring into the main storage tank outside of shop area to keep from been expose and spilling into the ground floor and creating a hazard.
7932 | remove all combustibles away from main electrical box such as plastics ,paper ,wood products at lease (3) feet away
7933 | renew application for a cutting and welding permit from the downtown permit office located at 1002 Washington fire marshal's permit section.
7934 | NoData
7935 | NoData
7936 | NoData
7937 | provide and install a plain exit sign on exit door
7938 | provide and install sign on exit door from the inside of the door close to the middle section
7939 | provide and install can with a metal lid and the wording oily rags
7940 | provide and install metal dike where waste oil storage tank is located in case of leaks to contain the waste oil from going into the ground area and contamination .
7941 | apply for a flammable and combustible liquids storage and use permit tier two (2) permit for waste oil storage over (60) gallons from the permit office at 1002 Washington fire marshal's permit section
7942 | NoData
7943 | provide and install metal can for oily rages
7944 | provide and obtain a falcon lock so as to secure the lid on the 911 emergency red box to keep your gate key locked inside of the red box to be open by the marshal when purchase and placed.
7945 | all breakers in the main electrical box shall be properly mark in case of an emergency
7946 | provide a plain exit sign on exit door leading directly to the outside of the garage
7947 | apply for a cutting and welding permit or remove from premise
7948 | provide and install the 911 emergency red box welded with an extra key from your gate lock in case of an emergency or fire.
7949 | provide a dike container for waste oil tanlk incase of leakage
7950 | apply for a flammable and combustible liquids storage and use permit type tier (2) for a waste oil storage tank over (60) gallons. or over (5) gallons of gasoline and remove any plastic containers for storing flammable liguids and provide approved metal can .
7951 | provide and install sign on exit door close to the middle inside of door area.
7952 | NEED TO APPLY FOR P2 PERMIT ASSEMBLY NEED TO APPLY FOR 911 K1 KEY BOX PERMIT NEED TO POST CERTIFICATE OF OCCUPANCY OR KEEP A RECORD ONSITE
7953 | ALL FIRE EXTINGUISHERS ARE TAGGED AND WITHIN DATE AT TIME OF INSPECTION
7954 | ALARM SYSTEM NEEDS TO BE TESTED AND APPROVED BY ALARM COMPANY
7955 | ALL EXITS ARE CLEARED AND UNOBSTRUCTED AT TIME OF INSPECTION
7956 | NoData
7957 | NoData
7958 | NoData
7959 | NoData
7960 | NoData
7961 | NoData
7962 | NEED TO APPLY FOR CERTIFICATE OF OCCUPANCY ALSO APPLY FOR PUBLIC ASSEMBLY PERMIT
7963 | DOOR TO ELECTRICAL ROOM SHALL BE LABELED
7964 | NoData
7965 | NoData
7966 | EXTINGUISHERS SHALL BE NO LESS THAN 4ft FROM FLOOR AND NO HIGHER THAN 5ft
7967 | NoData
7968 | NoData
7969 | NoData
7970 | FOR YOUR INFORMATION
7971 | NoData
7972 | FIRE EXTINGUISHERS NEED TO BE INSPECTED AND TAGGED
7973 | NoData
7974 | NoData
7975 | NoData
7976 | NoData
7977 | NoData
7978 | Amount Due: $830.05
7979 | NoData
7980 | NoData
7981 | NoData
7982 | NoData
7983 | Mount extinguisher on wall.
7984 | Remove extension cords used as permanent source of power.
7985 | Replace missing spacers.
7986 | See above- per our discussion (through email/ phone) the following MAQ see table for quantities allowed- you have 14 days to get under the amount allowed
7987 | Provide inventory for current material.
7988 | See above.
7989 | See above- per our discussion through email (provided Fire Engineer contact information)
7990 | A "fail safe" is required on the access gate.
7991 | Obtain a key box permit from the Houston Permitting Center.
7992 | NoData
7993 | Obtain and post the Certificate of Occupancy.
7994 | A 911 key box is required on the access gate.
7995 | Have sprinkler/pump repaired as soon as possible. Continue self-imposed fire watch and follow up within 7 days for progress of system repairs.
7996 | NoData
7997 | Ensure the proper clearance is maintained by the electrical charging stations as required by code.
7998 | For Reference
7999 | The Hazardous Materials Management Plan included with this report must be filled out and stored in the Fire Department depository box in a weather proof packet.
8000 | The last drop test completed on the rolling fire door was 4/28/2017. Have the annual drop test performed and tagged. Maintain annual tests
8001 | Clearance in aisles must be maintained when not restocking. Ensure adequate aisle space is maintained.
8002 | Complete the HMIS included with this report to account for all Hazardous Materials on site.
8003 | An alarm company technician shall be on-site during alarm test to ensure the monitoring station is receiving a HAZMAT signal and the Houston Fire Department is the responding agency.
8004 | NoData
8005 | REMOVE STORAGE BLOCKING ACCESS, KEEP SECURITY GATE OPEN DURING BUSINESS HOURS (SECURE OPEN WITH A CHAIN OR SIMILAR), AND ALLOW IMMEDIATE ACCESS TO DOOR AS ITS A MARKED EMERGENCY EXIT - USE PANIC HARDWARE OR SIMILAR TO COMPLY WITH FIRE CODE.
8006 | REMOVE STORAGE BLOCKING ACCESS, KEEP SECURITY GATE OPEN DURING BUSINESS HOURS (SECURE OPEN WITH A CHAIN OR SIMILAR), AND ALLOW IMMEDIATE ACCESS TO DOOR AS ITS A MARKED EMERGENCY EXIT - USE PANIC HARDWARE OR SIMILAR TO COMPLY WITH FIRE CODE.
8007 | NoData
8008 | NoData
8009 | NoData
8010 | NoData
8011 | replace missing circuit cover.
8012 | as per code
8013 | check all fire extinguisher,replace missing fire extinguisher in building 1 unit 1
8014 | no gas no test needed.
8015 | Carol Barefield 832 969 8953, Robert Woodard 832 883 7741 Properties with 3 or more units are required to register with the City of Houston as required by Ordinance No. 2006-1124 (Apartment Security Ordinance).Please contact the City of Houston “Multi-Family Rental Property Registration” at 832-394-8841 or log on to http://www.houstonmultifamily.org/
8016 | replace bad batteries in building 2 unit c.replace missing smoke alarm in building 1 unit 1
8017 | NoData
8018 | NoData
8019 | NoData
8020 | NoData
8021 | Have a licensed fire protection company perform an annual fire alarm inspection and correct any deficiencies.
8022 | Have a licensed fire protection company perform an annual fire sprinkler inspection and correct any deficiencies.
8023 | Have a licensed fire protection company perform a 5 year FDC inspection and correct any deficiencies.
8024 | The fire sprinkler system requires monitoring.
8025 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
8026 | NoData
8027 | NoData
8028 | NoData
8029 | NoData
8030 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
8031 | Need annual inspection of fire alarm. Last inspection was performed on 2/10/2015. All alarm panels must be tagged.
8032 | Need annual inspection of sprinkler system. Last inspection performed on 2/10/2015.
8033 | NoData
8034 | NoData
8035 | EXTENSION CORDS SHALL NOT BE USED FOR APERMANET SOURCE OF POWER IN FACILITY. AND SURGE PROTECTOR SHALL NOT BE USED IN CONJUCTION WITH ANOTHER ONE AS A SOURCE OF POWER.COMPLIANCEWITHIN 30 DAYS
8036 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL PERFORM A TEST OF ALL THE FIRE ALARM SYSTEM ANNUNCIATION DEVICES NOT LESS THAN EVERY 3 YEARS.COMPLIANCE WITHIN 30 DAYS
8037 | ROMOVE ALLCOMBUSTIBLE MATERIALS FROM ELECTRICAL ROOM AND OR RISER ROOMCOMPLIANCE WITHIN 30 DAYS
8038 | FOLLOW CODE REFERRED TO ABOVE CONCERNING LOCKS OR LOCKING. ANY AND ALL DROP BARS ATTACHED TO EXIT DOORS SHALL BE REMOVED.COMPLIANCE WITHIN 30 DAYS
8039 | NoData
8040 | NoData
8041 | Please have a flow test done on all 5 private fire hydrants found on property.
8042 | please make sure all trash/debris is placed inside dumpster for removal.
8043 | fail safe" boxes are in need of repair. No pull cord is attached to chain for manual operation
8044 | Please identify all electrical cutoff with proper unit number.
8045 | visually inspect all draft stops for solid construction. Please repair any damaged draft stops.
8046 | 18" x 18" HFD 4 Sign is required at main gate.
8047 | Please place a blue reflector on driveway marking fire hydrant location.
8048 | working smoke alarms/notification devices located inside all sleeping units.
8049 | gas test was done on 3/2020 for all buildings.
8050 | NoData
8051 | NoData
8052 | Correct the restricted (top level) re-entry call box, on level 11, so the re-entry door can be unlocked from a remote location per code.
8053 | Add keys to gate and FCC (security office) to the 911 box. Update the swipe card for gate and FCC per code.
8054 | Update mobility impaired list every 6 months.
8055 | Update key sets per code.
8056 | Return the following areas to their designed fire resistance rating per code. FCC above door. Stairwells around sprinkler pipe.
8057 | Correct the following doors so they close and latch from the open position per code. SE door on level 2. Door to fire pump room.
8058 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriateinspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualEmergency radio coverage- AnnualFire Extinguishers- AnnualDry pipe partial- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualDry pipe full- 3 YearFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearClean agent – Semi-annualKitchen Hood System- Semi-annualBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
8059 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. • Present Permits that apply to facility Address listed • on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS.
8060 | Replace missing outlet face plate.
8061 | Renew fire alarm permit.
8062 | Please renew your expired access gate permit (a4)Permit expired on 01/29/2021. If you have any questions or need an invoice, please contact the HPC office at 832-394-8811.
8063 | NoData
8064 | NoData
8065 | NoData
8066 | Please renew your expired access gate permit (a4) thatexpired on 01/29/2021. If you have any questions or need an invoice, please contact the HPC office at 832-394-8811.
8067 | ALL YELLOW AND RED TAG ISSUES MUST BE CORRECTED
8068 | NoData
8069 | NoData
8070 | NoData
8071 | NoData
8072 | NoData
8073 | NoData
8074 | NoData
8075 | NoData
8076 | NoData
8077 | NoData
8078 | NoData
8079 | NoData
8080 | NoData
8081 | NoData
8082 | Extension cords are only to be used as temporary day of use for portable appliances. Except for special multiplug extension cords, it is one appliance per extension cord.
8083 | This is for informational purposes, no violation noted.
8084 | The inspection tag was missing from an extinguisher located on a forklift. Have any and all missing inspection tags replaced by the company who performs your extinguisher inspections.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8085 | The owner/occupant shall be heldresponsible for the correction and abatement of all violations listed in thisnotice of violations report. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8086 | Provide documentation for annual hydrant test.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8087 | Greater care must be taken to prevent the accumulation of dust created by the woodworking activities at your facility with periodic inspection and cleaning of the areas in an also around the woodworking areas. You may consider a code compliant dust collection system with explosion protection to help with the control of dust.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8088 | For Informational purposes.
8089 | For informational purposes.
8090 | A key boxshall be properly placed on apparatus access gates as per HFD LSB #4 (accesscontrol gates). The key box shall be ofan approved type and shall contain keys, card, or gate code for immediateaccess for lifesaving or firefighting purposes.Fail-safesystem shall be properly placed on apparatus access gates as per HFD LSB #4(access control gates).COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8091 | All HFD fire department access doors and their components and/or hardware must be maintained in operable condition at all times. Test the function of all of these doors, including the ability to gain entry with the appropriate key using minimal effort. Make corrections as necessary.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8092 | All electrical junctions must be covered with the appropriate cover. Replace any missing junction box, switch, or plug covers.COMLIANCE: WITHIN 30 CALENDAR DAYS.
8093 | The requiredfire-resistance rating of fire-resistance-rated construction shall bemaintained. Such elements shall beproperly repaired, restored or replaced when damaged, altered, breached orpenetrated.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
8094 | Correctly fill out the HMIS using the attachedform and following the provided instructions for all hazardous materials storedat your facility. The classification ofthe hazardous materials shall comply with the 2012 international fire codeclassifications system.It is highly advisable to seek technicalassistance in correctly completing the HMIS for the hazardous material beingstored at the facility.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
8095 | The pavement markings which identify the fire apparatus access lane are required to be maintained. Replace any and all missing pavement markings designating the fire lane.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8096 | The properly marked fire lane must remain clear of obstructions.IMMEDIATE COMPLIANCE REQUIRED.
8097 | A workingspace (cleared of all combustible material) of not less than 30 inches inwidth, 36 inches in depth and 78 inches in height shall be provided in front ofelectrical service equipment.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
8098 | Repair ASAP.
8099 | Repair ASAP.
8100 | NoData
8101 | NoData
8102 | NoData
8103 | NoData
8104 | NoData
8105 | NoData
8106 | Have all Fire Extinguishers serviced, and provided with a current service tag .. Annually.
8107 | Ensure that all Fire Extinguishers are properly mounted on hangers or brackets throughout the Business.
8108 | Have Kitchen Fire Suppression/Ansul System serviced, and provided with a current service tag .. every 6 months.
8109 | Discontinue the uses of Extension cords as permanent wiring throughout the building.
8110 | Apply for Public Assembly & Open Flames / Candles Permit for correct location … 2301 Main St. Ste. # 200
8111 | Provide current Public Assembly & Open Flames / Candles permits for the correct location … 2301 Main St. Ste. # 200
8112 | Provide sign, "Maximum Occupant Load 160" in a visible location, near main entrance.
8113 | NoData
8114 | NoData
8115 | NoData
8116 | NoData
8117 | NoData
8118 | NoData
8119 | NoData
8120 | Renew p2 (Assembly) permit at 1002 Washington, 832.394.8811. Failure to renew permit will render a re-inspection fee.
8121 | NoData
8122 | NoData
8123 | NoData
8124 | NoData
8125 | NoData
8126 | NoData
8127 | NoData
8128 | NoData
8129 | NoData
8130 | NoData
8131 | NoData
8132 | NoData
8133 | NoData
8134 | NoData
8135 | NoData
8136 | Test results must be placed inside FMB
8137 | NEED LAST TEST OF DAMPERS FOR HVAC.
8138 | Red tagged corrected in kitchen
8139 | FMB, MUST HAVE THE LAST TWO YEARS OF FIRE DRILLS. PROPER DOCUMENTATION PROVIDED.
8140 | Proper documentation provided and entered into FMB
8141 | NoData
8142 | Last test tag must be put into the FMB
8143 | At no time should these gate be pad locked or unapproved hardware.
8144 | Panic hardware must be installed on locations stated about.
8145 | Certificate of Occupancy for the core building must be included in the FMB.
8146 | ALL PERMITS MUST BE IN FMB AND EACH SECTION OF THE BINDER MUST BE TABBED SEPARATELY. Missing permits, safety survey and certificate of occupancy for core building.
8147 | Egress to public way must not be obstructed. Panic hardware must be installed.
8148 | NoData
8149 | NoData
8150 | NoData
8151 | Annual permit for Minute Maid Park's C-9.
8152 | NoData
8153 | NoData
8154 | P-2 permit is expired. Renew permit per code.
8155 | NoData
8156 | 5/14/2020 - Yellow and RedCorrected 10/1/2020 - OK
8157 | 5/14/2020 - OK
8158 | FDC for hose cabinets only.2/21/2020 - Blue, OK
8159 | 6/24/2019 - OK
8160 | Obstructed drills OK
8161 | Drill log OK
8162 | 4/4/2019 - OK
8163 | 3/2019 - Have all fire extinguishers inspected.
8164 | Add two extinguishers to gym
8165 | Correct all violations within 60 calendar days.
8166 | 1/31/2020 - Have all hose cabinets inspected.
8167 | Conduct and document required annual fire safety training.
8168 | Remove carts that block main fire alarm panel. Prohibit future storage in front of panel.
8169 | Replace missing ceiling tile above stage and in laundry room.
8170 | Two boiler permits expired. Update expired permits.
8171 | Elevator permit expired 3/31/2020.Update expired elevator permit.
8172 | Place permanent "Roof Access" sign on door to electrical room that contains roof access ladder (near sliding glass door).
8173 | Last documented 1/27/2018 - Multiple deficiencies reported with no documentation of correction. No updated egress lighting test with passing results.Citation for failure to correct deficiencies on 1/27/18 issued on 2/25/2020. Inspector will issue additional citations for failure to correct ongoing deficiencies.
8174 | Remove paint from doors to rooms 227 and 114.
8175 | NoData
8176 | NoData
8177 | NoData
8178 | NoData
8179 | NoData
8180 | NoData
8181 | NoData
8182 | NoData
8183 | NoData
8184 | NoData
8185 | NoData
8186 | NoData
8187 | NoData
8188 | NoData
8189 | NoData
8190 | NoData
8191 | NoData
8192 | NoData
8193 | NoData
8194 | NoData
8195 | NoData
8196 | NoData
8197 | NoData
8198 | NoData
8199 | NoData
8200 | NoData
8201 | NoData
8202 | NoData
8203 | NoData
8204 | NoData
8205 | NoData
8206 | NoData
8207 | NoData
8208 | NoData
8209 | 2/1/2021 - REDCorrected 2/2/2021 - OK
8210 | 12/15/2018 - Multiple FailsCorrected 2/15/2020 - OK
8211 | 9/5/2017 - Blue, OK
8212 | 12/2020 - OK
8213 | 6/5/2019 - OK
8214 | Monthly drills conducted and logged - OK
8215 | 2/1/2021 - OK
8216 | 1/2020 - Have all portable fire extinguishers inspected.
8217 | Correct all violations within 60 calendar days.
8218 | 2/4/2020 - BlueHave sprinkler system inspected and correct any deficiencies
8219 | Conduct and document required annual fire safety training.
8220 | Conduct more obstructed fire drills.
8221 | Update expired elevator permit (exp. 9/30/2019)
8222 | Mount permanent signs on gate leading to cafeteria enclosure and on door to sprinkler riser room. Signs must be permanent and read, "Riser Room" or "Fire Sprinkler Room"
8223 | Have current egress lighting test performed and have any deficiencies corrected.Last egress lighting test 8/28/2019 - multiple failures corrected 3/13/2020.
8224 | THERE SHALL BE NO COMBUSTIBLE MATERIAL STORAGEDWITHIN 3 FT IN ALL DIRCETIONS OF BATTERY CHARGERS STATION.COMPLIANCEWITHIN 30 DAYS
8225 | THE OWNER / OCCUPANT SHALL BE HELD RESPONSIBLE FOR THE CORRECTIONAND ABATEMENT OF ALL VIOLATIONS LISTED IN THIS NOTICE OF VIOLATIONS REPORT.COMPLIANCE WITHIN THE TIME DATED ON EACH VIOLATION.
8226 | THE EXIT PATHWAYS AND EXIT STAIRWAYS LEADING AWAY FROM THEWAREHOUSE AND STORE FRONTSHALL HAVE A CLEAR AND UNBLOCKED PATH TO AN AREAOF SAFE REFUGE AT ALL TIMES. COMBUSTIBLE COMMODITIES SHALL NOTBE STOREDUNDER STAIRS WHICH ARE USED EGRESS AT ANYTIME.COMPLIANCE WITHIN 7 DAYS
8227 | THE 911 KEY BOX, OR KNOX BOX 3200 SERIESHINGED LID, SHALL BE OF AN APPROVED TYPE LISTED IN ACCORDANCE WITH UL 1037 ANDSHALL CONTAIN KEYS FOR IMMEDIATE ACCESS FOR LIFE-SAVING OR FIRE-FIGHTINGPURPOSES.(SEE ATTACHED LIST FOR APPROVED LICENSEDCOMPANIES.)911 KEY BOX, OR KNOX BOX, SHALL BE LOCATED WITHIN 48 TO 60 INCHESABOVE THE GROUND LEVEL.COMPLIANCEWITHIN 30 DAYS
8228 | OPEN JUNCTION BOXES SHALL BE COVERED TO PREVENT EXPOSED WIRINGTHROUGHOUT FACILITY.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8229 | THE REQUIRED FIRE-RESISTANCE RATING OFFIRE-RESISTANCE-RATED CONSTRUCTION SHALL BE MAINTAINED. SUCH ELEMENTS SHALL BE PROPERLY REPAIRED,RESTORED OR REPLACED WHEN DAMAGED, ALTERED, BREACHED OR PENETRATED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8230 | FIREDETECTION, ALARM AND EXTINGUISHING SYSTEMS SHALL BE MAINTAINED IN AN OPERATIVECONDITION AT ALL TIMES, AND SHALL BE REPLACED OR REPAIRED WHERE DEFECTIVE. THEFIRE PROTECTION SPRINKLER SYSTEM SHALL BE TESTED ANNUALLY BY A LICENSED COMPANYAND ALL TROUBLE (YELLOW) TAG(S) SHALL BE REMOVED AND ACCEPTABLE (WHITE) SERVICETAG(S) SHALL BE AFFIXED TO ENSURE SYSTEM IS MAINTAINED IN OPERATIVE CONDITION.COMPLIANCE WITHIN 30 CALENDAR DAYS
8231 | HAVE THE APPROPRIATE FIRE EXTINGUISHER MOUNTED WITHIN THE APPROPRIATE DISTANCEFROM THE CHARGING STATION.COMPLIANCE WITHIN 30 DAYS
8232 | APPROVED PLANS ARE TO BE KEPT ON SITE AT ALL TIMES. IF APPROVED PLANS CANNOT BE LOCATED, A REQUESTTO THE BUILDING DEPARTMENT MAY BE ABLE TO DUPLICATE THE ORIGINAL. APPROVED PLANS MUST BE SUBMITTED TO FIREMARSHAL OR THE PROCESS FOR HIGH-PILED STORAGE PLAN SUBMITTAL PROCESS SHALL BERESTARTED.ALL ACCESSDOORS SHALL BE IDENTIFIED WITH THE LETTERING "HFD" WHICH MEETS THEABOVE CODE REQIREMENTS.BEING MARKEDON THE UPPER LEFT HAND CONER OF EACH DOOR WITH LETTERING SHALL NOT BE LESS THANFOUR INCHES IN HEIGHT ON A CONTRASTING BACKGROUND. LETTERING SHALL BE LEGIBLE, DURABLE, AND REFLECTION IN NATURE. THESE DOORS WILL BE NOTED ON YOUR CONSTRUCTION DOCUMENTS.COMPLIANCEWITHIN 30 DAYS.
8233 | FOLLOW CODE REFERRED TO ABOVE CONCERNING LOCKS OR LOCKING. ANY AND ALL DROP BARS ATTACHED TO EXIT DOORS SHALL BE REMOVED THAT PREVENTS EMERGENCY DOORS FROM OPENING WITH ONE ACTION OPENING. REPAIR AND OR REPLACE THEEXIT ACCESS DOOR THAT WAS RUSTED OUT AND FALLING APART.ALL ACCESS AND EXIT DOORS SHALL BE KEYEDALIKE. ENSURE ALL FIREFIGHTER ACCESS DOORS HAVE APPROVED HARDWARE THAT ISREADILY OPERABLE FROM THE EGRESS SIDE. (PANIC HARDWARE OR LEVER ACTION WHICHOPEN WITH ONE MOVEMENT AND REQUIRE NO SPECIAL TOOLS OR KNOWLEDGE) COMPLIANCE WITHIN 30 DAYS
8234 | ENSURE THAT ALL DUMPSTERS ARE MAINTAINED 10FEET MINIMUM FROM THEBUILDING AT ALL TIMES.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8235 | EXIT SIGNS SHALL BE ILLUMINATED AT ALL TIMES. TO ENSURE CONTINUED ILLUMINATION FOR ADURATION OF NOT LESS THAN 90 MINUTES IN CASE OF PRIMARY POWER LOSS, THE SIGNILLUMINATION MEANS SHALL BE CONNECTED TO AN EMERGENCY POWER SYSTEM PROVIDEDFROM STORAGE BATTERIES, UNIT EQUIPMENT OR AN ON-SITE GENERATOR. COMPLIANCE: WITHIN 30CALENDAR DAYS.
8236 | THEEXIT PATHWAYS AND EXIT STAIRWAYS LEADING AWAY FROM THE WAREHOUSE AND STOREFRONTSHALL HAVE A CLEAR AND UNBLOCKED PATH TO AN AREA OF SAFE REFUGE ATALL TIMES. COMPLIANCEWITHIN 7 DAYS
8237 | APPLY FOR AND OBTAIN A HFD KEY BOX PERMIT (K1) FROM THE CITY OFHOUSTON PERMIT CENTER LOCATED AT 1002 WASHINGTON AVE. (832)394-9000.COMPLIANCE: WITHIN30 CALENDAR DAYS.
8238 | NFPA 13: 12.12.1.1 - WOOD PALLETS SHALL BE PERMITTED TO BE STOREDIN THEFOLLOWINGARRANGEMENTS:(1) STOREDOUTSIDE.(2) STOREDIN A DETACHED STRUCTURE.(3) STOREDINDOORS WHERE ARRANGED IN ACCORDANCE WITH 12.12.1.2. NFPA 13:12.12.1.2 – WOOD PALLETS, WHERE STORED INDOORS, SHALL MEET THEFOLLOWING:(1) PALLETSSHALL BE STORED NO HIGHER THAN 6 FEET.(2) EACH PALLETPILE OF NO MORE THAN 4 STACKS SHALL BE SEPARATED FROM OTHER PALLET PILES BY ATLEAST 8 FEET OF CLEAR SPACE OR 25 FEET OF COMMODITY.COPLIANCEWITHIN 7 DAYS
8239 | HAVE ACERTIFIED RACKING COMPANY REPAIR AND OR REPLACE ANY AND ALL DAMAGED RACKS. COMPLIANCE WITHIN 30 CALENDAR DAYS.
8240 | APPLY FOR AND OBTAIN A HFD KEY BOX PERMIT (L1) FROM THE CITY OF HOUSTON PERMIT CENTER LOCATED AT 1002 WASHINGTON AVE. (832)394-9000.COMPLIANCE:WITHIN 30 CALENDAR DAYS.AT LEAST ONE APPROVED PORTABLE FIRE EXTINGUISHER, HAVING A MINIMUMCAPACITY OF 18 LB. DRY CHEMICAL WITH B:C RATING (AS PER NFPA 58 2011 EDITION SECTION8.5.1 AND 8.5.2) SHALL BE LOCATED NO MORE THAN 50 FEET FROM THE LP GAS STORAGE LOCATION.
8241 | NoData
8242 | NoData
8243 | NoData
8244 | Emergency lights must be in working order.
8245 | Remove extension cords used as permanent source of power.
8246 | Fire extinguishers need current inspection tags.
8247 | Ansul system must be repaired.
8248 | Please renew both Access gate & Key box permits
8249 | No combustible material shall be stored within 3 ft. in all directions of battery charging station.Compliance within 30 days.
8250 | EXIT SIGNS SHALL BE ILLUMINATED AT ALL TIMES. TO ENSURE CONTINUED ILLUMINATION FOR A DURATION OF NOT LESS THAN 90 MINUTES IN CASE OF PRIMARY POWER LOSS, THE SIGN ILLUMINATION MEANS SHALL BE CONNECTED TO AN EMERGENCY POWER SYSTEM PROVIDED FROM STORAGE BATTERIES, UNIT EQUIPMENT OR AN ON-SITE GENERATOR. Compliance within 30 days
8251 | Lumber being stored at the rear of the building must be secured with an approved fence.Compliance within 30 days.
8252 | THE REQUIRED FIRE-RESISTANCE RATING OF FIRE-RESISTANCE-RATED CONSTRUCTION SHALL BE MAINTAINED. SUCH ELEMENTS SHALL BE PROPERLY REPAIRED, RESTORED OR REPLACED WHEN DAMAGED, ALTERED, BREACHED OR PENETRATED.Compliance within 30 days.
8253 | AISLES WIDTHS STATED ON THE APPROVED PLANS ARE NOT BEING MAINTAINED AND SHALL BE BROUGHT INTO COMPLIANCE.Compliance within 30 days.
8254 | Fire extinguishers must be within 20 ft. of battery charging area.Compliance within 30 days.
8255 | PLANS WERE SUBMITTED AND APPROVED BY THE FIRE MARSHAL’S OFFICE FOR HIGH PILE STORAGE. WHEN THE REMODIFICATION FROM THE APRROVED PLANS TOOK PLACE NO PLANS WERE SUBMITTED OR APPROVED. WHEN THERE ARE ANY DEVIATIONS FROM THE ORIGINAL APPROVED PLANS, NEW PLANS HAVE TO BE SUBMITTED FOR APPROVAL. A COPY OF THE ORIGINAL APPROVED PLANS MUST BE SUBMITTED AS REFERENCE.Compliance within 30 days
8256 | ALL ACCESS DOORS SHALL BE IDENTIFIED WITH LETTERING “HFD”, WHICH MEETS THE ABOVE CODE REQUIREMENTS, BEING MARKED ON THE UPPER LEFT-HAND CORNER OF EACH DOOR.Compliance within 30 days.
8257 | Remove all obstructions from exits that will prevent egress continuity.Compliance within 30 days.
8258 | 6/3/2020 - Blue, OK
8259 | 12/29/2018 - OK
8260 | 10/2020 - OK, but due next month.
8261 | 6/18/2019 - OK
8262 | Monthly drills conducted and logged - OK
8263 | 11/2018 - Have all portable fire extinguishers inspected.
8264 | Correct all violations within 60 calendar days.
8265 | Conduct and document more obstructed fire drills.
8266 | Remove plastic drapes from library and prohibit their use elsewhere in school.
8267 | Have detector sensitivity test performed and provide documentation that deficiencies were corrected.ORProvide documentation of an acceptable sensitivity test within the last five years.
8268 | Update expired elevator permit (exp 3/31/2020).
8269 | Replace current (damaged) alarm room sign with permanent sign.Place permanent "Roof Access" sign on door to Room 202.
8270 | Have egress lighting performed and provide documentation that deficiencies were corrected.
8271 | Install panic hardware on double gates near T-buildings.
8272 | Immediately remove all chains and padlocks from perimeter fence gates.Some chains are welded in place and will need to be cut from fence posts.
8273 | NoData
8274 | Repair ASAP.
8275 | NoData
8276 | NoData
8277 | NoData
8278 | NoData
8279 | NoData
8280 | NoData
8281 | NoData
8282 | NoData
8283 | Event manager submitted a site plan of the event and the plan has been approved.
8284 | Information only.
8285 | Replace failsafe feature on automatic gates.
8286 | Information only.
8287 | FYI: This is a condo community.
8288 | NoData
8289 | Repair ASAP.
8290 | Repair ASAP.
8291 | NoData
8292 | NoData
8293 | NoData
8294 | NoData
8295 | NoData
8296 | NoData
8297 | NoData
8298 | NoData
8299 | NoData
8300 | NoData
8301 | NoData
8302 | NoData
8303 | NoData
8304 | NoData
8305 | NoData
8306 | NoData
8307 | NoData
8308 | NoData
8309 | NoData
8310 | NoData
8311 | NoData
8312 | NoData
8313 | NoData
8314 | NoData
8315 | NoData
8316 | NoData
8317 | NoData
8318 | NoData
8319 | NoData
8320 | MAKE SURE BOTH THE LEFT AND RIGHT SIDE EXIT DOORS REMAIN UNLOCKED DURING BUSINESS HOURS
8321 | REMOVE THE NEWSPAPER RACKE FROM IN FRONT OF THE EXIT DOOR
8322 | LABEL THE DOOR WITH THE ELECTRICAL PANELS IN IT "ELECTRICAL PANELS INSIDE"
8323 | REPLACE ALL MISSING OR DAMAGED CEILING TILES IN THE STORE
8324 | RENEW THE EXPIRED M3(FUEL DISPENSER) PERMIT AT 1002 WASHINGTON AVE. 832-394-8811 APPLY FOR AND POST THE L1(LPG STORAGE) PERMIT AT 1002 WASHINGTON AVE. 832-394-8811
8325 | INSTALL EMERGENCY EGRESS LIGHTS IN CASE OF POWER OUTAGE OR POWER FAILURE
8326 | NoData
8327 | NoData
8328 | NoData
8329 | NoData
8330 | NoData
8331 | NoData
8332 | NoData
8333 | NoData
8334 | NoData
8335 | NoData
8336 | NoData
8337 | NoData
8338 | NoData
8339 | NoData
8340 | HAVE ALL PORTABLE FIRE EXTINGUISHERS INSPECTED AND HAVE A CURRENT INPECTION TAGE PUT ON THEM
8341 | HAVE A PORTABLE FIRE EXTINGUISHERS INSTALLED NEXT TO THE ENTRANCE/EXIT DOOR FOR THE FUEL PUMPS
8342 | MAKE SURE TO KEEP BOTH THE LEFT AND RIGHT SIDE DOORS UNLOCKED DURING BUSINESS HOURS
8343 | LABEL THE ROOM DOOR WITH THE ELECTRICAL PANELS IN IT (ELECTRICAL PANELS INSIDE)
8344 | INSTALL AND EXIT SIGN ABOVE THE ENTRANCE/EXIT DOORS
8345 | APPLY FOR THE L1(PROPANE STORAGE) PERMIT AT 1002 WASHINGTON AVE. 832-394-8811
8346 | INSTALL AND EMERGENCY LIGHT IN THE BUSINESS IN CASE OF POWER OUTAGE OR POWER FAILURE
8347 | PUT A SIGN ON THE FRONT DOOR THAT READS "THESE DOORS MUST REMAIN UNLOCKED DURING BUSINESS HOURS"
8348 | NoData
8349 | NoData
8350 | NoData
8351 | NoData
8352 | NoData
8353 | NoData
8354 | NoData
8355 | NoData
8356 | NoData
8357 | NoData
8358 | NoData
8359 | NoData
8360 | NoData
8361 | HAVE ALL PORTABLE FIRE EXTINGUISHERS SERVICED AND TAGGED
8362 | REMOVE GAMING MACHINES FROM IN FRONT OF SECONDARY EXIT DOOR AND KEEP SECONDARY EXIT DOOR UNLOCKED DURING BUSINESS HOURS REMOVE TABLE FROM IN FRONT OF MAIN ENTRANCE/EXIT DOOR AND KEEP BOTH THE LEFT AND RIGHT SIDE EXIT DOOR UNLOCKED DURING BUSINESS HOURS
8363 | REMOVE GAMING MACHINES FROM IN FRONT OF SECONDARY EXIT DOOR AND KEEP SECONDARY EXIT DOOR UNLOCKED DURING BUSINESS HOURS REMOVE TABLE FROM IN FRONT OF MAIN ENTRANCE/EXIT DOOR AND KEEP BOTH THE LEFT AND RIGHT SIDE EXIT DOOR UNLOCKED DURING BUSINESS HOURS
8364 | MAKE SURE THE KITCHEN SUPRRESSION SYSTEM IS SERVICED AND INSPECTED EVERY 6 MONTHS
8365 | LABEL THE STORAGE ROOM WITH THE ELECTRICAL PANEL IN IT "ELECTRICAL PANELS INSIDE"
8366 | MAKE SURE BOTH THE LEFT AND RIGHT SIDE ENTRANCE/EXIT DOORS REMAIN UNLOCKED DURING BUSINESS HOURS
8367 | LABEL THE ROOM DOOR WITH THE ELECTRICAL BREAKER BOX PANEL IN IT "ELECTRICAL PANEL INSIDE"
8368 | fire extinguishers on site but no properly placed due to code not inspected or tagged
8369 | POSTED OCCUPANCY NOT TO EXCEED 49 TILL A VALID CERTIFICATE OF OCCUPANCY IS OBTAINED AND POSTED AN ASSEMBLY PERMIT NEEDS TO BE OBTAINED ALSO NO HOOKHA ALLOWED INSIDE PREMISES ALL HOOKHA NEEDS TO BE REMOVED FROM INSIDE BUSINESS
8370 | no C of O on premises no Assembly permit . capacity from previous established noted from ILMS as 299 on follow up still no C of O or Assembly Permit business was allow to open as previous visit.
8371 | NoData
8372 | NoData
8373 | NoData
8374 | NoData
8375 | NoData
8376 | NoData
8377 | NoData
8378 | NoData
8379 | NoData
8380 | NoData
8381 | NoData
8382 | NoData
8383 | NoData
8384 | NoData
8385 | NoData
8386 | NoData
8387 | NoData
8388 | NoData
8389 | NoData
8390 | NoData
8391 | NoData
8392 | NoData
8393 | NoData
8394 | NoData
8395 | NoData
8396 | NoData
8397 | Move the guy wire next to the fire hydrant to maintain 3 feet of clearance around the hydrant.
8398 | NoData
8399 | NoData
8400 | NoData
8401 | The fire pump has been tagged by your service provider and is in need or repair. Per code, the system must remain in operational readiness condition. Have all repairs completed in the next 30 days.
8402 | A 5 year hydrostatic flow test must be performed as required by code. A report and service tag will be placed in the pump room and and all risers providing extinguishment to individual buildings (Bld C, Bld B5, Bld E)
8403 | An annual flow test of the fire pump must be performed and found to be compliant with standards. A report must be provided to our office.
8404 | A flow test and inspection of the water tank and piping system must be performed and the 5 year interior inspection completed in accordance with NFPA 25. Provide a report by the service company to our office indicating the system tests have passed. All deficiencies found during inspection and testing must be repaired or replaced to meet standards. .
8405 | For Reference
8406 | The required maintenance, service, and testing to the (red) private fire hydrants on site must be performed.The following report(s) must be provided to our office:- Site map indicating the location for all private hydrants (red)- Maintenance and Testing for each hydrant as specified in NFPA 25- 5 year flow test of the fire service main pipingEnsure that ALL fire hydrants are accessible and there are no obstructions (fence, ground, etc..) prohibiting their use
8407 | NoData
8408 | NoData
8409 | NoData
8410 | Replace or repair the red tagged fire extinguishers.
8411 | Remove the obstructions placed in front of the exit.
8412 | Have a licensed fire protection inspect and tag the extinguishing systems on the paint booths.
8413 | Secure the compressed gas cylinders.
8414 | Propane shall not be used in buildings.
8415 | Protected propane storage is required.
8416 | Remove propane storage from the building.
8417 | PAINT BOOTH SPRINKLER SYSTEM DUE FOR INSPECION.
8418 | HAVE ALL FIRE EXTINGUISHERS INSPECTED AND TAGGED.
8419 | REMOVE STORAGE THAT IS LOCATED BEHIND PAINT BOOTH
8420 | HAVE ALL EMERGENCY ILLUMINATION LIGHTS REPAIRED OR REPLACED.
8421 | NoData
8422 | NoData
8423 | NoData
8424 | YOU WILL NEED TO APPLY FOR A TIER 1 HIGH PILE PERMIT, BUT FIRST GET TECHNICAL ASSISTANCE TO DETERMINE REQUIREMENTS FOR YOUR FACILITY TO BECOME AN APPROVED HI-PILE STORAGE OCCUPANCY.
8425 | NO CERT OF OCC (MUST BE APPLIED FOR - SEE BELOW) FIRE EXTINGUISHERS CURRENT (7/18)
8426 | YOU WILL NEED TO APPLY FOR A HI-PILE CERTIFICATE OF OCCUPANCY, TIER 1 HI-PILE PERMIT, AND 911 KEYBOX PERMIT. ALL CAN BE OBTAINED FROM THE PERMIT OFFICE AT THE ADDRESS NOTED ABOVE.
8427 | TEST ALL EXIT SIGNS AND INCLUDED EMERGENCY LIGHTING FOR PROPERY OPERATION. REPLACE/REPAIR AS NEEDED.
8428 | AN ENGINEERING FIRM OR QUALIFIED FIRE PROTECTION COMPANY WILL NEED TO BE CONTRACTED TO ASSESS YOUR FACILITIY'S HI-PILE STORAGE ALLOWANCES - THIS IS BASED ON A NUMBER OF FACTORS (BLDG CEILING HEIGHT, COMMODITY TYPE STORED, AMOUNT OF WATER SPRINKLER SYSTEM CAN DELIVER, ECT.) BASED ON CURRENT FIRE CODE AND SPRINKLER STANDARDS.
8429 | KEYBOX REQUIRES UPDATED KEYS FOR RE-KEYED DOORS
8430 | See above, per our conversation, when spraying parts.
8431 | See above, maintain the safety of exits (free from obstructions)
8432 | See above, per our conversation you need to maintain the extinguishers on a annual basis ( the current extinguisher has no tag and we need a receipt to prove the date)
8433 | See above-provide the following for welding.
8434 | See above, per our conversation, apply for the F7( storage of flammable/combustible liquid) and the H3 permit (welding)
8435 | Fire extinguishers are due for annual inspection before the end of 12/2020.
8436 | Mount the fire extinguishers placed on the ground.
8437 | Replace missing ceiling tiles.
8438 | Clear and maintain 36 inches of clearance in front of the breaker panels.
8439 | Clear and maintain aisle clearance.
8440 | NoData
8441 | NoData
8442 | NoData
8443 | NoData
8444 | NoData
8445 | NoData
8446 | Remount the fire extinguisher in the kitchen to ensure the top of the fire extinguisher isn't higher than 5 feet from the ground.
8447 | Move the class k extinguisher located in the side exit hallway and remount in the kitchen area.
8448 | Remove obstructions in front of the exit located on the side of the business.
8449 | Have a licensed fire protection company inspect and tag the vent hood extinguishing system. Have the vent hoods cleaned and tagged with the date of professional cleaning.
8450 | Post address numbers on the front of the business.
8451 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
8452 | Repair the inoperable emergency illumination on the exit signs.
8453 | Post the occupant load.
8454 | ALL FIRE EXTINGUISHERS SHALL BE MOUNTED NO HIGHER THAN 5FT IF LESS THAN 40LBS.
8455 | NoData
8456 | ALL COMPRESSED GAS CYLINDERS SHALL BE SECURED TO PREVENT BEING KNOCKED OVER.
8457 | POST ALL PERMITS IN A LOCATION SO THAT THEY ARE READILY AVAILABLE FOR INSPECTION.
8458 | FIRE ALARM PERMIT EXPIRED 6-26-19. RENEW PERMIT
8459 | APPLY FOR CERTIFICATE OF OCCUPANCY FOR MAINTENANCE BUILDING.
8460 | Fire Sprinklers are out of service. Fire alarm is in alarm and supervisory mode. Continue with self-fire watch until the fire alarm and fire sprinkles are back in regular service.Complete and return the fire watch agreement prior to COB today.
8461 | Fire Alarm Red Tagged Impaired72 Hour Notice IssuedSelf Fire Watch initiated 2-22-21
8462 | NoData
8463 | Fire Alarm and Sprinkler System Annual Inspection is out of date.
8464 | Fire Alarm and Sprinkler System Annual Inspection is out of date.
8465 | Entrance Toggle Switch is not working.
8466 | Fire Alarm and Sprinkler Systems have been tagged Impaired. Make all corrections.
8467 | NoData
8468 | NoData
8469 | NoData
8470 | Fire Alarm 4/30/2020; Fire Sprinkler 4/30/2020; Fire Extinguisher 4/2020
8471 | Correct the Trouble Alarm on the Fire Alarm Control Panel
8472 | NoData
8473 | Have a licensed fire protection company perform an annual sprinkler inspection and correct any deficiencies.
8474 | Have the emergency lighting tested and replace any inoperable lighting.
8475 | Failure to comply with violations found on the Inspection Report
8476 | Varnett Charter School
8477 | FDC TEST REQUIRED EVERY 5 YEARS; IF TEST COMPLETEDPROVIDE DOCUMENTATION FROM FIRE SPRINKLER COMPANY
8478 | correct the yellow tagged fire sprinkler system
8479 | SIGN REQUIRED TO IDENTIFY THE FIRE DEPARTMENT CONNECTION
8480 | NoData
8481 | NEED TO FIX YELLOW TAG 10-5-20 LAST DATE
8482 | NEED TO BE SERVICE 3-2-17
8483 | NEED TO BE SERVICE 8-19 LAST DATE
8484 | ELEVATOR NO TO BE INSPECTED
8485 | NoData
8486 | NoData
8487 | Fire Alarm is Red Tagged ImpairedFire Sprinkler System is out of service.Maintain Self Fire-watch until systems are back in regular service.
8488 | Fire Alarm Red TagMaintain Self Fire Watch until fire protection systems are back in normal service.
8489 | See above- the current "K" extinguisher is in compliance (12-2020) maintain the extinguisher
8490 | See above- the current fire extinguishers are in compliance (maintain them) 12-2020
8491 | See above- all extinguishers need to be "marked" with signage
8492 | V.K.PBP Wings LLC.Manager on Duty- Heather
8493 | See above- maintain the emergency exit lighting (test it and repair if necessary)
8494 | See above- the current system is in compliance (12-2020) maintain the system
8495 | See above- Provide the physical address #'s on the building.
8496 | See above- per our conversation relocate the extinguisher in the front of the facility to a more visible location.
8497 | See above- per our conversation, obtain the F7 permit for (storage of flammable/combustible liquids)
8498 | See above- per our conversation, provide documentation of the certificate of occupancy.
8499 | Have a licensed fire protection company punch the holes in the dates of service for the fire extinguishers.
8500 | Mount the class K fire extinguisher in the kitchen.
8501 | NoData
8502 | No violations noted.
8503 | Fire Alarm Is Impaired Fire Sprinklers are out of serviceSelf Fire Watch established, Maintain self fire watch until all FP systems are in regular service.
8504 | NoData
8505 | Provide address numbers for the front of the business.
8506 | NoData
8507 | NoData
8508 | NoData
8509 | LINT TRAP MUST BE CLEAN DAILY
8510 | LOCK ON KEYBOX IS RUSTED AND INOPERABLE
8511 | Illuminated exit signs above interior door needs to be installed.
8512 | Service Tags need to be updated on fire panel.
8513 | Annual testing tag needs to be updated
8514 | Audibility testing needs to be posted at the fire panel.
8515 | Fire extinguisher in building needto be serviced along with the hose cabinets. Update expired tags.
8516 | Sensitivity tag needs to be posted on fire panel
8517 | NoData
8518 | NoData
8519 | NoData
8520 | NoData
8521 | NoData
8522 | NoData
8523 | NoData
8524 | NoData
8525 | NoData
8526 | Provide keys for the fire pump, mechanical rooms and elevator fire service keys in the key box.
8527 | NoData
8528 | NoData
8529 | NoData
8530 | NoData
8531 | NoData
8532 | NoData
8533 | NoData
8534 | NoData
8535 | Fire alarm test passed and signals received by monitoring company inspection is final.
8536 | If you read our LSB-1 Standard regarding Day Cares or any business, 2-A, 10B:C is the minimum rating for any portable fire extinguisher in any business. Please replace the existing 1-A, 10B:C in the kitchen with a 2-A, 10B:C or maneuver the other portable fire extinguishers in the building. Make sure that the existing fire extinguishers are not more than 75 feet apart from another fire extinguisher with an unobstructed path of travel.
8537 | Cert. of Occupancy # is 09103737Fire Alarm Permit Issued 11/9/2020, expires 11/11/2021.
8538 | NoData
8539 | NoData
8540 | NoData
8541 | NoData
8542 | NoData
8543 | NoData
8544 | NoData
8545 | MAKE REPAIRS TO CLEAR YELLOW TAG FROM ALARM
8546 | INSTALL MISSING CAPS AT FDC
8547 | NoData
8548 | ENSURE ALL STAIRWAY DOORS CLOSE AND LATCH UNDER OWN POWER
8549 | UPDATE KEY SETS IN ACCORDANCE WITH LSB 6
8550 | INCLUDE 2 HOISTWAY DOOR TOOLS
8551 | NoData
8552 | NoData
8553 | REPAIR ALL PENETRATIONS IN CEILINGS
8554 | REPAIR/RETURN GARAGE STANDPIPE TO SERVICE AS SOON AS POSSIBLE
8555 | INSTALL SIGN LABELING ROOF TEST CONECTION
8556 | NoData
8557 | NoData
8558 | INSTALL SIGN INDICATING LOCATION OF FCC
8559 | MAINTAIN CURRENT COPIES OF ALL FIRE PERMITS TOGETHER FOR INSPECTION
8560 | NoData
8561 | THE OWNER / OCCUPANT SHALL BE HELD RESPONSIBLE FOR THE CORRECTION AND ABATEMENT OF ALL VIOLATIONS LISTED IN THIS NOTICE OF VIOLATIONS REPORT. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8562 | FIRE EXTINGUISHERS EVERY 75 FEET IN THE BACK OF THE WAREHOUSE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8563 | BREAKER PANEL REQUIRED THREE FEET OF SPACE OF NO STORAGE OF CLEAREANCE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8564 | APPLY FOR AND OBTAIN A KEY BOX AND HIGH-PILED OPERATIONAL PERMIT FROM THE CITY OF HOUSTON PERMITTING CENTER LOCATED AT 1002 WASHINGTON AVE. (832-394-9000). COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8565 | AT THE TIME OF INSPECTION, APPROVED PLANS COULD NOT BE PRESENTED FOR INSPECTION BY THE FIRE MARSHAL. APPROVED PLANS ARE TO BE KEPT ON SITE AT ALL TIMES. IF APPROVED PLANS CANNOT BE LOCATED, A REQUEST TO THE BUILDING DEPARTMENT MAY BE ABLE TO DUPLICATE THE ORIGINAL. APPROVED PLANS MUST BE SUBMITTED TO FIRE MARSHAL OR THE PROCESS FOR HIGH-PILED STORAGE PLAN SUBMITTAL PROCESS SHALL BE RESTARTED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8566 | NFPA 13: 12.12.1.2 – WOOD PALLETS, WHERE STORED INDOORS, SHALL MEET THE FOLLOWING:(1) PALLETS SHALL BE STORED NO HIGHER THAN 6 FEET.(2) EACH PALLET PILE OF NO MORE THAN 4 STACKS SHALL BE SEPARATED FROM OTHER PALLET PILES BY AT LEAST 8 FEET OF CLEAR SPACE OR 25 FEET OF COMMODITY.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8567 | AISLES WIDTHS STATED ON THE APPROVED PLANS ARE NOT BEING MAINTAINED AND SHALL BE BROUGHT INTO COMPLIANCE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8568 | THE EXIT PATHWAYS AND EXIT STAIRWAYS LEADING AWAY FROM THE WAREHOUSE SHALL HAVE A CLEAR PATH TO AN AREA OF SAFE REFUGE.COMPLIANCE: WITHIN 7 CALENDAR DAYS.
8569 | NoData
8570 | NoData
8571 | NoData
8572 | BREAKER PANELS REQUIRED A THREE FEET DISAANCE CLEARANCE WITH NO STORAGE HAZARDS.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8573 | FIRE EXTINGUISHERS ARE REQUIRED EVERY 75 FEET IN THE WAREHOUSE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8574 | AT THE TIME OF INSPECTION, APPROVED PLANS COULD NOT BE PRESENTED FOR INSPECTION BY THE FIRE MARSHAL. APPROVED PLANS ARE TO BE KEPT ON SITE AT ALL TIMES. IF APPROVED PLANS CANNOT BE LOCATED, A REQUEST TO THE BUILDING DEPARTMENT MAY BE ABLE TO DUPLICATE THE ORIGINAL. APPROVED PLANS MUST BE SUBMITTED TO FIRE MARSHAL OR THE PROCESS FOR HIGH-PILED STORAGE PLAN SUBMITTAL PROCESS SHALL BE RESTARTED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8575 | AISLES WIDTHS STATED ON THE APPROVED PLANS ARE NOT BEING MAINTAINED AND SHALL BE BROUGHT INTO COMPLIANCE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8576 | THE EXIT PATHWAYS AND EXIT STAIRWAYS LEADING AWAY FROM THE WAREHOUSE SHALL HAVE A CLEAR PATH TO AN AREA OF SAFE REFUGE.COMPLIANCE: WITHIN 7 CALENDAR DAYS.
8577 | NoData
8578 | NoData
8579 | ALL FIRE EXTINGUISHERS SHALL HAVE A CURRENT ANNUAL INSPECTION TAG BY AN APPROVED LICENSED FIRE PROTECTION EQUIPMENT COMPANY. ALL SERVICING, TESTING, MAINTENANCE AND TAGGING OF LISTED PORTABLE FIRE EXTINGUISHERS SHALL BE CONDUCTED ANNUALLY BY QUALIFIED PERSONNEL IN ACCORDANCE WITH LSB STANDARD 01, "INSTALLATION AND MAINTENANCE OF PORTABLE FIRE EXTINGUISHERS" COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8580 | ISSUED PERMITS SHALL BE KEPT AT FACILITY AT ALL TIMES AND SHALL BE READILY AVAILABLE FOR INSPECTION BY THE FIRE CODE OFFICIAL.APPLY FOR AND OBTAIN (HIGH_PILED STORAGE) OPERATIONAL PERMIT FROM THE CITY OF HOUSTON PERMITTING CENTER LOCATED AT 1002 WASHINGTON AVE. (832-394-9000). COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8581 | AT THE TIME OF INSPECTION, APPROVED PLANS COULD NOT BE PRESENTED FOR INSPECTION BY THE FIRE MARSHAL. APPROVED PLANS ARE TO BE KEPT ON SITE AT ALL TIMES. IF APPROVED PLANS CANNOT BE LOCATED, A REQUEST TO THE BUILDING DEPARTMENT MAY BE ABLE TO DUPLICATE THE ORIGINAL. APPROVED PLANS MUST BE SUBMITTED TO FIRE MARSHAL OR THE PROCESS FOR HIGH-PILED STORAGE PLAN SUBMITTAL PROCESS SHALL BE RESTARTED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8582 | Please replace defective heat detector located in building 4.
8583 | NoData
8584 | GATES SIGNS SHALL BE AT EVERY ENTRY/EXIT DRIVE-THRU.
8585 | NoData
8586 | NoData
8587 | NoData
8588 | NoData
8589 | NoData
8590 | NoData
8591 | NoData
8592 | NoData
8593 | NoData
8594 | NoData
8595 | NoData
8596 | NoData
8597 | NoData
8598 | NoData
8599 | NoData
8600 | NoData
8601 | NoData
8602 | HAVE A FIRE PROTECTION ENGINEER EVALUATE ALL AREAS OF THE FACILITY INCLUDING ALL STORAGE, USAGE, PROCESSES AND DRAWINGS TO ASSURE COMPLIANCE WITH ALL APPLICABLE CODES. A COPY OF THE STAMPED FIRE PROTECTION ENGINEERS REPORT SHALL BE SUBMITTED FOR REVIEW TO THE CODE OFFICIAL. COMPLIANCE WITHIN 30 CALENDAR DAYS. MORE TIME MAY BE GRANTED UPON WRITTEN REQUEST FROM THE FIRE ENGINEER ONLY.
8603 | FILL OUT THE HMIS USING THE GUIDELINE PROVIDED. COMPLIANCE WITHIN 30 DAYS.
8604 | HAVE QUALIFIED SPRINKLER COMPANY PERFORM 5 YEAR TESTING ON THE SPRINKLER RISERS. COMPLIANCE WITHIN 30 DAYS.
8605 | ALL FIRE EXTINGUISHERS SHALL HAVE A CURRENT ANNUAL INSPECTION TAG BY AN APPROVED LICENSED FIRE PROTECTION EQUIPMENT COMPANY. ALL SERVICING, TESTING, MAINTENANCE AND TAGGING OF LISTED PORTABLE FIRE EXTINGUISHERS SHALL BE CONDUCTED ANNUALLY BY QUALIFIED PERSONNEL IN ACCORDANCE WITH LSB STANDARD 01, "INSTALLATION AND MAINTENANCE OF PORTABLE FIRE EXTINGUISHERS" COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8606 | FIRE DETECTION, ALARM AND EXTINGUISHING SYSTEMS SHALL BE MAINTAINED IN AN OPERATIVE CONDITION AT ALL TIMES, AND SHALL BE REPLACED OR REPAIRED WHERE DEFECTIVE.THE FIRE PROTECTION SPRINKLER SYSTEM SHALL BE TESTED ANNUALLY BY A LICENSED COMPANY AND ALL TROUBLE TAG(S) SHALL BE REMOVED AND ACCEPTABLE SERVICE TAG(S) SHALL BE AFFIXED TO ENSURE SYSTEM IS MAINTAINED IN OPERATIVE CONDITION.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8607 | USING THE FORMAT PROVIDED, A CURRENT HMIS STATEMENT SHALL BE SUBMITTED TO THE HAZMAT / HIGH-PILED 180 TEAM FOR REVIEW. THE HMIS FORM AND INSTRUCTIONS ON HOW TO FILL OUT THE FORM CAN BE FOUND AT THE CITY OF HOUSTON WEBSITE: HTTP://WWW.HOUSTONTX.GOV/FIRE/FORMS/HMISCORRECTLY FILL OUT A NEW HMIS FOR ALL HAZARDOUS MATERIALS STORED INSIDE THE BUILDING. THE WAREHOUSE AREA AND THE HAZARDOUS MATERIALS STORAGE ROOM REQUIRE SEPARATE HMIS’S. THE CLASSIFICATION OF THE HAZARDOUS MATERIALS SHALL COMPLY WITH THE 2012 INTERNATIONAL FIRE CODE CLASSIFICATIONS SYSTEM.IT IS HIGHLY ADVISABLE TO SEEK TECHNICAL ASSISTANCE IN CORRECTLY COMPLETING THE HMIS FOR THE HAZARDOUS MATERIAL BEING STORED ON THE FACILITY.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8608 | ISSUED PERMITS SHALL BE KEPT AT FACILITY AT ALL TIMES AND SHALL BE READILY AVAILABLE FOR INSPECTION BY THE FIRE CODE OFFICIAL.APPLY FOR AND OBTAIN A (HAZMAT STORAGE) OPERATIONAL PERMIT FROM THE CITY OF HOUSTON PERMITTING CENTER LOCATED AT 1002 WASHINGTON AVE. (832-394-9000). COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8609 | AT THE TIME OF INSPECTION, APPROVED H-ROOM PLANS COULD NOT BE PRESENTED FOR INSPECTION BY THE FIRE MARSHAL. APPROVED PLANS ARE TO BE KEPT ON SITE AT ALL TIMES. IF APPROVED PLANS CANNOT BE LOCATED, A REQUEST TO THE BUILDING DEPARTMENT MAY BE ABLE TO DUPLICATE THE ORIGINAL.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8610 | HAVE QUALIFIED SPRINKLER COMPANY ADDRESS ALL THE ISSUES STATED ON THE YELLOW TAG ON THE SPRINKLER RISER. COMPLIANCE WITHIN 30 DAYS.
8611 | THE SPRINKLER SYSTEM SHALL BE EVALUATED BY A QUALIFIED FIRE PROTECTION ENGINEER OR A MINIMUM NICET LEVEL 3 FIRE SPRINKLER TECHNICIAN TO DETERMINE IF THE SYSTEM IS ADEQUATE FOR THE COMMODITIES BEING STORED. THE EVALUATION SHALL INDICATE THE SPRINKLER DENSITY, CHARTS AND TABLES TO DETERMINE IF THE SYSTEM PROVIDES ADEQUATE COVERAGE FOR CURRENT STORAGE ARRAY. FPE SHALL ALSO ADDRESS CONTAINMENT ISSUES, POSSIBLE CONTROL AREAS, VENTILATION, AND ALL OTHER GUIDELINES SET FORTH IN 2012 IFC FOR THE STORAGE OF FLAMMABLE/ COMBUSTIBLE LIQUIDS. IF YOU CHOOSE NOT TO DO THIS, LOWER ALL FLAMMABLE/ COMBUSTIBLE LIQUIDS BELOW MAXIMUM ALLOWABLE QUANTITIES LISTED IN CH. 50 AND 57 OF THE 2012 IFC. COMPLIANCE WITHIN 30 DAYS.
8612 | LOWER ALL HAZARDOUS MATERIALS THAT EXCEED MAXIMUM ALLOWABLE QUANTITIES PER TABLE 3404.3.4.1 FROM THE 2006 IFC OR TABLE 5704.3.4.1 FROM THE 2012 IFC. AFTER AMOUNTS ARE BELOW MAQ, A NEW HMIS SHALL BE SUBMITTED SHOWING THE NEW NUMBERS UNDER MAQ. COMPLIANCE BY MAY 14, 2018
8613 | HAVE QUALIFIED SPRINKLER COMPANY ACCESS THE TECH SERVICE ROOM AND ADD THE AMOUNT OF SPRINKLER HEADS NEEDED. COMPLIANCE WITHIN 30 DAYS.
8614 | REMOVE ALL ILLEGAL LOCKS AND DROP BARS ON ALL EXIT DOORS IN YOUR WAREHOUSE. EXITS REQUIRE ONE MOTION TO EXIT THE BUILDING. COMPLIANCE BY FRIDAY 2-9-2018
8615 | Repair ASAP.
8616 | Alarm panel is currently displaying a blue tag no action is required for this item.
8617 | There is a yellow tag on the sprinkler riser. When the necessary repairs are made forward the information to me.
8618 | The fire pump currently has a yellow tag attached once the necessary repairs are made forward the information to me.
8619 | NoData
8620 | NoData
8621 | NoData
8622 | NoData
8623 | NoData
8624 | NoData
8625 | NoData
8626 | NoData
8627 | NoData
8628 | ADD ADDRESS NUMBERS IN A VISIBLE LOCATION THAT IS VISIBLE FROM THE STREET.
8629 | ADD DECALS TO FRONT ENTRY DOORS THAT READS, "THIS DOOR TO REMAIN UNLOCKED DURING BUSINESS HOURS".
8630 | NoData
8631 | NoData
8632 | NoData
8633 | NoData
8634 | NoData
8635 | NoData
8636 | NoData
8637 | NoData
8638 | NoData
8639 | NoData
8640 | NoData
8641 | NoData
8642 | NoData
8643 | NoData
8644 | NoData
8645 | NoData
8646 | NoData
8647 | NoData
8648 | NoData
8649 | NoData
8650 | NoData
8651 | NoData
8652 | NoData
8653 | NoData
8654 | Provide Electrical Spacers for 1st floor Electrical Room Panels.
8655 | NoData
8656 | 1) Provide repair (Correction Tag) for Trouble Alarm on Main Fire Alarm Panel. 2) Replace or Repair Emergency Lights for the 1st floor east side hallway and the 3rd floor emergency stairwell.
8657 | Discontinue storage inside ground floor Stair "A."
8658 | 1st Floor Electrical Room.
8659 | 1) Provide bright red paint for Key Box 2) Provide Lubricant for Lock periodically to prevent rusting an d easy opening of sticking lock.
8660 | Provide current update for Emergency Contact List and Mobility Impaired List for Fire Depository Box.
8661 | Replace Ceiling Tile inside 3rd floor Electrical Room and the Elevator Room.
8662 | Throughout Equipment Rooms.
8663 | NoData
8664 | NoData
8665 | NoData
8666 | NoData
8667 | NoData
8668 | NoData
8669 | NoData
8670 | Proof of gas test needed.
8671 | NoData
8672 | NoData
8673 | NoData
8674 | 1) Gate right of office needs new falcon lock and conduit needs to be secured to gate. 2) Manual gate on Sabo can be left like it is (unlocked) or secure gate with chain and place key in new 911 box mounted to gate post. 3) Kleckley gate needs failsafe and 911 box installed. 4) Manual gate on Kingspoint needs new 911 box mounted on gate post with new falcon lock and key to gate placed inside 911 box.
8675 | NoData
8676 | NoData
8677 | NoData
8678 | LSB2020.1.3.6 Installation.Portable fire extinguishers shall be installed on the hangers or in the brackets supplied, mounted in cabinets, or set on shelves, unless the extinguisher is of the wheeled type.Compliance: 30 calendar days.
8679 | 109.2 Owner/occupant responsibility. Correction and abatement of violations of this code shall be the responsibility of the owner. If an occupant creates, or allows to be created, hazardous conditions in violation of this code, the occupant shall be held responsible for the abatement of such hazardous conditions.
8680 | 6103.2.2 Industrial vehicles and floor maintenance machines. LP-gas containers on industrial vehicles and floor maintenance machines shall comply with Sections 11.13 and 11.14 of NFPA 58. Industrial lift trucks stored inside of buildings shall be kept in an approved area. LP-gas containers not attached for use shall be stored outside of the building in accordance with Table 6104.3 .Compliance: immediately.
8681 | 604.2.4 Means of egress illumination. Emergency power shall be provided for means of egress illumination in accordance with Section 1006.3.Compliance: 30 calendar days.
8682 | Where access to or within a structure or an area is restricted because of secured openings or where immediate access is necessary for life-saving or fire-fighting purposes, the fire code official is authorized to require a key box or a fire depository box to be installed in an approved location. The key box shall be of an approved type listed in accordance with UL 1037, and shall contain keys to gain necessary access as required by the fire code official. Key boxes shall be provided in accordance with Houston Fire Department LSB Standard No. 05, “Key Boxes.”
8683 | Ensure extinguishers are unobstructed.
8684 | Clear and maintain clearance in front of the breaker panels.
8685 | Ensure all exit doors are unlocked while the building is occupied.
8686 | NoData
8687 | NoData
8688 | NoData
8689 | NoData
8690 | Empty can nightly as needed.
8691 | Remove boxes and filters from mechanical rooms.
8692 | Mobility impairment needs to be updated.Update emergency contact info.
8693 | Need an additional lock out/ tag out.
8694 | F7 Permit is expire at this time
8695 | COMPLIANCE DATE: 15 CALENDAR DAYS
8696 | NoData
8697 | NoData
8698 | NoData
8699 | NoData
8700 | Fire Alarm Red TagMaintain Self Fire Watch until fire protection systems are back in normal service.
8701 | A valid Certificate of Occupancy is required before occupying any building in the City of Houston. Apply for this C of O or a name change of the previous business if there has been no change of use between businesses. This can be done at 1002 Washington Ave. and you can find information on the City of Houston website under occupancy inspection.Compliance by 9-17-2020
8702 | HAVE FIRE EXTINGUISHER LOCATED IN ELECTRICAL ROOM INSPECTED AND TAGGED.
8703 | LABEL DOOR WHERE ELECTRICAL PANEL IS LOCATED WITH SIGN THAT READS, "ELECTRICAL ROOM".
8704 | MOVE EXIT SIGN THAT IS LOCATED IN OFFICE WHERE THERE IS NO DOOR.
8705 | REMOVE ALL STORAGE THAT IS LOCATED DIRECTLY IN FRONT OF ELECTRICAL PANEL. KEEP A 3FT CLEARANCE IN FRONT OF ELECTRICAL PANEL AT ALL TIMES.
8706 | NoData
8707 | NoData
8708 | Fire Sprinkler System is out of service.Maintain the prior established self fire watch until all fire protection systems are in regular service.
8709 | NoData
8710 | NoData
8711 | SEVERAL REMINDERS AND EXTRA TIME ALLOWED TO PAY FOR b1 PERMIT; STILL REMAINS UNPAID. ADD RE-INSPECTION FEE AND MUST BE PAID IN 10 DAYS
8712 | NoData
8713 | NoData
8714 | NoData
8715 | NoData
8716 | All fire prevention permits for this location are voided. Customer has moved since 2019
8717 | NoData
8718 | NoData
8719 | NoData
8720 | NoData
8721 | NoData
8722 | NoData
8723 | NoData
8724 | NoData
8725 | Access Gate expired 09/2020. Renew within 7 days.
8726 | All gates must have a 911 knox box or an approved LSB 04 padlock.
8727 | All Access gates must comply to LSB 04. Current gates must remain open until all issues are corrected. Gates must comply within 30 days
8728 | LAST INSPECTED 11/2019 - CURRENT ANNUAL INSPECTION REQUIRED. ADDRESS ISSUES NOTED ON YELLOW TAG FROM LAST ANNUAL INSPECTION.
8729 | Building B has a Fire Sprinkler Valve that has not been had the annual inspection. Perform the inspection and make any corrections required.
8730 | Approved submitted plans for the American Spectaclar event at the George R Brown and conducted a permit inspection(Assembly) in Hall B3.
8731 | NoData
8732 | NoData
8733 | NoData
8734 | NoData
8735 | NoData
8736 | The required permits shall be purchased within 2 weeks and maintained on site to avoid citations.
8737 | Obtain an L1: LPG operational permit and post on site for the storage and use of propane.Permits may be obtained at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811 www.houstonpermittingcenter.org
8738 | Obtain a P2: Public Assembly operational permit. This permit is required due to your facility's A-2 occupancy type with occupant load over 50 persons, as stipulated on the Certificate of Occupancy.Permits may be obtained at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811 www.houstonpermittingcenter.org
8739 | NoData
8740 | Repair ASAP.
8741 | Repair ASAP.
8742 | NoData
8743 | NoData
8744 | The owner/occupant is responsible for obtaining all permits and correcting all fire code violations.
8745 | Must place used oily rags in the metal container with the self closing lid.
8746 | Must place an exit sign above the exit door in the office.
8747 | Must obtain a hot works permit for the cutting/welding rigs.
8748 | Must have the exit sign and emergency lights repaired or replaced as needed to operate normally.
8749 | Must obtain the H3(Hot Works) and the F7(Flammable/Combustible Storage and Use) permits from the Houston Permitting Center located at 1002 Washington Avenue. Fire Permits are located on the second floor.
8750 | Must obtain a F7 permit for the storage of waste oil tanks located on the business property.
8751 | Must place "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED" on the rear exit door and the door must remain unlocked.
8752 | The fire suppression system for the vent hoods is due for service before the end of 03/2021.
8753 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
8754 | Clear and maintain working space in front of the breaker panels.
8755 | NoData
8756 | NoData
8757 | NoData
8758 | NoData
8759 | NoData
8760 | NoData
8761 | NoData
8762 | NoData
8763 | NoData
8764 | NoData
8765 | NoData
8766 | NoData
8767 | NoData
8768 | NoData
8769 | Permits Expired1/28/2021; Unpaid Fees $652.18
8770 | LAST INSPECTED 4/2019 - NEEDS CURRENT ANNUAL AND ALSO 5TH YEAR INSPECTION (PER YELLOW TAG). CORRECT YELLOW TAG ISSUES NOTED BY FIRE PROTECTION COMPANY ON LATEST INSPECTION REPORT.
8771 | NEED KEYS FOR BUILDING ACCESS TO BOTH FRONT AND BACK DOORS
8772 | PROVIDE NFPA SIGN (SIMILAR TO ONE AT CURRENT MAIN ENTRANCE)
8773 | NEEDS CURRENT ANNUAL INSPECTION - MOST CURRENT TAG IS SERVICE TAG FROM 2019
8774 | Please correct deficiencies noted on yellow tag.
8775 | NoData
8776 | NoData
8777 | Fire extinguishers must be tagged annually.
8778 | NoData
8779 | Repair ASAP.
8780 | Repair the exit sign located in the boys locker room hallway, in the corner of the hallway, near the restroom.
8781 | Means of egress paths shall be maintained and reliable. Clear out all excessive storage in the Boy and Girls locker rooms. Clear out the storage in the hallway by the Gym Door (B115). Remove the mats, chairs, and equipment.
8782 | Provide documentation for a current emergency egress light annual test.An approved licensed master electrician or licensed electrical service company shall test all emergency lighting systems annually. The battery units, whether of the acid or alkali type, shall be tested continuously for a minimum of 90 minutes.Failed devices shall be repaired or replaces as soon as possible. Provide dated documentation stating the master electrician and/or company's certification number, and that all devices passed the 90-minute test.
8783 | Standpipe hose annual inspection is needed. Provide current annual inspection tag and documentation in the Fire Marshals Binder.Check all standpipe hose cabinets for current tags / inspections:- Annual inspection tag- 3yr pressure test- 5yr Hydrostatic test for pipingNoted - by exit near B117-C and in the kitchen
8784 | Verify that all extinguishers have had their annual inspection and are marked with a current tag.
8785 | The semi annual kitchen ansul system test is expired. Provide a current test and tag on the system.
8786 | Storage shall be kept orderly and egress paths kept clear. Clear out all excessive storage in the Boy and Girls locker rooms. Clear out the storage in the hallway by the Gym Door (B115). Remove the mats, chairs, and equipment.
8787 | Maintain ceiling clearance minimums as stated in the fire code. - C124 no storage top shelf- E107-
8788 | Clear out combustibles and trash / rubbish out of the swimming pool basement and boiler room.Egress entanglement items such as water hose should be stored neatly or removed. Tripping and egress hazards removed.
8789 | Provide documentation for an intercom or two way communication device test
8790 | Provide a current annual fire safety training sign in sheet / documentation.
8791 | Replace missing ceiling tiles B117-A coaches office and any other places where they are missing.
8792 | Remove hanging displays and / or decorations- T-26 (including lights)
8793 | Provide a master fire drill log
8794 | Provide approved fire alarm system plans for every T-building on site for review of the inspecting code official. The produced plans must match the existing T-buildings on location, not T-buildings that have been moved and replaced by another T-building. If no fire alarm system plans can be produced, submit fire alarm system plans to the City of Houston Plans Checking department for review and approval.
8795 | Provide a current Elevator Permit.
8796 | Renew the H1 permit that expired on 11/4/2020
8797 | Some Certificate of Occupancy permits for the T Buildings do not match their designation. Some existing T-buildings that were previously on site were moved to 6301 South Loop East - Brookline ES and were replaced with other T-buildings. Provide a Certificate of Occupancy for each T-building (matching the building designation marked on the building).
8798 | Maintain clearance space minimums required by code, around all electrical panels and components. C-124 noted specifically
8799 | Renew the expired burglar alarm permit
8800 | Keep fire Marshal’s Binder / Records Orderly. Remove old or expired copies. Remove duplicate copies. Keep old records in an archived binder or another location. Provide copies of all current life safety system test in the Fire Marshal’s Binder for review by the inspecting code official. Missing reports noted:- Standpipe Hose 5yr- Fire Alarm System Annual Inspection Report- Egress Light Test- Intercom Test
8801 | Provide test documentation for the current annual Fire Alarm System test
8802 | NoData
8803 | NoData
8804 | NoData
8805 | All areas designated as a fire extinguisher locations by a sign shall have an extinguisher mounted or housed in an approved manner. Compliance: 30 calendar days.
8806 | NoData
8807 | Per fire code, a copy of the approved plans shall be maintained on the premises at all times.Compliance: 30 calendar days.
8808 | HIGH-PILED COMBUSTIBLE STORAGE.Storage of combustible materials in closely packed piles or combustible materials on pallets, in racks or on shelves where the top of storage is greater than 12 feet (3658 mm) in height. When required by the fire code official, high-piled combustible storage also includes certainhigh-hazard commodities, such as rubber tires,Group A plastics, flammable liquids, idle palletsand similar commodities, where the top of storage is greater than 6 feet (1829 mm) in height. NFPA 13: 12.12.1.1 - WOOD PALLETS SHALL BE PERMITTED TO BE STORED IN THE FOLLOWING ARRANGEMENTS:(1) Stored outside.(2) Stored in a detached structure.(3) Stored indoors where arranged in accordance with 12.12.1.2. NFPA 13: 12.12.1.2 – WOOD PALLETS, WHERE STORED INDOORS, SHALL MEET THE FOLLOWING:(1) pallets shall be stored no higher than 6 feet.(2) each pallet pile of no more than 4 stacks shall be separated from other pallet piles by at least 8 feet of clear space or 25 feet of commodity.You are not approved for high-piled storage and previously signed a owner's statement of intended use, which stated that you would not be a high-piled storage facility. Lower all commodities to below 12 feet and lower all high hazard commodities to below 6 feet.IMMEDIATE COMPLIANCE IS REQUIRED.
8809 | For informational purposes.
8810 | For informational purposes.
8811 | The owner/occupant shall be heldresponsible for the correction and abatement of all violations listed in thisnotice of violations report. COMPLIANCE:WITHIN 30 CALENDAR DAYS
8812 | The 911 key box, or Knox Box 3200 series hinged lid, shall be of an approved type listed in accordance with UL 1037 and shall contain keys for immediate access for lifesaving or firefighting purposes.(SEE ATTACHED LSB STANDARD 05 FOR MORE INFORMATION.)
8813 | You must provide a 911 key box with a key for the fire department to gain emergency access to the facility according to LSB Standard 05.COMMPLIANCE: WITHIN 30 CALENDAR DAYS.
8814 | The 911 key box, or Knox Box 3200 series hinged lid, shall be of anapproved type listed in accordance with UL 1037 and shall contain keys forimmediate access for lifesaving or firefighting purposes.(SEE ATTACHED LSB STANDARD 05 FOR MORE INFORMATION.)
8815 | The new 911 key box shall be attached according to the requirements described in LSB 5.3.3 above.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8816 | Mark your building(s) with the address as stated above.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8817 | The "FDC" sign shall be labeled with reflective white letters no less than 2 inches in height and follow the above code.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8818 | A working space (cleared of all combustible material) of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
8819 | NoData
8820 | NoData
8821 | NoData
8822 | NoData
8823 | NoData
8824 | NoData
8825 | NoData
8826 | NoData
8827 | NoData
8828 | NoData
8829 | Maximum Allowable Quantities for Corrosives are as follows:INDOOR STORAGE OUTDOOR STORAGE975 Gallons (liquid) 1950 Gallons (liquid)9,750 Pounds (solid) 19,500 Pounds (solid)To exceed the above listed quantities, an application for an H4 Certificate of Occupancy is required.A guideline is included with this notice which specifies requirements needing to be met to start the Hazmat process.
8830 | Any extension cords currently being used as permanent wiring must be removed.This violations applies to all occupancies on location.
8831 | NoData
8832 | No Violations at the time of inspection
8833 | NoData
8834 | NoData
8835 | NoData
8836 | NoData
8837 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRESUPPRESSION EQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALSAND DOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ONSITE FOR FIRE MARSHAL INSPECTION
8838 | WHERE LOCAL FIRE MARSHAL APPROVALS AREREQUIRED BY REGULATORY AGENCIES, APPROVED FIRE SAFETY AND EVACUATION PLANSSHALL BE PREPARED, MAINTAINED AND POSTED IN GROUP E OCCUPANCIES
8839 | NoData
8840 | INFORMATION TO BE INCLUDED IN FIRE EVACUATIONPLANS
8841 | POST ADDRESS CONSPICUOUSLY - THE LOCATION MUST HAVE A NUMERICAL ADDRESS WHICH IS CLEARLY VISIBLE FROM THE STREET
8842 | THE CERTIFICATE OF OCCUPANCY AND ALLREQUIRED PERMITS MUST BE POSTED CONSPICUOUSLY IN THE BUSINESS AT ALL TIMES
8843 | MISSING ILLUMINATED EMERGENCY EXIT SIGNS MUST BE INSTALLED AND TESTED
8844 | INFORMATION TO BE INCLUDED IN FIRE SAFETYPLANS
8845 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
8846 | OBTAIN A CERTIFICATE OF OCCUPANCY AND ANY OTHER PERMITS REQUIRED PER THE CODE
8847 | NoData
8848 | NoData
8849 | FAILURE TO FOLLOW UP ON CORRECTING VIOLATIONS
8850 | REMOVE DEADBOLT (PLAYGROUND EXIT) AND LOCKING DOOR HANDLE (FRONT ENTRY/EXIT) WHICH ARE BEING USED IN CONJUNCTION WITH PANIC HARDWARE
8851 | NoData
8852 | NoData
8853 | NoData
8854 | NoData
8855 | No violations noted at this time.
8856 | NoData
8857 | NoData
8858 | NoData
8859 | The owner/occupant is responsible for correcting all fire code violations.
8860 | Need to have an audibility test performed.
8861 | Need to have sensitivity test done every 2 years.
8862 | NoData
8863 | NEED TO BE SERVICE 2-5-20 LAST DATE
8864 | NoData
8865 | Fire panel need service. Has a trouble signal light on. 1-25-2020 last date
8866 | Need service . Last date 6-18
8867 | NoData
8868 | NoData
8869 | FIRE PANEL ROOM ,RISER ROOM,BOILER ROOM FIRE EXTINGUISHERS NEED TO BE SERVICE. 5-18 LAST DATE
8870 | NoData
8871 | NEED TO BE SERVICE, HAS A TROUBLE SIGNAL ON. LAST DATE 6-11-20. FIX ALL TAGS
8872 | NEED TO BE SERVICE. LAST DATE 3-19
8873 | FAILURE TO GET THE SPRINKLER SYSTEM SERVICE AND FIRE PANEL HAS TROUBLE LIGHT ON
8874 | NoData
8875 | NEED SERVICE HAS TROUBLE LIGHT ON. LAST DATE 1-22-2020
8876 | NEED SERVICE IN NOVEMBER LAST DATE 5-20
8877 | NEED SERVICE. LAST DATE 5-19
8878 | NoData
8879 | NEED SERVICE. LAST DATE 7-19
8880 | FAILURE TO SERVICE FIRE EXTINGUISHERS 7-19 LAST DATE
8881 | NEED SERVICE 7-19 LAST DATE
8882 | NEED SERVICE 8-19 LAST DATE
8883 | NoData
8884 | FIRE PANEL NEED SERVICE. 4-5-19 LAST DATE
8885 | FAILURE TO SERVICE THE FIRE PANEL 4-5-19 LAST DATE
8886 | NoData
8887 | NoData
8888 | Have a licensed fire protection company service and tag the ansul system. The vent hood is due for cleaning.
8889 | NoData
8890 | NoData
8891 | NoData
8892 | P2 permit is expired. Expired on 1/12/2021. Amount owed for permit 503.95 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
8893 | Needs to be inspected.
8894 | Provide compliance letters
8895 | It is the owner/occupants responsibility to correct the violation found.
8896 | The FDC on the south side of the building was found to have 2.5 inch "male" couplings. Contact a licensed fire protection company to have the FDC replaced with a fitting that has 2.5 inch "female" couplings.
8897 | NoData
8898 | NoData
8899 | REMOVE AUTOMOBILE PARTS STORAGE THAT IS LOCATED DIRECTLY IN FRONT OF ELECTRICAL PANEL.
8900 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
8901 | Permit Expired 1/22/2021; Unpaid Fees $385.38
8902 | Apply for hot works permit.
8903 | NoData
8904 | NoData
8905 | NoData
8906 | Audibility test required every 3 years.
8907 | Sprinkler due for 5 year test.
8908 | NoData
8909 | Sign on FDC must indicate which building is covered.
8910 | Sleeping quarters window must be accessible to be used as a secondary egress
8911 | Fire drills must be updated
8912 | Alarm system must operate without trouble signal
8913 | NoData
8914 | NoData
8915 | NoData
8916 | Provide address numbers on the front of the business.
8917 | Remove obstructions in front of the class K fire extinguisher located in the kitchen.
8918 | NoData
8919 | Make all repairs to all fire protection systems. Continue the self initiated fire watch until all Fire Alarms and Fire Sprinkler Systems are back in regular ready status.
8920 | NoData
8921 | NoData
8922 | NoData
8923 | Event manager has submitted a site drawing for the Art Heist Event.
8924 | HAVE RED TAG ON FIRE ALARM PANEL REPAIRED WITHIN 7 BUSINESS DAYS.
8925 | NoData
8926 | NoData
8927 | NoData
8928 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
8929 | NoData
8930 | The City of Houston requires an occupancy with an electronic access gate and key box to hold and maintain a K1 (Key Box) and A4 ( Access Gate) permit. Permits can be obtained through the Houston Permitting Center located at 1002 Washington Ave Houston, Tx 77002. 832-394-8811
8931 | Approved no violations noted.
8932 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
8933 | Permit Expired 1/27/2021; Unpaid Fees $385.38
8934 | NoData
8935 | NoData
8936 | Repair ASAP.
8937 | Please have annual test done on both systems
8938 | Please have annual test done on both systems
8939 | NoData
8940 | Event manager submitted a site plan of the event and the plan has been approved.
8941 | NoData
8942 | NoData
8943 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
8944 | Renewal of the assembly permit is required.
8945 | NoData
8946 | NoData
8947 | NoData
8948 | NoData
8949 | Sign letter provided.
8950 | Label exterior electrical boxes with unit number they operate.
8951 | Sign letter provided.
8952 | FYI: Last gas test performed on 2/22/2018. #17138120.
8953 | Need access gate permit.
8954 | Sign letter provided.
8955 | Need key box permit.
8956 | Main gate- Switch not working. Need keys for failsafe to place in 911 box. Back gate (entrance side) paint 911 box red. Need new pad locks for failsafe and keys to be placed in 911 box. Back gate (exit side) switch not working. Need new pad lock and key for 911 box.
8957 | NoData
8958 | NoData
8959 | NoData
8960 | NoData
8961 | NoData
8962 | NoData
8963 | NoData
8964 | NoData
8965 | NoData
8966 | Have a licensed fire protection company service and tag the fire extinguishers.
8967 | Have a licensed fire protection company service and tag the vent hood suppression system.
8968 | Repair the emergency illumination on the exit signs.
8969 | Repair the exit sign located in the boys locker room hallway, in the corner of the hallway, near the restroom.
8970 | Means of egress paths shall be maintained and reliable. Clear out all excessive storage in the Boy and Girls locker rooms. Clear out the storage in the hallway by the Gym Door (B115). Remove the mats, chairs, and equipment.
8971 | Provide documentation for a current emergency egress light annual test.An approved licensed master electrician or licensed electrical service company shall test all emergency lighting systems annually. The battery units, whether of the acid or alkali type, shall be tested continuously for a minimum of 90 minutes.Failed devices shall be repaired or replaces as soon as possible. Provide dated documentation stating the master electrician and/or company's certification number, and that all devices passed the 90-minute test.
8972 | Standpipe hose annual inspection is needed. Provide current annual inspection tag and documentation in the Fire Marshals Binder.Check all standpipe hose cabinets for current tags / inspections:- Annual inspection tag- 3yr pressure test- 5yr Hydrostatic test for pipingNoted - by exit near B117-C and in the kitchen
8973 | Verify that all extinguishers have had their annual inspection and are marked with a current tag.
8974 | The semi annual kitchen ansul system test is expired. Provide a current test and tag on the system.
8975 | Storage shall be kept orderly and egress paths kept clear. Clear out all excessive storage in the Boy and Girls locker rooms. Clear out the storage in the hallway by the Gym Door (B115). Remove the mats, chairs, and equipment.
8976 | Maintain ceiling clearance minimums as stated in the fire code. - C124 no storage top shelf- E107-
8977 | Clear out combustibles and trash / rubbish out of the swimming pool basement and boiler room.Egress entanglement items such as water hose should be stored neatly or removed. Tripping and egress hazards removed.
8978 | Provide documentation for an intercom or two way communication device test
8979 | Provide a current annual fire safety training sign in sheet / documentation.
8980 | Replace missing ceiling tiles B117-A coaches office and any other places where they are missing.
8981 | Remove hanging displays and / or decorations- T-26 (including lights)
8982 | Provide a master fire drill log
8983 | Provide approved fire alarm system plans for every T-building on site for review of the inspecting code official. The produced plans must match the existing T-buildings on location, not T-buildings that have been moved and replaced by another T-building. If no fire alarm system plans can be produced, submit fire alarm system plans to the City of Houston Plans Checking department for review and approval.
8984 | Provide a current Elevator Permit.
8985 | Some Certificate of Occupancy permits for the T Buildings do not match their designation. Some existing T-buildings that were previously on site were moved to 6301 South Loop East - Brookline ES and were replaced with other T-buildings. Provide a Certificate of Occupancy for each T-building (matching the building designation marked on the building).
8986 | Renew the H1 permit that expired on 11/4/2020
8987 | Maintain clearance space minimums required by code, around all electrical panels and components. C-124 noted specifically
8988 | Renew the expired burglar alarm permit
8989 | Provide test documentation for the current annual Fire Alarm System test
8990 | Keep fire Marshal’s Binder / Records Orderly. Remove old or expired copies. Remove duplicate copies. Keep old records in an archived binder or another location. Provide copies of all current life safety system test in the Fire Marshal’s Binder for review by the inspecting code official. Missing reports noted:- Standpipe Hose 5yr- Fire Alarm System Annual Inspection Report- Egress Light Test- Intercom Test
8991 | NoData
8992 | NoData
8993 | NoData
8994 | Yellow/Red Tagged Fire Alarm Panel.
8995 | Annual generator load test is due.
8996 | While putting locks on 911 boxes, one lock was faulty and would not release my falcon key. Please return faulty lock for a new one.
8997 | 5 year gas test is due
8998 | F7 (Fuel Storage) permit is needed for the generator fuel storage tank
8999 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
9000 | CORRECT YELLOW TAG ON SPRINKLER SYSTEM.
9001 | NoData
9002 | NoData
9003 | NoData
9004 | NoData
9005 | NoData
9006 | NoData
9007 | NoData
9008 | NoData
9009 | NoData
9010 | Building owner/management company has a 72 hour notice to have a licensed fire sprinkler service company assess the deficiencies and the necessary corrective actions to make the fire suppression system operational.
9011 | Contact the office of emergency communications (OEC) when life safety systems are placed out of service.
9012 | Require a licensed automatic fire sprinkler service company.
9013 | Must be maintained and operational at all times.
9014 | NoData
9015 | NoData
9016 | NoData
9017 | NoData
9018 | NoData
9019 | REMOVE AUTOMOBILE PARTS STORAGE THAT IS LOCATED DIRECTLY IN FRONT OF ELECTRICAL PANEL.
9020 | NoData
9021 | NoData
9022 | NoData
9023 | NoData
9024 | NoData
9025 | NoData
9026 | The building has been vacated and is currently managed by Kin Properties. Mr. Brett Burstell will is managing the proper disposal of product left on site and ensuring all life safety equipment is maintain in operational readiness condition. Phone 561-988-2816Cell 561-239-4499bburstell@kinproperties.com
9027 | Per our conversation, all deficiencies must be restored
9028 | NoData
9029 | NoData
9030 | NoData
9031 | NoData
9032 | remove all trash and rubbish away from outside vehicles in parking area. that are in the back of truck
9033 | only (5) gallons of gasoline is allow in a metal approved gas can before a permit is needed. no class 1 flammable liquids are allow in plastic containers.
9034 | label all breakers and switches in the electrical panel
9035 | NoData
9036 | remove all excess waist use oil on top of (55) gallon containers and ground area, plus remove all other materials that are contaminated with oil which are on top of wait oil barrels.
9037 | All doors in the storage room area shall be properly identified in case of an emergency or fire with the following wordage ,office ,storage room, restroom exc.
9038 | remove all combustibles in front of electrical panel such as boxes paper, plastics exc
9039 | NoData
9040 | Your business location is not permitted to perform spray painting without a spray booth and a spraying/dipping permit. Cease all spray painting at this time.
9041 | Need to have a metal trash can with a metal lid for oily rags.
9042 | Need to remove the trash and clutter around the business, inside and out. Rubber, plastics, wood, garbage, and fabrics.
9043 | NoData
9044 | NoData
9045 | Fire extinguishers must be inspected annually.
9046 | NoData
9047 | Please renew Access Gate permit, expired 7/27/19.
9048 | NoData
9049 | NoData
9050 | RENEW P2 (ASSEMBLY PERMIT) THAT EXPIRED ON 1-28-21.
9051 | Please renew Access Gate and Key Box permits expired 1/29/20.
9052 | Provide Cover for 5th floor Electrical Room Junction Box. Provide Electrical Cover Plate for wall outlet inside Fire Command Room.
9053 | Provide mounting for Fire Extinguisher inside 6th floor Mechanical Room.
9054 | NoData
9055 | Provide Current Annual Inspection Tag for the Fire Sprinkler System. Provide Current (documented) Fire Pump Weekly Log for the respective address.
9056 | Provide Current Annual Inspection Tag for Fire Alarm System.
9057 | Replace missing/broken Cap on FDC connection.
9058 | Provide bright red paint for front entrance Key Box.
9059 | Provide 5-inch white numbers above front entrance doors.
9060 | Provide Current Emergency Contact List and Mobility Impaired List. Repair hole on Fire Depository Box.
9061 | Replace Ceiling Tile inside Fire Command Room. Repair Sheetrock Holes inside 3rd floor Mechanical Room above the door and 2nd floor Mechanical Room above the Air Compressor.
9062 | 1st floor Mechanical Room.
9063 | NoData
9064 | NoData
9065 | NoData
9066 | NoData
9067 | Gas cylinders must be secured. Attach chain to non-movable object in order to keep cylinders upright
9068 | NoData
9069 | 24" clearance must be maintained between ceiling and combustible materials (Non-sprinkled building)
9070 | NoData
9071 | All fire extinguishers must have current inspection tags.
9072 | Current audibility test required
9073 | NoData
9074 | Fire alarm is not operational, red tagged on 6/5/19 and currently no power to unit. 72 hour notice given.
9075 | Sprinkler requires annual testing
9076 | Current Sensitivity test required
9077 | Post the occupant load.
9078 | Renew the expired permit.
9079 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
9080 | GET ALARM SYSTEM INSPECTED.
9081 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES. KEEP PLANS UPDATED PER CODE AND TRAIN QUARTERLY.
9082 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
9083 | Please replace defective heat detector located in building 4.
9084 | NoData
9085 | Owner waiting on C.O.O in order to apply for hotworks permit.
9086 | NoData
9087 | NoData
9088 | Forklifts must have current fire extinguisher.
9089 | NoData
9090 | Address must be visible from the street.
9091 | Breaker box must be labeled.
9092 | Apply for hotworks permit.
9093 | Apply for oil storage permit.
9094 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
9095 | Work with building engineer to correct the top level re-entry per code.
9096 | Exit sign at the South West stairwell is not illuminated. Fix exit sign per code.
9097 | Fire extinguisher in kitchen (eco station 26) needs inspection per code.
9098 | This is a 72 hour notice to correct the red tag on the k extinguishing system in the kitchen per code.
9099 | Remove combustible storage from electric room per code.
9100 | Work with building engineer to correct the top level re-entry per code.
9101 | Remove items blocking access to the fire hose by the fire alarm panel per code.
9102 | Outlet cover missing, add outlet cover on electric outlet per code.
9103 | Return the following area to its fire resistance rating per code. Boiler room.
9104 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriateinspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualEmergency radio coverage- AnnualFire Extinguishers- AnnualDry pipe partial- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualDry pipe full- 3 YearFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearClean agent – Semi-annualKitchen Hood System- Semi-annualBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
9105 | Move the storage in front of the breaker boxes in the kitchen per code. Maintain proper clearance per code.
9106 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. • Present Permits that apply to facility Address listed • on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS.
9107 | Add occupancy side signage to the South West stairwell per code. Send layout to inspector for approval prior to printing.
9108 | NoData
9109 | The fork lift requires a fire extinguisher with a minimum rating of 10BC.
9110 | Remove obstructions in front of exits.
9111 | The spray booth suppression systems are past due for inspection.
9112 | Clear and maintain 3 feet of clearance around the spray booth.
9113 | Provide a "Falcon padlock" or a "Knox padlock" for the 911 key box.
9114 | Ensure all compressed gas cylinders are secured.
9115 | Provide protected storage for propane cylinder.
9116 | Remove propane cylinder from inside the shop. Outdoor storage is required.
9117 | Repair or replace the emergency illumination on the exit signs.
9118 | Exits are required to be unlocked while the building is occupied.
9119 | F7 (FLAMM/COMB STORAGE) PERMIT EXPIRED 2-16-21. CONTACT HOUSTON PERMITTING OFFICE TO RENEW.
9120 | NoData
9121 | Move the storage blocking direct access to the exit in the warehouse and maintain a clear path to all exits. Immediate compliance required.
9122 | Place a fire pump and electrical room sign on the outside of the doors leading into these rooms.Compliance by 3-5-2021
9123 | Remove the propane bottles not being used on forklifts and secure them outside the building.Compliance by 3-5-2021
9124 | All forklifts powered by propane, fuel, or diesel shall have a tagged mounted fire extinguisher.Compliance by 3-5-2021
9125 | Move large dumpster a minimum of 10 feet from the building and the smaller dumpster a minimum of 5 feet from the building.Compliance by 3-5-2021
9126 | NoData
9127 | NoData
9128 | NoData
9129 | Fire extinguishers with a minimum rating of 2A:10BC are required in the business.
9130 | Remove tables blocking the second exit.
9131 | A propane permit is required for cooking. Obtain the permit or remove the propane tank located in the rear of the property.
9132 | All exits are required to be unlocked while the building is occupied.
9133 | Remove old untagged extinguishers from the property.
9134 | The Vent hoods require professional cleaning. Ensure stickers with the date of cleaning are placed on the vent hoods.
9135 | Discontinue the use of "piggyback" extension cords in the kitchen area.
9136 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
9137 | Repair the main entrance door to ensure all doors swing in direction of egress.
9138 | Repair or replace the inoperable emergency illumination.
9139 | Post the occupant load (98).
9140 | NoData
9141 | ENSURE SELF CLOSING OILY RAG CAN IS MAINTAINED IN EACH ELEVATOR CONTROL ROOM AND IS EMPTIED AFTER EACH WORK DAY
9142 | NoData
9143 | NoData
9144 | UPDATE ELEVATOR MATRIX, BUILDING CONTACTS, MOBILITY IMPAIRED LIST
9145 | NoData
9146 | MAINTAIN 2 HOISTWAY DOOR TOOLS
9147 | PLACE INDEPENDENT SERVICE KEYS IN FCC BUT OUTSIDE THE FIRE DEPOSITORY BOX
9148 | INSTALL SIGNS FOR CONTROL/ELECTRIC/MECHANICAL ROOMS THAT ARE NOT PROPERLY INDICATED
9149 | NoData
9150 | NoData
9151 | ENSURE ALL OPEN ELECTRIC/JUNCTION BOXES/PANELS ARE PROPERLY COVERED/ENCLOSED
9152 | ENSURE ACCESS TO FIREFIGHTER PHONES AND VERIFY OPERATION
9153 | ENSURE ROOF TOP STANDPIPE TEST CONNECTION HAS SIGNAGE
9154 | INSTALL ELEVATOR CAR NUMBERS WHERE MISSING
9155 | MAINTAIN APPROPRIATE NUMBER OF LOCK OUT DEVICES IN ELEVATOR CONTROL ROOMS
9156 | VERIFY STAIRWAY SIGNS ARE PRESENT AND CORRECT
9157 | NoData
9158 | NoData
9159 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
9160 | GET ALARM SYSTEM INSPECTED.
9161 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES. KEEP PLANS UPDATED PER CODE AND TRAIN QUARTERLY.
9162 | NoData
9163 | NoData
9164 | NoData
9165 | NoData
9166 | Correct violations to avoid re-inspection fees and/or citations.
9167 | Correct CLS Yellow Tag 9/9/2019 on Fire Alarm System. (Also on IR# 258620) Note: The Fire Alarm Panel was in trouble mode and then I witnessed it change to All Systems Normal. Pics included.
9168 | NoData
9169 | NoData
9170 | ALL VERTICAL ROLLING FIRE DOORS SHALL BE INSPECTED ANNUALLY BY A LICENSED COMPANY.COMPLIANCE: 30 CALENDAR DAYS.
9171 | ALL LPG CAGES SHALL BE STORED OUTSIDE10 FT AWAY FROM BUILDING.COMPLIANCE: 30 CALENDAR DAYS.
9172 | AN ANNUAL INSPECTION SHALL BE DONE ON FIRE ALARM PANEL BY A LICENSED COMPANY.AN SEMI ANNUAL INSPECTION ISSHALL BEMAINTAINED ON FIRE SUPPRESSION SYSTEM FOR BUILDING A.AN ANNUAL INSPECTION SHALL BE DONE ON THE IN RACK SPRINKLER SYSTEM INSIDE OF MAIN WAREHOUSE.
9173 | ALL PERMITS REQUIRED FOR FACILITY TO OPERATE SHALL BE POSTED OR READY FOR REVIEW.MISSING H2(HIGH PILED ), H1( HAZARDOUS MATERIAL )COMPLIANCE: 30 CALENDAR DAYS.
9174 | ALL PERMITS REQUIRED FOR FACILITY TO OPERATE SHALL BE POSTED OR READY FOR REVIEW.MISSING H2(HIGH PILED ), H1( HAZARDOUS MATERIAL )COMPLIANCE: 30 CALENDAR DAYS.
9175 | NoData
9176 | NoData
9177 | NoData
9178 | NoData
9179 | Please have a flow test done on all 6 private hydrants excluding both City of Houston hydrants located on North side complex.
9180 | Please remove all debris (sofas, old mattresses, trash) located behind and near dumpsters.
9181 | LPG containers not allowed on property.
9182 | Please repair all micro switches located inside 911 boxes and place inside a master lock key that opens padlock on manual gates.
9183 | Please identify all electrical switches with proper unit numbers.
9184 | Please visually inspect all draft stops for solid construction & repair all damaged areas.
9185 | Blue reflector is required to identify all 9 hydrant locations on property. 6 - private hydrants3 - city hydrants
9186 | please verify all sleeping units are furnished with a working smoke alarm including egress pathway from apartment unit.
9187 | Please provide a valid access gate permit for Tradewinds Apts.
9188 | Please provide a valid key box permit for Tradewinds Apts.
9189 | Please repair all damaged 911 boxes including micro switches and failsafe pull boxes.
9190 | Please have annual test done on both systems
9191 | Please have annual test done on both systems
9192 | NoData
9193 | IT IS THE BUSINESS OWNER OR BUILDING OCCUPANTS RESPONSIBILITY TO ADDRESS ALL MATTERS NOTED IN THIS REPORT
9194 | NoData
9195 | PROVIDE EMPLOYEE TRAINING PER ABOVE NOTED FIRE CODE
9196 | PROVIDE SDS'S FOR ALL HAZARDOUS SUBSTANCES STORED/USED ON PROPERTY
9197 | DESIGNATE PERSON(S) IN APPROPRIATE MITIGATING ACTIONS NECESSARY FOR FLAMMABLE LIQUIDS SPILLS, LEAKS OR FIRES PER ABOVE FIRE CODE
9198 | KEYS IN KEYBOXES DID NOT ALLOW ACCESS TO BUILDING AS REQUIRED PER ABOVE FIRE CODE - PROVIDE KEYS TO FIRE CODE OFFICIAL SO THAT THEY MAY BE PLACED IN KEYBOX FOR EMERGENCY ACCESS FOR FIRST RESPONDERS
9199 | NoData
9200 | Repair or replace the inoperable emergency illumination on the exit signs.
9201 | Ensure locking bars are removed from the exits while the building is occupied.
9202 | Remove obstructions in front of exits.
9203 | NoData
9204 | NoData
9205 | NoData
9206 | NoData
9207 | NoData
9208 | NoData
9209 | NoData
9210 | Several fire extinguishers are missing inspection tags. Fire extinguishers are required to have an inspection tag with date of service. Repair or replace the red tagged fire extinguisher.
9211 | NoData
9212 | NoData
9213 | NoData
9214 | NoData
9215 | NoData
9216 | No C of O.
9217 | NoData
9218 | No C of O.
9219 | NoData
9220 | NoData
9221 | COMPLIANCE DATE: 30 CALENDR DAYS
9222 | SERVICE AND MOUNT ALL FIRE EXTINGUISHERS
9223 | Secure O2 compressed gas cylinders according to this code.
9224 | Secure O2 compressed gas cylinders according to this code.
9225 | REPLACE ALL DAMAGED OR MISSING CEILING TILES.
9226 | NoData
9227 | NoData
9228 | NoData
9229 | NoData
9230 | NoData
9231 | NoData
9232 | NoData
9233 | NO VIOLATIONS found at the time of inspection.
9234 | Please have fire extinguishers serviced.
9235 | RE-NEW "PUBLIC ASSEMBLY" permit within 10 business days, by 10/18/13
9236 | NoData
9237 | NoData
9238 | NoData
9239 | NoData
9240 | NoData
9241 | INFORMATION
9242 | INFORMATION
9243 | INFORMATION
9244 | LAST ANNUAL FIRE ALARM TEST---2-19-20BRING UP TO CODE
9245 | LAST EMERGENCY LIGHTING TEST FOUND IN FIRE MARSHAL BINDER --10-14-16
9246 | UPDATE THE MOST RECENT PERMITS AND PLACE IN FIRE MARSHAL BINDER
9247 | K1 permit expired
9248 | NoData
9249 | NoData
9250 | NoData
9251 | NoData
9252 | NoData
9253 | NoData
9254 | The fire alarm control unit was found to have a yellow tag attached. Contact a licensed fire protection to correct the violations and ensure a current service tag reflecting the corrections made is attached.
9255 | NoData
9256 | Provide annual test and service tag for fire alarm system.
9257 | Provide documentation/report for emergency lighting system testing and all necessary repairs.
9258 | Provide annual inspection and service tag of fire extinguishers.
9259 | Correct trouble alert on fire alarm system.
9260 | Provide Fire Alarm Permit
9261 | Maintain minimum ceiling in water heater room.
9262 | Three perimeter exit signs need repair.
9263 | The permit amount for oxidizing gas is &gt;504 cu. ft. on site. With 4 "H" bottles (2 oxygen, 2 nitrous) on site of min. 240 cu. ft. each, a C7: Compressed Gas annual operational permit must be obtained and posted on site(this is not a construction permit, but an operational permit that is required to be held by the occupant/business). Permits may be obtained at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811www.houstonpermittingcenter.orgCompliance is required within 2 weeks: 3/19/2021
9264 | NoData
9265 | NoData
9266 | NoData
9267 | NoData
9268 | NoData
9269 | Provide annual test and service tag for fire alarm system.
9270 | Provide documentation/report for emergency lighting system testing and all necessary repairs.
9271 | Provide Fire Alarm Permit.
9272 | NoData
9273 | NoData
9274 | Maintain minimum ceiling in water heater room.
9275 | Three perimeter exit signs need repair.
9276 | Provide annual test and service tag for fire alarm system.
9277 | Correct Trouble alert on fire alarm system.
9278 | NoData
9279 | NoData
9280 | NoData
9281 | The following annual operational permits shall be obtained and posted on site within 2 weeks:-P2: Public Assembly (101-299 occupants)-Fire Alarm PermitPermits are available at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811 www.houstonpermittingcenter.org
9282 | NoData
9283 | Remove all combustible items inside this room
9284 | NoData
9285 | Remove all combustibles from room.
9286 | Alarm Panel must be keep free from any objects or picture covering in order to hide the view of the fire alarm panel. Picture must be removed.
9287 | All doors inside class room must be kept in its original use. It appears that the glass window was removed from theses doors. I am asking for the City of Houston approved plans identifying that these doors were installed without the protective glass window.
9288 | NoData
9289 | NoData
9290 | door must open freely and not be stuck when using panic hardware. Door must be corrected within 24 hrs.
9291 | Blocked Exit door must be corrected within 24 hrs.
9292 | All emergency exit doors must open, close and latch on its own. Panic hardware must not have more than 5 lb. of pressure when opening.
9293 | Fail to correct fire code violations by compliance date. Reinspect must be paid and follow up in 30 days from this date 3/5/2021
9294 | All extra tables and chairs must be remove from room and cleared from exit door.
9295 | The fire alarm and sprinkler systems are due for an annual inspection. Have both systems inspected to achieve compliance.Sprinkler system in building 2 and 11 have no water pressure due to pipe rupture from inclement weather.A 24 hrs. 7 days a week inhouse firewatch is required until both systems are back in compliance.
9296 | NoData
9297 | NoData
9298 | NoData
9299 | Retag fire extinguisher in electrical/ mechanical room.
9300 | Install fail-safe on access gate.
9301 | Install knox-box on gates.
9302 | Replace cover on junction box.
9303 | Cover opening in electrical room with fire resistant caulking.
9304 | Place knox box on access gates.
9305 | NoData
9306 | NoData
9307 | NoData
9308 | NoData
9309 | NoData
9310 | NoData
9311 | NoData
9312 | ALL FIRE EXTINGUISHERS SHALL HAVE A CURRENT ANNUAL INSPECTION TAG BY AN APPROVED LICENSED FIRE PROTECTION EQUIPMENT COMPANY. COMPLIANCE WITHIN 30 DAYS.
9313 | Make sure that the LPG storage cabinet is locked and secured.Compliance within 30 days.
9314 | An annual and quarterly test of the fire suppression system must be performed and all deficiencies must be repaired or replaced. Approved tags must be affixed to the riser to indicating that the system is in operational readiness.Compliance within 30 days.
9315 | Fire alarm must tested and serviced annually by a licensed fire protection vendor.Compliance within 30 days.
9316 | A 5 year hydrostatic test must be performed on the suppression system. I was unable to find the 5 year tag with the most recent hydrostatic test performed within the past 5 years.Compliance within 30 days.
9317 | Aisle clearance and width must been maintained to for egress continuity.Compliance within 30 days.
9318 | Keys to give HFD access to the building must be placed in the 911 key box. During the follow up visit in 30 days, the keys will be tested and placed in key box.Compliance within 30 days.
9319 | NoData
9320 | NoData
9321 | NoData
9322 | NoData
9323 | NoData
9324 | NoData
9325 | NoData
9326 | NoData
9327 | NoData
9328 | NoData
9329 | no violations found
9330 | NoData
9331 | NoData
9332 | NoData
9333 | NoData
9334 | NoData
9335 | NoData
9336 | NoData
9337 | NoData
9338 | Coverage inspection passed for buildings 1-A and 1-B for all levels. Standpipe inspection also passed for all levels. The sprinkler permit is final.
9339 | NoData
9340 | NoData
9341 | NoData
9342 | NoData
9343 | NoData
9344 | NoData
9345 | NoData
9346 | Mech/Electrical Rm needs to have combustibles materials and storage removed from area.
9347 | NoData
9348 | All emergency exit lights need to be tested and results need to be place in separate tab inside FMB.
9349 | Up to date Damper Test documentation required and entered into FMB
9350 | Expired service tag needs to be updated.
9351 | Remove any storage above the required distance of the sprinkler heads.
9352 | Remove all combustible storage from all Elec/Mech rooms.
9353 | A Knox box is required all at points of entry to the property where apparatus access maybe used.
9354 | At no time should exit doors be keep open by any means or use of a wedge, locking device. Fire doors must remain in the closed position at all times.
9355 | Last 12 months of updated records must be tabbed and entered into FMB
9356 | Replace very small evac rt. placard with a minimum size 8.5x11and follow the requirements in my attachment that I included in my email.
9357 | Required amount of drills obstructed and unobstructed for the last 12 mo. must be entered into the FMB
9358 | NoData
9359 | Access Gate Permit required. A key type pad lock must be used to secure the gate chain. At no time should a combination lock be used.
9360 | NoData
9361 | Key Box permit required. Upon installation of new boxes, pad locks keys need to be placed into the new Knox box. A follow up from the Fire Marshalls Office will be required to open the box.
9362 | Exit doors need to have panic hardware installed.
9363 | All required current permits and certificate of occupancy for the school and early learning center must be entered into the FMB and tabbed accordingly per example in my email attachment.
9364 | Remove outdoor benches from area that our blocking the opening of the exit doors. Remove small teacher desk blocking exit pathway.
9365 | NoData
9366 | NoData
9367 | NoData
9368 | NoData
9369 | NoData
9370 | NoData
9371 | NoData
9372 | NoData
9373 | NoData
9374 | NoData
9375 | NoData
9376 | NoData
9377 | NoData
9378 | NoData
9379 | NoData
9380 | NoData
9381 | NoData
9382 | NoData
9383 | NoData
9384 | NoData
9385 | NoData
9386 | NoData
9387 | NoData
9388 | NoData
9389 | NoData
9390 | NoData
9391 | NoData
9392 | NoData
9393 | NoData
9394 | NoData
9395 | NoData
9396 | NoData
9397 | NoData
9398 | NoData
9399 | NoData
9400 | NoData
9401 | NoData
9402 | NoData
9403 | NoData
9404 | NoData
9405 | NoData
9406 | NoData
9407 | NoData
9408 | NoData
9409 | NoData
9410 | NoData
9411 | NoData
9412 | NoData
9413 | NoData
9414 | NoData
9415 | NoData
9416 | NoData
9417 | NoData
9418 | NoData
9419 | NoData
9420 | NoData
9421 | NoData
9422 | NoData
9423 | NoData
9424 | NoData
9425 | NoData
9426 | NoData
9427 | NoData
9428 | NoData
9429 | NoData
9430 | NoData
9431 | NoData
9432 | NoData
9433 | NoData
9434 | NoData
9435 | NoData
9436 | NoData
9437 | NoData
9438 | NoData
9439 | NoData
9440 | NoData
9441 | See above, per our conversation you need to maintain the extinguishers on a annual basis ( the current extinguisher has no tag and we need a receipt to prove the date)
9442 | See above-provide the following for welding.3-4-2021 per owner, not using a welding/torch in the facility.
9443 | See above, per our conversation, apply for the F7( storage of flammable/combustible liquid) and the H3 permit (welding)3-4-2021 Per owner- they will not need the permits because they removed all storage of flammable and welding equipment.
9444 | NoData
9445 | NoData
9446 | NoData
9447 | NoData
9448 | NoData
9449 | NoData
9450 | NoData
9451 | NoData
9452 | NoData
9453 | NoData
9454 | NoData
9455 | NoData
9456 | NoData
9457 | NoData
9458 | NoData
9459 | NoData
9460 | I spoke with the Manager Jennifer Aguirre about the status of the fire alarm , sprinkler system and running water. Ms. Aguirre states that every apartment unit had smoke detectors and running water. The apartment community does not have a sprinkler system.
9461 | NoData
9462 | NoData
9463 | NoData
9464 | NoData
9465 | NoData
9466 | NEED SERVICE. HAS TROUBLE LIGHT ON. 9-18-2019 LAST DATE
9467 | NEED SERVICE . 12-2019 LAST DATE
9468 | NoData
9469 | NEED SERVICE. 8-2018 LAST DATE
9470 | FAILURE TO GET THE FIRE EXTINGUISHERS SERVICE. 8-18 LAST DATE
9471 | NoData
9472 | #NAME?
9473 | #NAME?
9474 | #NAME?
9475 | #NAME?
9476 | NoData
9477 | NoData
9478 | NoData
9479 | NoData
9480 | NoData
9481 | NoData
9482 | NoData
9483 | NoData
9484 | NoData
9485 | NoData
9486 | NoData
9487 | NoData
9488 | NoData
9489 | NoData
9490 | NoData
9491 | NoData
9492 | NoData
9493 | NoData
9494 | NoData
9495 | NoData
9496 | NoData
9497 | NoData
9498 | NoData
9499 | NoData
9500 | NoData
9501 | NoData
9502 | NoData
9503 | NoData
9504 | NoData
9505 | NoData
9506 | NEED TO BE SERVICE 5-18 LAST DATE
9507 | NEED SERVICE 3-19 LAST DATE
9508 | FAILURE TO SERVICE SPRINKLER SYSTEM 5-18 AND FIRE EXTINGUISHERS 3-19
9509 | NoData
9510 | NoData
9511 | NoData
9512 | NoData
9513 | NoData
9514 | NoData
9515 | NoData
9516 | NoData
9517 | NoData
9518 | NoData
9519 | NoData
9520 | NoData
9521 | NoData
9522 | NoData
9523 | NoData
9524 | NoData
9525 | NoData
9526 | NoData
9527 | NoData
9528 | NoData
9529 | NoData
9530 | NoData
9531 | NoData
9532 | NoData
9533 | NoData
9534 | NoData
9535 | Repair the fire alarm panel.
9536 | Correct the yellow tag deficiencies on the fire sprinkler system.
9537 | Replace the missing breaker cover on the breaker panel located in the pool service closet.
9538 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
9539 | last annual tag 10/26/2019; multiple service tags placed on panel not organized
9540 | NoData
9541 | NoData
9542 | last annual inspection 2/2019;monthly inspections not being completed
9543 | fire lane signs and curb markings faded
9544 | NoData
9545 | NoData
9546 | NoData
9547 | FIRE PANEL NEED TO BE SERVICE TO FIX THE YELLOW TAG 11-6-20 LAST DATE
9548 | NEED TO BE SERVICE AND NEED TO FIX YELLOW TAG 3-6-20
9549 | NEED TO BE SERVICE 6-19 LAST DATE
9550 | NEED TO BE SERVICE 8-20 LAST DATE
9551 | Renew the public assembly permit.
9552 | NoData
9553 | NoData
9554 | The vent hood suppression system is due for service before the end of 03/2021.
9555 | Fire extinguishers are due for annual service before the end of 03/2021.
9556 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
9557 | Owner's responsibility. Comply with the above fire code.
9558 | The fire alarm panel has an yellow tag attached for 4300 and 4310 Dunlavy. Have fire alarm system serviced to achieve compliant status. Sprinkler system shows to be compliant at this time.
9559 | NoData
9560 | NoData
9561 | NoData
9562 | ENSURE FIRE ALARM SYSTEM IS INSPECTED ANNUALLY.
9563 | ENSURE ALL EMERGENCY LIGHTS ARE OPERATING PROPERLY.
9564 | #NAME?
9565 | POST ADDRESS NUMBERS ON THE FRONT OF THE BUSINESS. NUMBERS ARE REQUIRED TO BE A MINIMUM OF 4 INCHES IN HEIGHT AND PLACED ON A CONTRASTING BACKGROUND.
9566 | -ENSURE ALL EXITS ARE UNLOCKED WHILE THE BUILDING IS OCCUPIED. -PLACE STICKERS ON EXIT DOORS STATING: "THIS DOOR TO REMAIN UNLOCKED WHEN THE BUILDING IS OCCUPIED".
9567 | OBTAIN AND POST AN ASSEMBLY PERMIT. REQUIRED FOR OCCUPANT LOADS GREATER THAN 49.
9568 | CLEAR AND MAINTAIN 36 INCHES IN FRONT OF BREAKER PANELS.
9569 | DISCONTINUE THE USE OF EXTENSION CORDS AS A PERMANENT SOURCE OF WIRING.
9570 | REMOVE STORAGE IN FRONT OF EXIT PATH.
9571 | Remove curtain blocking exit.
9572 | OBTAIN AND MOUNT AT LEAST 2 FIRE EXTINGUISHERS WITH A MINIMUM RATING OF 2A:10BC TO ENSURE THERE'S AN EXTINGUISHER WITHIN 75 FEET OF UNOBSTRUCTED TRAVEL DISTANCE.
9573 | NoData
9574 | REPLACE MISSING OUTLET AND SWITCH COVERS.
9575 | MOUNT THE FIRE EXTINGUISHERS ACCORDING TO THE CODE LISTED ABOVE.
9576 | REPAIR OR REPLACE THE EMERGENCY ILLUMINATION ON THE EXIT SIGNS AS WELL AS THE STAND ALONE EMERGENCY LIGHTING TO ENSURE IT IS FULLY OPERATIONAL.
9577 | NoData
9578 | NoData
9579 | NoData
9580 | You can use any of the listed exit signs of the fire code, as long as they are illuminated at all times, but they must be UL924 rated.
9581 | Remove the items blocking the exit door on the north side of the factory floor.
9582 | Owner/occupant is responsible for correcting all fire code violations and obtaining any necessary Certificates. The owner/occupant must obtain a Certificate of Occupancy through the Building Department located at 1002 Washington Avenue. Phone number for Occupancy is 832-394-8800. Phone number for Houston Permitting Center is 832-394-9000.
9583 | Must place address numbers to the front of the business that are minimum 4 inches tall and at least a 1/2 inch wide numbers.
9584 | Replace missing switch plate. Place cover on the electrical panel and cover open breakers with metal or plastic spacers.
9585 | Move portable fire extinguishers that are being obstructed or move the obstruction.
9586 | Place "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED" on this inside of the door. This reminds the employees to unlock the doors when the building is occupied.
9587 | Must be internally or externally illuminated.
9588 | NO VIOLATIONS FOUND UPON INSPECTION OF: MONTESSORI COUNTRY DAY SCHOOL3/8/2021.
9589 | INFORMATION ONLY
9590 | NoData
9591 | Approved no violations found.
9592 | Fire Sprinklers are out of service. Fire alarm is in alarm and supervisory mode. Continue with self-fire watch until the fire alarm and fire sprinkles are back in regular service.Complete and return the fire watch agreement prior to COB today.
9593 | Fire Alarm Red Tagged Impaired72 Hour Notice IssuedSelf Fire Watch initiated 2-22-21
9594 | NoData
9595 | NoData
9596 | OBTAIN AND POST THE FOLLOWING PERMITS: -GATE PERMIT (A4) -911 KEYBOX PERMIT (K1)
9597 | H1 (HAZARDOUS MATERIALS) PERMIT EXPIRED 1-12-21. RENEW PERMIT WITHIN 10 BUSINESS DAYS
9598 | NoData
9599 | NoData
9600 | Fire Alarm is Red Tagged ImpairedFire Sprinkler System is out of service.Maintain Self Fire-watch until systems are back in regular service.
9601 | NoData
9602 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
9603 | No violations noted at this time.
9604 | no violations found at this time;fire alarm 1/20/2021; fire extinguisher 1/2021
9605 | NoData
9606 | Have a licensed fire protection company repair the red tagged alarm panel and correct any deficiencies.
9607 | NoData
9608 | Nonrequired fire protection systems shall be maintained or removed.
9609 | The exceptions listed in the IFC2012.903.2 must be met in order to be considered nonrequired.
9610 | NoData
9611 | NoData
9612 | NoData
9613 | NoData
9614 | NoData
9615 | NoData
9616 | NoData
9617 | NoData
9618 | NoData
9619 | Exit sign broken in front door
9620 | Labels missing on fuses in electrical box in electrical room
9621 | Tenant is using BBQ pit on balcony
9622 | Building over capacity
9623 | NoData
9624 | Please keep this path clear moving forward.
9625 | your occupancy is under 50 so its not required however I always recommend a panic hardware device so that the concern of being trapped behind the key lock never happens.
9626 | Do not block door with tables or chairs.
9627 | Good Job, what was found was correct while on location. Keep up the good work!!
9628 | NoData
9629 | NoData
9630 | NoData
9631 | NoData
9632 | NoData
9633 | NoData
9634 | NoData
9635 | NoData
9636 | NoData
9637 | NoData
9638 | Carlos Mejea
9639 | See above for the storage of tires.
9640 | See above for the Fire extinguishers (all of the current extinguishers are out of date) 2-2016
9641 | Apply for the (F7) permit with the permitting office.
9642 | NoData
9643 | NoData
9644 | NoData
9645 | NoData
9646 | NoData
9647 | NoData
9648 | 5 YEAR STAIRWELL PRESSURIZATION TEST IS DUE
9649 | 4yr DAMPER INSPECTION IS DUE
9650 | 5 YEAR NATURAL GAS TEST IS DUE
9651 | NoData
9652 | LAST ANNUAL INSPECTION ON SPRINKLER RISER---- 8-21-2019
9653 | FIRE ALARM PERMIT EXPIRED--9-9-2020
9654 | A4-ACCESS GATE PERMIT EXPIRED --1-17-2021
9655 | K1-911 BOX PERMIT EXPIRED----1-17-2021
9656 | FIRE ALARM PERMIT EXPIRED--9-9-2020
9657 | PLACE NEW PERMITS INSIDE THE FIRE MARSHAL BINDER
9658 | FIRE ALARM PERMIT EXPIRED--9-9-2020
9659 | FIRE ALARM PERMIT EXPIRED--9-9-2020
9660 | ENSURE ALL FIRE DETECTION EQUIPMENT, FIRE SUPPRESSIONEQUIPMENT, ELEVATORS, ETC ARE INSPECTED PER ESTABLISHED INTERVALS ANDDOCUMENTED - ALL DOCUMENTATION SHOULD BE POSTED OR ORGANIZED AND KEPT ON SITEFOR FIRE MARSHAL INSPECTION
9661 | THE SPRINKLER SYSTEM IS RED TAGGED - A RED TAG WAS ISSUED IN 02/17/21 AND MUST BE INSPECTED AND SERVICED OR REPAIRED IMMEDIATELY REPAIRS ARE INDICATED ON THE FIRE ALARM BUT THE FIRE ALARM PANEL READS "OFF - NORMAL" AND THE SUPERVISORY LIGHT IS ILLUMINATED; REPAIR THE FIRE ALARM PANEL AND REMOVE IT FROM SUPERVISORY MODE
9662 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS PANEL READS SUPERVISORY MODE THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS
9663 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
9664 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTIONFEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90DAYS
9665 | NoData
9666 | Current permits: F7, M3, H3 M3 not needed. Inspector will cancel Lower quantity of acetylene on hand to 200 cu. ft. or less, or obtain C7 (compressed flammable gas) permit
9667 | Working with building dept
9668 | Discontinue use of plastic fuel cans. Replace plastic cans with metal safety cans with self-closing lids.
9669 | Tim Garcia Fernando Hernandez
9670 | Ensure all extinguishers have tags that show inspection by licensed company within the past year.
9671 | Ensure that fire extinguishers are mounted on all dirt moving equipment (including John Deere tractor).
9672 | Once verified during occupancy inspection, clearly post address numbers and building letter designations, if applicable.
9673 | H3 permit expired 2/21/2021
9674 | The 5 year hydrostatic flow test must be completed and passed. Any deficiencies must be corrected.(Compliance in 30 days)
9675 | The required 5 year test must be completed on the water storage tank. Any deficiencies must be corrected.(Compliance in 30 days)
9676 | Ensure that when restocking aisles, product is placed on one side of the aisle before placing in the racks and access is maintained as required by code.
9677 | The required mechanical ventilation failed the "paper test" and requires service. They system must run continuously as required by code. Have all deficiencies corrected and ensure proper ventilation is maintained.(Compliance within 30 days)
9678 | An HMIS must be completed for each control area in the facility in the format provided with this notice.(Compliance in 30 days)
9679 | Ensure separation of incompatible materials is sufficient and all hazardous chemicals are stored as required by approved plans.
9680 | 8/2020 - OK
9681 | 7/23/2020 - REDCorrected 10/8/2020 - OK
9682 | 8/6/2020 - YELLOWCorrected 11/5/2020 - OK
9683 | 1/23/2017 - Blue, OK
9684 | 12/2020 - OK
9685 | 8/31/2020 - OK
9686 | 7/16/2019 - OK
9687 | Obstructed drills OK
9688 | Monthly drills conducted. Log OK.
9689 | 4/26/2018 - OK
9690 | 7/17/2020 - OK
9691 | Correct all violations within 60 calendar days.
9692 | 5/18/2017 - Have audibility test performed and correct deficiencies.
9693 | 2/28/2020 - Have current load bank performed and provide report.
9694 | Have all private hydrants flow tested and provide report.
9695 | Repair all non-working sliding fire doors and provide report. Doors must have stickers stating the date of test.
9696 | Permit expired 3/31/2020 - Update expired elevator permit.
9697 | NoData
9698 | NoData
9699 | NoData
9700 | NoData
9701 | Last inspection 8/2020, but extinguisher in daycare shows low charge. Charge/replace extinguisher.
9702 | Correct all violations within 30 calendar days.
9703 | 8/11/2020 - YELLOWYellow tag conditions from 2019 were not corrected and were carried over to the 2020 sprinkler inspection. As this was listed as a violation on last year's inspection report for this facility, failure to correct yellow tag within 30 days will result in citations being issued.Corrected 1/8/2021 - OK
9704 | Have sensitivity test performed and provide documentation that any deficiencies were corrected.Automatic, internal sensitivity testing. Panel is clear.
9705 | NoData
9706 | NoData
9707 | NoData
9708 | NoData
9709 | NoData
9710 | NoData
9711 | NoData
9712 | Please provide compliance letters for all life safety inspections
9713 | Level A needs to be inspected last done 2019.Level F is missing extinguisher.
9714 | Adjust closer so door latches
9715 | Update building information and mobility impairment list every 6 months. Legend Card is needed
9716 | This is a re-entry floor.Stairwell signage needs to reflect what the door does for entry. If door states no re-entry the the door should be locked
9717 | This is a re-entry floor,Floors 3-7 must meet the requirements of Code word 971, Required re-entry doors, on at least every fifth floor, which are locked from the stairway side, shall have the capability of being unlocked without unlatching upon a signal from an approved location (see Section 1005.3.2.4 of the Fire Code) and be subordinate to the fire alarm. The re-entry requirement shall provide that the first floor and the top floor be required to be unlocked in every multi-story building-Example: A nine story building shall be required to have re-entry on the first, fifth, and ninth floors. An eleven story building shall have re-entry on the first, fifth, tenth and eleventh floors.
9718 | NoData
9719 | NoData
9720 | NoData
9721 | 8/2020 - OK
9722 | No violations found.
9723 | 4/24/2020 - Blue, OK
9724 | New installation 3/15/2019. Not due for audibility until 3/15/2022.
9725 | 8/14/2020 - YellowCorrected 1/8/2021 - OK
9726 | 10/28/2018 - Blue, OK
9727 | 9/2020 - OK at time of inspection, but due this month.
9728 | 8/2020 - OK
9729 | 4/22/2020 - OK
9730 | Obstructed drills OK.
9731 | Monthly drills conducted. Log OK
9732 | Smart panel. 24/7 sensitivity monitoring.
9733 | 6/19/2020 - OK
9734 | This location is required to have one (1) fire extinguisher with a minimum rating of 2:A 10:BC. The extinguisher should be mounted with the top being no higher than 5 feet off the ground, the bottom at least 4 inches off the ground, and positioned in such a way that it is easily accessible, readily visible, and not subject to damage. No point inside the occupancy should be greater than 75 feet from an extinguisher.
9735 | Provide address numbers on the front of the exterior of the building that at a minimum of 4 inches tall, 0.5 inches wide in stroke width, easily visible from the street, and that contrast in color with their background.
9736 | Ensure all fire extinguishers have a annual acceptable service tag from a licensed fire protection company.
9737 | Systems or devices that are permanently out of service or any non-required life safety system or fire protection system that no longer functions as originally installed shall be removed or the appearance changed so as not to be mistaken for functioning life safety or fire protection equipment.
9738 | Ensure all exit signs are properly illuminated under battery back up power.
9739 | NoData
9740 | a4 permit expired 10/1/2020
9741 | Need to have all the exit signs and emergency lighting tested and repaired if necessary. During the initial inspection, we found at least two exit signs/emergency lights in the rear of the restaurant that needed repairs or replacement.
9742 | It is the owner/occupants responsibility to correct all violations prior to the follow up inspection.
9743 | Need to make sure that the space adjacent to the electrical panels is clear of combustible materials according to the specifications above.
9744 | Need to hire a licensed sprinkler inspection company to inspect and tag the sprinkler system and make any repairs if necessary prior to follow up inspection. Inspected March 9, 2020, but system is yellow tagged. Needs to be serviced.
9745 | I have provided the contact information and address to the Houston Permitting Center in this report. A duplicate copy of the Certificate of Occupancy can be acquired at this location. Also need to obtain a copy of the Public Assembly(P2) permit from the Houston Permitting Center.
9746 | Need to have the class K(silver) fire extinguisher inspected and tag by a licensed fire equipment and inspection company.
9747 | Need to hire a licensed plumber to perform a 5 year gas test prior to the follow up inspection and make any repairs if necessary.
9748 | Need to have the two(2) ANSUL fire suppression systems inspected and tagged. If any repairs are necessary, they need to be completed prior to the follow up inspection.
9749 | Once the occupancy is determined, need to post the occupant load according to the code above.
9750 | The Places of Assembly permit needs to be obtained and posted in the business.
9751 | Need to hire a licensed fire equipment and inspection company to inspect and tag all portable fire extinguishers.
9752 | Need to display the building address above the double doors along the East Freeway side.
9753 | The licensed plumber must obtain a gas test permit from the City of Houston Permitting Center located at 1002 Washington Avenue prior to performing the required gas test.
9754 | Need to hire a licensed sprinkler inspection company to inspect and tag the sprinkler system and make any repairs if necessary prior to follow up inspection. Inspected March 9, 2020, but system is yellow tagged. Needs to be serviced.
9755 | The licensed plumber must obtain a gas test permit from the City of Houston Permitting Center located at 1002 Washington Avenue prior to performing the required gas test.
9756 | I have provided the contact information and address to the Houston Permitting Center in this report. A duplicate copy of the Certificate of Occupancy can be acquired at this location. Also need to obtain a copy of the Public Assembly(P2) permit from the Houston Permitting Center.
9757 | Once the occupancy is determined, need to post the occupant load according to the code above.
9758 | Need to hire a licensed plumber to perform a 5 year gas test prior to the follow up inspection and make any repairs if necessary.
9759 | 9/2020 - OK
9760 | 1/20/2021 - Blue, OK
9761 | New installation 8/19/2019. Audibility not due until 8/19/2022.
9762 | 8/6/2020 - YellowCorrected 11/5/2020 - OK
9763 | 7/15/2020 - Blue, OK
9764 | 8/2020 - OK
9765 | 4/21/2020 - OK
9766 | Obstructed drills OK.
9767 | Monthly drills conducted. Log OK.
9768 | Smart panel. 24/7 sensitivity monitoring. Panel clear.
9769 | 6/19/2020 - OK
9770 | Add two portable fire extinguishers to each gym (4 total extinguishers.)
9771 | Correct all violations within 60 calendar days.
9772 | One hose cabinet in gym last inspected 12/2019. Have hose valve inspected.
9773 | 8/2020 - Have ANSUL system inspected.
9774 | One boiler permit expired 7/10/2020Update expired permit or verify that boiler was removed.
9775 | Exit sign inside main office "man trap" is above an egress-controlled door. Relocate sign or remove egress control mechanism.
9776 | NoData
9777 | NoData
9778 | Extinguisher in Bldg. E last inspected 8/2018. Have extinguisher inspected and check all extinguishers on campus.
9779 | Correct all violations by reinspection date, or provide action plan for items that cannot be completed by reinspection date.Fire alarm is still red-tagged, but alarm in daycare building is 100% functional. Fire alarm replacement is in bid as of this report. Will be replaced this year. Self-fire watch is currently in effect and will remain in place. See inspection #313817 for violations carried over to report for entire campus.
9780 | 10/14/2020 - RED TAGGEDReplacement of entire FA system tentatively scheduled for February 2021.Immediately initiate self-fire watch for all buildings. If possible, repair initiation and notification devices for Bldg. E. If Bldg. E cannot be brought to 100% function by 12/14/2020, a Fire Marshal standby will be mandatory. Initiation and notification appliances in other buildings shall not be replaced without plans and permits.If initiation and notification in Bldg. E can be repaired, the self-fire watch will remain in place until the close of business on 12/18/2020. No employees are allowed inside any building on campus from the close of business on 12/18/2020 through 1/4/2021 without a fire watch in place. Beginning 1/4/2021, a Fire Marshal standby may be required, depending upon status and duration of proposed F/A replacement.
9781 | Provide documentation of 90 minute egress lighting test. Provide documentation that any deficiencies were corrected.
9782 | Provide documentation of required annual fire safety training.
9783 | Provide daycare fire drill log for inspector to review.
9784 | NoData
9785 | NoData
9786 | 12/2020 - OK
9787 | 6/11/2019 - OK
9788 | Obstructed drills OK.
9789 | Monthly drills conducted. Log OK
9790 | 6/12/2020 - OK
9791 | Correct all violations within 60 calendar days.Within 14 days, provide action plan.
9792 | 10/14/2020 - RED & YELLOWWithin 14 days, provide action plan for fire alarm replacement. Action plan must include a definitive date replacement will begin.
9793 | ANSUL missing tag. Have system inspected and tagged.
9794 | Provide documentation of required annual fire safety training.
9795 | ADD ELECTRICAL PANEL INSERTS WHERE MISSING BREAKERS ARE LOCATED TO AVOID ACCIDENTAL ELECTROCUTION.
9796 | HAVE REQUIRED 5 YEAR GAS TEST PERFORMED FOR YOUR PLACE OF BUSINESS.
9797 | BEFORE GAS TEST IS PERFORMED A PERMIT MUST BE OBTAINED FROM THE HOUSTON PERMITTING OFFICE BY THE CERTIFIED PLUMBER.
9798 | HAVE ALL EMERGENCY EXIT LIGHTS THAT ARE NOT IN WORKING ORDER REPAIRED OR REPLACED. EXIT SIGNS SHALL BE ILLUMINATED AT ALL TIMES AND NOT BE DANGLING FROM THE CEILING.
9799 | ADD SIGN NEAR MAIN ENTRANCE WITH THE OCCUPANT LOAD.
9800 | ADD DECAL TO FRONT DOORS THAT READS, "THESE DOORS TO REMAIN UNLOCKED DURING BUSINESS HOURS". THIS SIGN SHALL BE VISIBLE FROM THE INSIDE.
9801 | NoData
9802 | NoData
9803 | NoData
9804 | Portable Fire Extinguisher(s) annual maintenance Dt: 7/20
9805 | Finaled CO in ILMS Proj# 17140358 '12 COR, referred to habitability
9806 | Due to blocked exits....see IRGO comments
9807 | Keep all exit door(s) and pathways clear. Please remove all carts, stock, boxes, etc. in front of exit to maintain a clear pathway
9808 | NoData
9809 | Illumination requirement for exit sign
9810 | No missing spacers allowed in electrical panels; All junction boxes, light switches and plug outlets must have cover plates installed
9811 | Illuminated Exit sign required for exit door on the East side of stock room
9812 | A spraying/dipping permit is required for dipping operations. A hazardous material permit is required for the solvent used in the dipping operations. Permits can be obtained at 1002 Washington Ave. Houston TX.
9813 | Repair or replace the inoperable emergency illumination.
9814 | Ensure dip-tank covers are compliant.
9815 | Place NFPA 704 hazard identification signs on the door leading to the dipping room and at the main entrance to the building.
9816 | Fire extinguishers are due for annual service before the end of 04/2021.
9817 | An approved automatic fire extinguishing system or dip-tank cover is required in accordance with sec. 2405.3.4
9818 | Ensure ventilation is adequate to prevent the dangerous accumulation of vapors.
9819 | Ensure transferring of solvent is compliant.
9820 | Ensure proper bonding is in place prior to transferring solvent.
9821 | Complete and return HMIS forms.
9822 | No violations found at this time. All exit doors clear. Fire extinguisher service tags are acceptable. Exit signs and emergency lighting is fully functional. No fire alarm and sprinkler system.
9823 | NoData
9824 | NoData
9825 | The owner / occupant shall be held responsible for the correction and abatement of all violations listed in this notice of violations report. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
9826 | Review the accompanying form and make any necessary changes.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
9827 | Please review your HMMP and update as needed.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
9828 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
9829 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
9830 | Provide documentation/report for fire damper testing and any necessary repairs.
9831 | Provide certificate of flame resistance, it shall indicate the color for all decorative materials. 1. new curtains, new certificate or 2. new certificate showing retesting of flame resistance. (Stage Curtains)
9832 | Correct 3/20/2020 Advantage Interest, Yellow Tag on Sprinkler System. Pics included. (Note: Yellow tag should not be scratched out.)
9833 | Provide Boiler Permits: 163936, 163937, 199062, 199063
9834 | NoData
9835 | NoData
9836 | Portable Fire Extinguisher(s) annual maintenance Dt: 3/21
9837 | Portable fire extinguishers are required to be mounted per code. Not allowed to be stored on floor, complied on site
9838 | Commercial Kitchen Hood 6-month extinguisher maintenance Dt: 3/21
9839 | K-rated [Kitchen] (Silver) portable fire extinguisher(s) annual maintenance Dt: 3/21
9840 | Commerical Kitchen hood 6-MONTH inspection Dt:1/21
9841 | 36" Working clearance must be maintained in front of electrical panels. Complied on site
9842 | NoData
9843 | No missing spacers allowed in electrical panels; All junction boxes, light switches and plug outlets must have cover plates installed
9844 | Commercial Kitchen hood has excessive grease buildup, requires cleaning
9845 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs
9846 | Toggle Switch is inoperable.
9847 | The manual gate 911 lock is rusted shut.
9848 | NoData
9849 | remove all metal parts and any other obstructions away from exit door
9850 | have both fire extinguishers inspected and tad
9851 | remove flammable or combustible materials from shop area such as boxes paper .leaves ,plastic containers from the emmediate area that could a fire hazard.
9852 | remove all flammable or combustible materials such as empty plastic bottles, empty boxes, paper ,cloth materials and any other trash from premises that create a fire hazard
9853 | provide metal covers for (5) gallon containers that are filled with waste oils temporary before dispensing into main plastic oil container designed for all waste oils.
9854 | label with the following words restroom ,office,main
9855 | provide and install a small 2/1-2 fire extinguisher at front office
9856 | all doors shall be properly identified in case of an emergency or fire with the following wordage such as restroom, storage room, office electrical room exc.
9857 | remove all waste oil from ground area where located
9858 | apply for a cutting and welding permit or remove the hold rig from premises.
9859 | make application permit for flammable or combustible liquids storage and use class (2) and class 3b over 25 gallons inside of shop or 60 gallons outside type f-7 at 1002 Washington fire marshal's permit section
9860 | repair all emergency lights that are not working
9861 | 1) COMPLETE HAZARDOUS MATERIAL INVENTORY STATEMENT (HMIS) 2) COMPLETE OWNER'S STATEMENT
9862 | PROVIDE AND POST CERTIFICATE OF OCCUPANCY
9863 | SEVICING REQUIRED FOR FIRE EXTINGUISHERS (LAST SERVICED 11-2011)
9864 | The fire alarm system must have an audibility test performed on it.
9865 | The fire alarm system must have an emergency lighting test performed on it.
9866 | a4 permit expired
9867 | NoData
9868 | NoData
9869 | NoData
9870 | NoData
9871 | NoData
9872 | NoData
9873 | NoData
9874 | NoData
9875 | NoData
9876 | Fire extinguishers shall be inspected and service tagged annually by a licensed fire protection equipment service company.
9877 | FA: Sept. 17 FS: March 16 FEX: June 17 GAS: None
9878 | Make all corrections to deficiencies of the Fire Alarm, Fire Sprinklers immediately.
9879 | Provide a list of all Fire Alarm and Fire Sprinkler deficiencies.
9880 | Replace missing fire extinguishers at the BBQ areas.
9881 | All automatic wet-pipe sprinkler systems shall be inspected and tested annually in accordance with NFPA 25 and state requirements, and service tagged by a licensed automatic fire sprinkler service company.
9882 | Inspect all Fire Doors and ensure they are operating as intended.
9883 | Label all unit breakers as to which unit it controls.
9884 | NoData
9885 | NoData
9886 | NoData
9887 | NoData
9888 | Correct the Trouble Alarm on the Fire Alarm Control Panel
9889 | Event Manager has submitted a site plan for the event.
9890 | The GRB has an annual assembly permit proj#5026247.
9891 | Please have all deficiencies noted on red tag corrected.
9892 | NoData
9893 | NoData
9894 | no violations found at this time>alarm 8/2020; extinguisher 8/2020; ansul 8/2020
9895 | Fire Alarm Is Red Tagged.72 Hour Notice Issued Self Fire Watch inplace
9896 | NoData
9897 | NoData
9898 | NoData
9899 | Retag fire extinguisher in electrical/ mechanical room.
9900 | Install fail-safe on access gate.
9901 | Install knox-box on gates.
9902 | Replace cover on junction box.
9903 | Cover opening in electrical room with fire resistant caulking.
9904 | Place knox box on access gates.
9905 | Owner's responsibility. Comply with the above fire code.
9906 | 911 Key box is required outside of the main entrance (front door) as per COH - LSB Standard # 5.
9907 | NoData
9908 | NoData
9909 | Renew the S1 and H3 permits.
9910 | Remove the exit sign leading to the shop.
9911 | Ensure compressed gas cylinders are secured.
9912 | Remove old fire extinguishers or have them inspected with a current inspection tag.
9913 | Remove obstructions in front of exits.
9914 | Have a licensed fire protection company service and tag the spray booth suppression system.
9915 | Clear and maintain space around the spray booth.
9916 | Propane storage within the building is prohibited.
9917 | Ensure the exit signs are illuminated in the shop.
9918 | NoData
9919 | NoData
9920 | NoData
9921 | NoData
9922 | NoData
9923 | NoData
9924 | NoData
9925 | NoData
9926 | NoData
9927 | NoData
9928 | NoData
9929 | Missing fire extinguisher in laundry.
9930 | FYI: No fueled equipment shall be stored inside a building.
9931 | Label exterior electrical boxes with the unit number they operate.
9932 | Need a gas leak test every 5 years. Last test was on 2/12/2016 expired 2/12/2021. #16013266.
9933 | Leave all gates open until all 911 features work as they should.
9934 | NoData
9935 | NoData
9936 | NoData
9937 | Exit lights need to be repaired.
9938 | NoData
9939 | Compliance letter.
9940 | Needs annual inspection + compliance letter once completed.
9941 | Compliance letter.
9942 | Room is clean and well taken care of. To avoid any possibility that an oily rag gets left behind by an elevator mechanic, please provide a metal, self closing trash can that is only used for oily rags, no trash.
9943 | Overview of the contents of the box.
9944 | Binder contents
9945 | NoData
9946 | Keysets are in good condition. Garage Master key needs to be labeled and added.
9947 | 2 Elevator hoistway door keys/tools are needed in the box.
9948 | NoData
9949 | Lock-out tag-outs are needed on the wall near the elevator power breakers.
9950 | Signage is needed to guide fire department personnel to the location of the sprinkler riser room.
9951 | Compliance letters for all fire protection systems.
9952 | NoData
9953 | NoData
9954 | NoData
9955 | COMPLIANCE DATE: 15 CALENDAR DAYS
9956 | SERVICE FIRE ALARM PANEL ON OR BEFORE ANNUAL DATE OF 3/16/21
9957 | NoData
9958 | NoData
9959 | NoData
9960 | NoData
9961 | NoData
9962 | NoData
9963 | ALL ACCESS AND EXIT DOORS SHALL BE KEYEDALIKE. ENSURE ALL FIREFIGHTER ACCESS DOORS HAVE APPROVED HARDWARE THAT ISREADILY OPERABLE FROM THE EGRESS SIDE. (PANIC HARDWARE OR LEVER ACTION WHICHOPEN WITH ONE MOVEMENT AND REQUIRE NO SPECIAL TOOLS OR KNOWLEDGECOMPLIANCEWITHIN 30 DAYS
9964 | THERE SHALL BE NO COMBUSTIBLE MATERIALSTORAGED WITHIN 3 FT IN ALL DIRCETIONS OF BATTERY CHARGERS STATION.COMPLIANCEWITHIN 30 DAYS
9965 | APPLY FORAND OBTAIN PERMIT FROM THE CITY OF HOUSTON PERMIT CENTER LOCATED AT 1002WASHINGTON AVE. (832)394-9000.COMPLIANCEWITHIN 30 DAYS
9966 | AT NO TIME SHALL ANY FIREEXTINGUISHER SYSTEM OR FIRE EXTINGUISHER ACTUATING SYSTEM BE OBSTRUCTION OR BLOCKED FROM VIEW OR ACCESS.COMPLIANCE IMMEDIATELY
9967 | THE OWNER / OCCUPANT SHALL BE HELDRESPONSIBLE FOR THE CORRECTION AND ABATEMENT OF ALL VIOLATIONS LISTED IN THISNOTICE OF VIOLATIONS REPORT.COMPLIANCE WITHIN 30 DAYS.
9968 | A LICENSED FIRE ALARM SERVICE COMPANY SHALLPERFORM A TEST OF ALL THE FIRE ALARM SYSTEM ANNUNCIATION DEVICES NOT LESS THANEVERY 3 YEARS.COMPLIANCE WITHIN 30 DAYS
9969 | A LICENSED FIRE PROTECTION SERVICE COMPANY SHALL CONDUCT HYDROSTATIC AND FLOW TESTS OF ALL FIRE DEPARTMENT CONNECTIONS, PIPING AND CHECK VALVE ASSEMBLIES, NOT LESS THAN EVERY FIVE (5) YEARS.PROVIDE WRITTEN REPORT OF INSPECTION FINDINGS IF COMPLETED WITHIN THE LAST FIVE (5) YEARS.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
9970 | FIREDETECTION, ALARM AND EXTINGUISHING SYSTEMS SHALL BE MAINTAINED IN AN OPERATIVECONDITION AT ALL TIMES AND SHALL BE REPLACED OR REPAIRED WHERE DEFECTIVE. THEFIRE PROTECTION SPRINKLER SYSTEM SHALL BE TESTED ANNUALLY BY A LICENSED COMPANYAND ALL TROUBLE (YELLOW) TAG(S) SHALL BE REMOVED AND ACCEPTABLE (WHITE) SERVICETAG(S) SHALL BE AFFIXED TO ENSURE SYSTEM IS MAINTAINED IN OPERATIVE CONDITION.COMPLIANCE IMMEDIATELY
9971 | FIRE DETECTION, ALARM AND EXTINGUISHINGSYSTEMS SHALL BE MAINTAINED IN AN OPERATIVE CONDITION AT ALL TIMES AND SHALL BEREPLACED OR REPAIRED WHERE DEFECTIVE.THE FIRE PROTECTION SPRINKLER SYSTEM SHALL BETESTED ANNUALLY BY A LICENSED COMPANY AND ALL TROUBLE(YELLOW TAG)TAG(S) SHALL BE REMOVED ANDACCEPTABLE (WHITE) SERVICE TAG(S) SHALL BE AFFIXED TO ENSURE SYSTEM ISMAINTAINED IN OPERATIVE CONDITION.COMPLIANCE: IMMEDIATELY.
9972 | AISLES WIDTHS STATED ON THE APPROVED PLANSARE NOT BEING MAINTAINED AND SHALL BE BROUGHT INTO COMPLIANCE.COMPLIANCE WITHIN30 DAYS
9973 | HAVE THE APPROPRIATE FIRE EXTINGUISHER MOUNTED WITHIN THE APPROPRIATEDISTANCE FROM THE CHARGING STATION.COMPLIANCE WITHIN 30 DAYS
9974 | APPROVED PLANS ARE TO BE KEPT ON SITE AT ALL TIMES. IF APPROVED PLANS CANNOT BE LOCATED, AREQUEST TO THE BUILDING DEPARTMENT MAY BE ABLE TO DUPLICATE THE ORIGINAL 1002WASHINGTON AVE HOUSTON TEXAS 77002APPROVED PLANS MUST BE SUBMITTED TO FIRE MARSHAL OR THE PROCESSFOR HIGH-PILED STORAGE PLAN SUBMITTAL PROCESS SHALL BE RESTARTED. COMPLIANCE WITHIN 30 CALENDAR DAYS.
9975 | AISLES WIDTHS STATED ON THE APPROVED PLANSARE NOT BEING MAINTAINED AND SHALL BE BROUGHT INTO COMPLIANCE.COMPLIANCEWITHIN 30 DAYS.
9976 | ALL ACCESS DOORS SHALL BE IDENTIFIED WITHLETTERING “HFD”, WHICH MEETS THE ABOVE CODE REQUIREMENTS, BEING MARKED ON THEUPPER LEFT-HAND CORNER OF EACH DOOR.COMPLIANCE WITHIN 30 CALENDAR DAYS.
9977 | A WORKING SPACE (CLEARED OF ALL COMBUSTIBLEMATERIAL) OF NOT LESS THAN 30 INCHES IN WIDTH, 36 INCHES IN DEPTH AND 78 INCHESIN HEIGHT SHALL BE PROVIDED IN FRONT OF ELECTRICAL SERVICE EQUIPMENT.COMPLIANCEWITHIN 30 DAYS
9978 | FOLLOW CODE REFERRED TO ABOVE CONCERNINGLOCKS OR LOCKING. ANY AND ALL DROP BARS ATTACHED TO EXIT DOORS SHALL BE REMOVEDTHAT PREVENTS EMERGENCY DOORS FROM OPENING WITH ONE ACTION OPENING.COMPLIANCEWITHIN 30 DAYS
9979 | NoData
9980 | NoData
9981 | NoData
9982 | Richard PollockNO VIOLATIONS FOUND AT THIS TIME.
9983 | No violations at this time.
9984 | Provide a 5 lb. (2A:10B/C ) fire extinguisher mounted in the kitchen area. Mount the fire extinguisher in a conspicuous location per the mounting instructions noted in the Life Safety Bureau code. Keep the receipt handy to provide the date of purchase. The extinguisher will need to be inspected annually, and the initial purchase date will be needed.
9985 | Make all code violation corrections and contact the inspecting code official when completed for reinspection.
9986 | Provide a 5 lb. (2A:10B/C ) fire extinguisher mounted in the kitchen area. Mount the fire extinguisher in a conspicuous location per the mounting instructions noted in the Life Safety Bureau code. Keep the receipt handy to provide the date of purchase. The extinguisher will need to be inspected annually, and the initial purchase date will be needed.
9987 | Provide a 5 lb. (2A:10B/C ) fire extinguisher mounted in the kitchen area. Mount the fire extinguisher in a conspicuous location per the mounting instructions noted in the Life Safety Bureau code. Keep the receipt handy to provide the date of purchase. The extinguisher will need to be inspected annually, and the initial purchase date will be needed.
9988 | Provide a 5 lb. (2A:10B/C ) fire extinguisher mounted in the kitchen area. Mount the fire extinguisher in a conspicuous location per the mounting instructions noted in the Life Safety Bureau code. Keep the receipt handy to provide the date of purchase. The extinguisher will need to be inspected annually, and the initial purchase date will be needed.
9989 | Provide a 5 lb. (2A:10B/C ) fire extinguisher mounted in the kitchen area. Mount the fire extinguisher in a conspicuous location per the mounting instructions noted in the Life Safety Bureau code. Keep the receipt handy to provide the date of purchase. The extinguisher will need to be inspected annually, and the initial purchase date will be needed.
9990 | A gas leak test is required by the state for foster homes. This is an annual test that must be performed by a licensed plumber. Provide documentation on their company letter head stating that the gas leak test was performed and passed. The letterhead report should be dated and contain the plumbers name and licensing number.
9991 | NoData
9992 | NoData
9993 | NoData
9994 | NoData
9995 | NoData
9996 | NoData
9997 | NoData
9998 | NoData
9999 | NoData
10000 | Ansul in paint booth must be inspected every 6 months.
10001 | Replace missing junction plate at paint booth.
10002 | Relocate extinguisher to avoid obstructions.
10003 | NoData
10004 | NoData
10005 | NoData
10006 | NO VIOLATIONS TO FACILITY AT THIS TIME. ALL LIFE SAFETY SYSTEMS ARE IN PLACE AND IN NORMAL OPERATING MODE.
10007 | ENSURE ALL EXTINGUISHERS ARE PROPERLY MOUNTED
10008 | ENSURE FDC SIGNS ARE CORRECT
10009 | PLACE CORRECT KEYS IN 911 KEY BOXES
10010 | UPDATE MOBILITY IMPAIRMENT LIST EVERY 6 MONTHS.
10011 | PLACE 8X10 LAMINATED KEY LEGEND IN DEPOSITORY BOX
10012 | MAINTAIN 2 HOISTWAY DOOR KEYS IN DEPOSITORY BOX
10013 | MAINTAIN ELEVATOR INDEPENDANT SERVICE KEYS (FOR NON-FIRE EVENTS) OUTSIDE OF BUT NEAR THE DEPOSITORY BOX
10014 | ENSURE ALL ELECTRICAL/MECHANICAL/ELEVATOR CONTROL ROOMS ARE PROPERLY LABLED
10015 | NoData
10016 | NoData
10017 | NoData
10018 | INSTALL SIGN AT ROOF TOP TEST CONNECTIONS
10019 | ENSURE ALL ELEVATOR DOORWAYS ON RECALL FLOOR HAVE APPROPRIATE "CAR NUMBER" SIGNS INSTALLED
10020 | NoData
10021 | ENSURE ALL STAIRWAY SIGNS ARE CORRECT
10022 | The property is not showing a 911 Key Box permit at this location. Please make an application and payment for a annual permit for the 911 key box.
10023 | The property is not showing a access gate permit at this location.
10024 | 911 Key Box was not found on entrance/ exit gate on Airline, property had a unsecured 911 Key Box on W. Cavalcade entrance/exit gate. A Knox Box 3200 hinged series UL approved 1037 tamper proof with a security switch as per IFC 2012 section 506.1 is recommended to allow emergency responders to gain entry if necessary.
10025 | NoData
10026 | LAST FIRE ALARM PANEL INSPECTION 1-10-20PAST DUE, BRING UP TO CODE.
10027 | PLACE UPDATED PERMITS IN FIRE MARSHAL BINDER
10028 | Facility has had a number of false alarms. In an attempt to keep facility safe for its occupants, facility management has hired a disinfecting company to keep facility cleanfrom possible germs and bacteria accumulation. Allis done in the interestof reducing possible Covid-19 transferor exposure. During the process, the disinfecting equipment has triggered accidentalautomatic alarms witch has caused an emergency response from emergency personnel. Moving forward, the Fire Alarm will be put in test mode while disinfecting process is initiated. There are no occupants during this process. Once the process is complete, the Fire Alarm panel will be put back in Normal Operating Mode. If nuisance alarms continue, facility will be issued a citation.
10029 | NoData
10030 | NoData
10031 | NoData
10032 | NoData
10033 | NoData
10034 | NoData
10035 | NoData
10036 | NoData
10037 | NoData
10038 | NoData
10039 | NoData
10040 | NoData
10041 | ADD EXIT SIGNS OF TOP FLOOR OF GARAGE. COMPLIANCE WITHIN 60 DAYS
10042 | NoData
10043 | REPAIR FIRE WALL IN STAIRWELL 8A, FIRE CAULK IN PENTHOUSE COMPLIANCE WITHIN 60 DAYS
10044 | LABEL HOSE CABINETS WHEN LABELING IS FADED. COMPLIANCE WITHIN 60 DAYS
10045 | NoData
10046 | NEED KEY CARDS FOR EACH KEY RINGS ACCESS SECURED FLLOS COMPLIANCE WITHIN 60 DAYS
10047 | PLACE SIGNAGE OVER PULL STATIONS IN 4TH FLOOR ELEVATOR LOBBY. COPLIANCE WITHIN 60 DAY
10048 | NoData
10049 | Facility needs to provide inspector with the following report documents that Show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). Certificate of Occupancy: Core of Building C of O only Active Fire Permits: Up to date and Paid. Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation. Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards. Fire Alarm Permit: Sprinkler Percentage Letter and Form: Building System Test Documentation LSB # 2 Electronic Locks-Semi Annual Sprinkler System- Annual Fire Alarm System Test- Annual Fire Extinguishers- Annual Fire Hoses- Annual Fire Pumps Flow Test- Annual Emergency Power & Lighting- Annual Generator Test (ATS) - Annual Fire Alarm Audibility Test- 3 Year Fire Hose Pressure Test- 3 year Fire Dampers- 4 Year Fire Alarm Sensitivity- 5 Year FDC Test (Bldg. & Garage) - 5 Year PRV / PRD Test- 5 Year Stair pressurization Test- 5 Year Standpipe System- 5 Year Water Supply Tank Inspection- 5 Year Boiler- Permit Elevator-Annual Permit Dry Partial or Full Trip Test Gas Test- 5 Year COMPLIANCE WITHIN 60 CALENDAR DAYS.
10050 | ADJUST STAIRWELL DOOR 8B,6B, 5A, AND 2A. COMPLIANCE WITHIN 60 DAYS
10051 | HAVE FIRE PROTECTION COMPANY EVALUATE LOCATION OF FIRE EXTINGUISHERS. COMPLIANCE WITHIN 60 DAYS
10052 | PENTHOUSE NEEDS TO BE EVALUATED FOR SPRINKLER COVERAGE. COMPLIANCE WITHIN 60 DAYS
10053 | NoData
10054 | NoData
10055 | NoData
10056 | NoData
10057 | Annual permit for Minute Maid Park's C-9.
10058 | COMPLIANCE DATE: 15 CALENDAR DAYS.
10059 | (k1 and a4) fire prevention permit is expired at this time.
10060 | NoData
10061 | NoData
10062 | COMPLIANCE DATE: 15 ALENDAR DAYS
10063 | (f7 and h3) fire prevention permit is expired at this time.
10064 | Replace missing Junction Box Cover inside Fire Command Room.
10065 | 2nd floor Stair "B."
10066 | NoData
10067 | Provide Current Annual Inspection Tags for All Fire Protection Equipment on property.
10068 | Provide Current Annual Inspection Tag for the Fire Sprinkler System.
10069 | NoData
10070 | NoData
10071 | NoData
10072 | NoData
10073 | Provide Removal of all Combustible documents stored within Electrical Room conduit throughout property.
10074 | Provide bright Red Paint for front entrance Key Box.
10075 | NoData
10076 | Provide current Emergency Contact List and Mobility Impaired List.
10077 | Repair Sheetrock Holes inside Fire Command Room. Replace Ceiling Tile inside Fire Command Room and 2nd floor Electrical Room.
10078 | Throughout Property.
10079 | Discontinue placing informational signage adjacent to the Emergency Elevator Signage.
10080 | NoData
10081 | NoData
10082 | Obtain a Key Box/Fire Depository Box Permit
10083 | Fire Sprinklers Do not have Current Tags:Annual TagSprinkler Data Plate is missing
10084 | Fire Extinguishers are out of date or missing annual tag.
10085 | Install Key Boxes on all secured exterior exits/entrances and place access keys/fobs in the boxes.
10086 | Place a Fire Depository Box as required by LSB #6Place all required information and keys in the Fire Depository Box as per LSB #6
10087 | Maintain and Update the Building File Check List. Comply with all required tests as they come due.
10088 | NoData
10089 | Obtain a P2 Places of Assembly Permit for the assembly places in excess of 49 maximum occupant load.
10090 | NoData
10091 | NoData
10092 | NoData
10093 | NoData
10094 | NoData
10095 | NoData
10096 | NoData
10097 | NoData
10098 | Please have fire extinguishers serviced.
10099 | CURRENTLY NO SERVICE TAGS AT ABOVE LOCATIONS. HAVE FIRE PROTECTION COMPANY ADD MISSING TAGS TO ALL ABOVE LOCATIONS SHOWING PROOF OF ALL REQUIRED QUARTERLY/ANNUAL/5YR INSPECTIONS.3/10/21 - 5yr AND ANNUAL TAGS NOW ON RISER, ALL PREVIOUS YEARS STILL MISSING, POSSIBLY BY SOMEONE AT COMPANY
10100 | PLACE REQUIRED SIGNAGE ON OUTSIDE OF CONTAINER PER ABOVE CODE AT BOTH ENTRANCES. ALSO PLACE A LABEL "LITHIUM BATTERY STORAGE" AT SAME LOCATIONS.
10101 | ONLY PANIC HARDWARE IS ALLOWED, AND THEY SHALL BE ACCESSIBLE FROM THE EXTERIOR BY USE OF A KEY WHICH WILL BE LOCATED IN 911 KEYBOX. CURRENTLY AT LEAST ONE HFD DOOR HAS NO KEY OPENABLE LOCK FROM EXTERIOR SIDE - REPLACE WITH APPROVED LOCKING DEVICE.
10102 | PROVIDE LABELED KEYS TO THIS CONTAINER TO CODE OFFICIAL SO THAT THEY MAY BE PUT IN 911 KEYBOX
10103 | Place sign on door identifying electrical room.
10104 | Replace missing ceiling tiles in electrical room (Houston terminal) and cover openings in electrical room ( corporate building).
10105 | Please clear area around electrical panel.
10106 | Repair exit light in corporate building.
10107 | NoData
10108 | NoData
10109 | Portable Fire Extinguisher(s) annual maintenance Dt: 2/21
10110 | Finaled CO in ILMS Proj# 5189395 '85 COR
10111 | No missing spacers allowed in electrical panels
10112 | fire extinguisher required at bbq pit.mount 3ft-5ft and minimum 5ft from bbq pit.
10113 | service red tag fire alarm due to the freeze.
10114 | repair missing door latch in stairway. Repair Trash chute door
10115 | repair emergency lighting, stair c 4fl and all other area as needed.
10116 | Carrie Mckenzie 7135201699
10117 | elev, k1, co, pool, fire alarm, multifamily, boiler are current.
10118 | January 1, 2017 as battery operated single station alarm is replaced, that smoke alarm shall be replaced with tamper-resistant battery-operated single station smoke alarm.
10119 | The audibility tests required by code must be completed for alarms servicing the buildings addressed to 9254 and 9258 Park South View. If this service has already been completed, provide documentation from the alarm company. Any deficiencies identified during this maintenance must be corrected.
10120 | The 5 year hydrostatic maintenance must be completed for the system. All deficiencies found during this service must be corrected.
10121 | As required by code, the 5 year maintenance must be completed for the water tank in the pump room. Any deficiencies found during this service must be corrected.
10122 | The deficiencies requiring a yellow tag for the alarm panel servicing the building addressed to 9258, which is tied to the suppression system installed in building 9254, must be corrected.
10123 | Because there is an approved HAZMAT occupancy (H3) located in building 9254 Park South View, Suite 450 (Land N Sea), it is required that an alarm company technician be on-site during the alarm tests to ensure that the monitoring station is receiving a "Hazmat Alarm" signal and the Houston Fire Department is the responding agency for this signal, if the alarm is initiated from this suite.Documentation from the alarm company must be provided that the HAZMAT signal is being identified suite 450.
10124 | The 3 year audibility testing is required for alarm panels located in building 2710, 2720 and 2730 Reed Rd. if this has been completed, a report from the alarm company may be sent for compliance. Any deficiencies noted during this maintenance must be corrected.
10125 | The alarm panel located in building 2720 Reed Rd has a 'TROUBLE' signal that must be addressed. Have any deficiencies restored for this system.Panels located in building 2710 and 2730 are in operational readiness condition.
10126 | Fire Alarm Is Impaired Fire Sprinklers are out of serviceSelf Fire Watch established, Maintain self fire watch until all FP systems are in regular service.
10127 | H3 permit expired
10128 | Make all repairs to all fire protection systems. Continue the self initiated fire watch until all Fire Alarms and Fire Sprinkler Systems are back in regular ready status.
10129 | NoData
10130 | NoData
10131 | NoData
10132 | NoData
10133 | NoData
10134 | NoData
10135 | Provide annual test and service tag for fire alarm system.(Note: New fire alarm panel installed with no annual inspection tag)
10136 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
10137 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
10138 | Provide documentation/report for annual 'Load Test' and any necessary repairs.
10139 | Provide documentation/report for fire damper testing and any necessary repairs.
10140 | Provide documentation/report for smoke detector sensitivity testing and any necessary repairs.
10141 | Provide Boiler Permits. 267057, 267058
10142 | NoData
10143 | NoData
10144 | NoData
10145 | provide and install metal canwith a cover metal lid
10146 | all fire extinguishers shall be inspected and tag once a year by a certifide company
10147 | provide and install a plain exit sign on both exit doors leading to the outside of the building
10148 | apply at 1002 Washington permit section or reduce to one barrel of waist oils 55 gallons capacity and provide sign stating waist oil
10149 | provide and install
10150 | NoData
10151 | NoData
10152 | NoData
10153 | NoData
10154 | ALL EXIT SIGNS SHALL BE ILLUMINATED AT ALL TIMES. REPAIR EXIT SIGN. -CAFETERIA
10155 | REMOVE ALL STORED COMBUSTIBLE MATERIAL FROM BOILER ROOMS, MECHANICAL ROOMS OR ELECTRICAL EQUIPMENT ROOMS. -ELECTRICAL ROOM
10156 | SECOND NOTICE PER INSPECTION REPORT #18112128 A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL OF THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY 3 YEARS. LAST AUDIBILITY TEST DATED: UNKNOWN. PROVIDE WRITTEN DOCUMENTATION/REPORT OF AUDIBILITY TEST AND MAINTAIN ON FILE FOR FIRE CODE OFFICIAL. ANY FAILURES OF THE AUDIBILITY TESTING SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
10157 | SECOND NOTICE PER INSPECTION REPORT #18112128 A REINSPECTON FEE AND/OR CITATION WILL BE ISSUED IF NOT COMPLETED. ---------------------------------------------------------------------- PROVIDE REPORT OF TEST RESULTS IF DECORATIVE MATERIALS ARE TO MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701. CERTIFICATE OF FLAME RESISTANCE SHALL INDICATE THE COLOR AND/OR NUMBER FOR ALL DECORATIVE MATERIALS THROUGHOUT SCHOOL. PROVIDE CERTIFICATE OF FLAME RESISTANCE THAT MEET FLAME PROPAGATON PERFORMANCE CRITERIA OF NFPA 701 BY AN APPROVED COMPANY. -GYM CURTAINS
10158 | CURRENT INFORMATION -FPS FIRE ALARM SYSTEM ANNUAL INSPECTION DATE: 12/4/2018 ACCEPTABLE BLUE TAG SPRINKLER SYSTEM INSPECTION DATE: N/A ANNUAL FIRE EXTINGUISHER INSPECTION DATE: 10/2018 ANSUL SYSTEM BI-ANNUAL INSPECTION DATE: N/A
10159 | REPLACE MISSING PORTABLE FIRE EXTINGUISHER -GYM
10160 | NoData
10161 | FYI.
10162 | ALL EMERGENCY LIGHTS SHALL BE REPAIRED AND TESTED TO ENSURE PROPER OPERATION IN CASE OF EMERGENCY. (GYM)
10163 | SECOND NOTICE PER INSPECTION REPORT #18112128 PROVIDE DOCUMENTATION FOR DETECTOR SENSITIVITY TESTING. VERIFY ALL DETECTOR SENSITIVITY IS IN WORKING CONDITION. LAST SENSITIVITY TEST DATED: UNKNOWN NOTE: FIRE ALARM COMPANY SHALL INDICATE DATE OF SENSITIVITY TESTING ON BLUE TAG OR IF SYSTEM IS AUTOMATIC.
10164 | REMINDER: ALL CURTAINS, DRAPERIES, HANGINGS AND OTHER DECORATIVE MATERIALS SHALL MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701 OR BE NONCOMBUSTIBLE. PROVIDE CERTIFICATE OF FLAME RESISTANCE (SEE FIRE CODE BELOW, 807.2) OR REMOVE ALL THAT DO NOT MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701 AND CANNOT PROVIDE A CERTIFICATE OF FLAME RESISTANCE.
10165 | HAND-HELD PORTABLE FIRE EXTINGUISHERS, NOT HOUSED IN CABINETS, SHALL BE INSTALLED ON THE HANGERS OR BRACKETS SUPPLIED. -BOTH BREAK ROOMS
10166 | NoData
10167 | Spray booth shall be inspected by a licensed HVAC company.Compliance: 30 calendar days.
10168 | NoData
10169 | NoData
10170 | NoData
10171 | NoData
10172 | NoData
10173 | NoData
10174 | NoData
10175 | NoData
10176 | Portable Fire Extinguisher(s) annual maintenance Dt: 6/20
10177 | NoData
10178 | NoData
10179 | NoData
10180 | NoData
10181 | COMPLIANCE DATE: 15 CALENDAR DAYS
10182 | Fire protection systems shall be maintained in accordance with the original installation standards for that system.
10183 | NoData
10184 | NoData
10185 | NoData
10186 | Have the required annual inspection/service performed on all extinguishers in the facility by a certified fire protection company, nd ensure that new hang tags are put in place.
10187 | NoData
10188 | #NAME?
10189 | NoData
10190 | NoData
10191 | NoData
10192 | NoData
10193 | NoData
10194 | NoData
10195 | NoData
10196 | NoData
10197 | NoData
10198 | NoData
10199 | NoData
10200 | NoData
10201 | NoData
10202 | NoData
10203 | Fire extinguisher must be mounted on the wall.Compliance within 30 days.
10204 | Make necessary repairs stated on yellow tag.Compliance within 30 days.
10205 | Exit sign must be maintained and operable.Compliance within 30 days.
10206 | Remove all combustible materials being stored from under all stairs.Compliance within 30 days.
10207 | Permit required from City of Houston to have a keybox.Compliance within 30 days.
10208 | Keybox required for HFD to have access to facilityCompliance within 30 days
10209 | NoData
10210 | NoData
10211 | NoData
10212 | NoData
10213 | NoData
10214 | NoData
10215 | NoData
10216 | Portable Fire Extinguisher(s) annual maintenance Dt: 1/21
10217 | Annual Fire alarm test Dt: 12/31/20
10218 | Annual Sprinkler system (wet) test Dt: 3/9/21
10219 | 5-year hydro/flow test Dt: 3/16/17
10220 | The owner / occupant is responsible for making all corrections to code violations. The fire alarm system must be repaired as soon as possible. All other code violations noted in the report shall be corrected prior to the re-inspection date noted on page 1 of the report.
10221 | Make sure fire drill are performed monthly. Also, 1/2 of fire drills shall be of the "obstructed" type and noted in the fire drill log / documentation.
10222 | Have a certified fire protection company repair the trouble status for the Fire Alarm System immediately.
10223 | Your gas leak test is good until March 29th, then it will need the two year gas leak test as required by State regulations for daycares.
10224 | NoData
10225 | 3-year audibility test needs to be performed, correct any deficiencies and report provided to fire marshal
10226 | Doors to electrical room(s) must be identified. Add sign to entrance door to riser room and electrical room with "RISER ROOM / ELECTRICAL ROOM UPSTAIRS"
10227 | NoData
10228 | NoData
10229 | NoData
10230 | NoData
10231 | NoData
10232 | NoData
10233 | NoData
10234 | NoData
10235 | NoData
10236 | NoData
10237 | NoData
10238 | NoData
10239 | NoData
10240 | NoData
10241 | NoData
10242 | NoData
10243 | NoData
10244 | NoData
10245 | NoData
10246 | NoData
10247 | NoData
10248 | NoData
10249 | NoData
10250 | NoData
10251 | NoData
10252 | NoData
10253 | NoData
10254 | Please renew your access gate (a4) permit that expired on 12/09/2020. If you need an invoice, please call the HPC office at 832-394-8811 for assistance. Thanks!
10255 | NoData
10256 | ALL RED TAGS MUST BE CLEARED WITHIN 72 HOURS
10257 | MAINTAIN FIRE WATCH. SYSTEM MUST BE RETURNED TO SERVICE WITHIN 72 HOURS OR A STANDBY FIRE MARSHAL MUST BE ASSIGNED.
10258 | NoData
10259 | NoData
10260 | NoData
10261 | NoData
10262 | NoData
10263 | NoData
10264 | NoData
10265 | REMOVE STORAGE IN ELECTRICAL ROOM
10266 | ONCE WATER LEAK IS FIXED REPLACE CEILING TILES IN ELECTRICAL ROOM
10267 | REPLACE COVER OF ELECTRICAL OUTLET OR CONDUITS NEAR STANDPIPES
10268 | BRING FIRE EXTINGUISHERS DOWN BELOW 5FT AND NO LOWER THAN 4 INCHES FROM THE GROUND.
10269 | 5 YEAR GAS TEST IS REQUIRED FOR YOUR PLACE OF BUSINESS. THE LAST TEST PERFORMED WAS 11-4-2013.
10270 | BEFORE GAS TEST IS PERFORMED A PERMIT MUST BE OBTAINED FROM THE HOUSTON PERMIT OFFICE.
10271 | REMOVE ALL STORAGE THAT IS LOCATED DIRECTLY IN FRONT OF ELECTRICAL PANEL. THERE SHOULD BE A 3 FT CLEARANCE IN FRONT OF ELECTRICAL PANEL AT ALL TIMES.
10272 | NoData
10273 | NoData
10274 | NoData
10275 | NoData
10276 | NoData
10277 | Properties with 3 or more units are required to register with the City of Houston as required by Ordinance No. 2006-1124 (Apartment Security Ordinance).Please contact the City of Houston “Multi-Family Rental Property Registration” at 832-394-8841 or log on to http://www.houstonmultifamily.org/Provide copy of lease agreement with smoke detector, fire extinguisher and openFlame cooking policy or addendum.
10278 | NoData
10279 | remove fuel power equibment
10280 | unit number shall be of a color which is in contrast to the background
10281 | label boiler room and storage room
10282 | repair ceiling penetration in boiler room and all other area as needed.
10283 | Required every 5 years and must be completed with an approved permit from theBuilding Department. PROVIDE A PNEUMATIC GAS TEST BY A LICENSED PLUMBER REQUIRED ONCE EVERYFIVE YEARS, A PERMIT FROM THE BUILDING DEPT. MUST BE OBTAINED FOR THISTEST
10284 | replace missing smoke alarm in apt 33, 34, 16, and all other as needed with 10yrs tamper resistant smoke alarm.
10285 | Ensure all exit doors open outwards in the direction of egress travel.
10286 | As an assembly occupancy with an occupant load &gt;50 persons according to your Certificate of Occupancy:-Ensure that all exit doors are equipped with panic hardware with no additional locking devices except for at the main doors.See Report Item #3 for further requirements on locks at the main doors
10287 | Post the max occupant load, as indicated on your Certificate of Occupancy, near the main entry.
10288 | Only the main doors may have a keyed deadbolt in addition to the panic hardware meeting the following guidelines:1) It must be readily distinguishable as locked2) Place a sign on the door, in minimum 1" letters that reads: "This Door to Remain Unlocked When Building is Occupied"
10289 | NoData
10290 | NoData
10291 | NoData
10292 | NoData
10293 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
10294 | Contact a licensed Fire Protection Company to make any repairs necessary to clear the "trouble" signal on the fire alarm control panel.
10295 | Provide annual test and service tag on fire alarm system.
10296 | Provide report for FDC hydrostatic test and blue tag (5th year) on sprinkler riser.
10297 | Correct supervisory alert on fire alarm panel.
10298 | Provide FDC signage.
10299 | Provide report for annual emergency lighting systems test.
10300 | Provide report for fire damper testing and maintenance.
10301 | Apply for, obtain, and post on site a P2: Public Assembly permit. This is required based on your facility's A-2 occupancy type with occupant load over 50 persons as denoted on your certificate of occupancy. The permit may be obtained at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811 www.houstonpermittingcenter.orgThis permit must be obtained prior to operations being initiated.
10302 | NoData
10303 | PLACE REQUIRED SIGNAGE ON OUTSIDE OF CONTAINER PER ABOVE CODE AT BOTH ENTRANCES. ALSO PLACE A LABEL "LITHIUM BATTERY STORAGE" AT SAME LOCATIONS.
10304 | ONLY PANIC HARDWARE IS ALLOWED, AND THEY SHALL BE ACCESSIBLE FROM THE EXTERIOR BY USE OF A KEY WHICH WILL BE LOCATED IN 911 KEYBOX. CURRENTLY AT LEAST ONE HFD DOOR HAS NO KEY OPENABLE LOCK FROM EXTERIOR SIDE - REPLACE WITH APPROVED LOCKING DEVICE.
10305 | PROVIDE LABELED KEYS TO THIS CONTAINER TO CODE OFFICIAL SO THAT THEY MAY BE PUT IN 911 KEYBOX
10306 | PROVIDE PROOF OF COMPLIANCE WITH ABOVE FIRE CODE WHEN STORAGE ARRANGEMENT IS FINALIZED. OUTSIDE CONSULTATION WITH AN ENGINEER IS ADVISED.
10307 | NoData
10308 | NoData
10309 | STORAGE OF FUEL FOR HVOF OPERATION MUST BE RELOCATED OUTSIDE OF BUILDING DUE TO POSSIBILITY OF FUEL VAPORS ACCUMULATING INSIDE BUILDING AND REACHING AN IGNITION SOURCE. = COMPLIANCE: 30 DAYS =
10310 | NoData
10311 | NoData
10312 | FUEL SOURCE FOR HVOF MUST HAVE SECONDARY CONTAINMENT PER ABOVE FIRE CODE
10313 | NoData
10314 | All fire extinguishers must be mounted.Compliance within 30 days.
10315 | Permit for keybox is required.Compliance within 30 days.
10316 | A copy of the HazMat Management Plan and HazMat Inventory Statement must be onsite at all times.Compliance within 30 days.
10317 | City approved and stamped plans must be onsite at all times. Permitting Office 1002 Washington Ave Houston, TX.Compliance within 30 days.
10318 | Key box must be easily accessible and operational with keys to access the gate and have access to enter the facility.Compliance within 30 days.
10319 | All combustible material must be removed 3ft away from electrical panels.Compliance within 30 days
10320 | All exits signs throughout the facility must be maintained and operational.Compliance within 30 days.
10321 | ALL MAG LOCKS SHALL HAVE A CITY OF HOUSTON TAG ATTACHED. PLANS SHALL BE SUBMITTED TO THE CITY FOR REVIEW AND APPROVAL FOR THESE MAG LOCKS.COMPLIANCE WITHIN 30 DAYS
10322 | NoData
10323 | Needs Annual Inspection
10324 | NoData
10325 | All updated permits need to be added to FMB
10326 | NoData
10327 | All fire systems tags that are expired need to be tested and tags dates updated to current dates.
10328 | Fire Extinguishers need to be serviced, inspected and tags updated to correct inspection date. Two extinguishers did not get corrected.
10329 | New addition access road does not have the required fire lanes.
10330 | Permit for fire lanes needed.
10331 | NoData
10332 | Knox box must be installed onto new gates and any existing outdated boxes.
10333 | Permit for elevator needs to be added to FMB
10334 | The class K fire extinguisher lost pressure.
10335 | NoData
10336 | NoData
10337 | NoData
10338 | Due to the ice storm the Sprinkler pipes burst on the first and the second floor causing the water to flood the Alarm System making both System to be Inoperable (Alarm and Sprinkler). Gave a 72 hour notice Than under the Fire Marshal Orders Initiated a Houston Fire Department Fire Watch Intervention starting 04-March-21.
10339 | The fire alarm and sprinkler systems are due for an annual inspection. Have both systems inspected to achieve compliance.Sprinkler system in building 2 and 11 have no water pressure due to pipe rupture from inclement weather.A 24 hrs. 7 days a week inhouse firewatch is required until both systems are back in compliance.
10340 | NoData
10341 | Have a licensed fire protection company service and tag the fire extinguishers.
10342 | Have a licensed fire protection company service and tag the vent hood suppression system. The vent hood requires professional cleaning.
10343 | Repair the emergency illumination on the exit sign located on the rear exit.
10344 | Post the occupant load.
10345 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
10346 | By orders of the Fire Marshal. The apartment community does not have a fire alarm or sprinkler systems. They do have domestic water.
10347 | By orders of the Fire Marshal. The apartment community does not have a fire alarm or sprinkler systems. The apartments community has water.
10348 | By orders of the Fire Marshal. The apartment community does not have a fire alarm or sprinkler systems. They do not have domestic water.
10349 | Need to install a Smoke Alarm in the Laundry Room.
10350 | All Electrical power shut off on the exterior of the building must correct identified to each resident.
10351 | The exterior Laundry room on the exterior of the building Portable Fire Extinguisher is out of its Inspection Date
10352 | NoData
10353 | Add numbers of address to building.
10354 | NoData
10355 | NoData
10356 | Need correct signage for these rooms.
10357 | Required unexpired permits need to be added to FMB. Old permits with old address need to be removed and current one added to new binder.
10358 | NoData
10359 | NoData
10360 | Proper permanent post and sign need to be added facing the street.
10361 | Fail to comply with violations
10362 | F7
10363 | Owner's responsibility. Comply with the above fire code.
10364 | 911 Key box is required outside of the main entrance (front door) as per COH - LSB Standard # 5.
10365 | The owner/occupant shall be held responsible for the correction and abatement of all violations listed in this notice of violations report. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
10366 | HIGH-PILEDCOMBUSTIBLE STORAGE. Storage of combustible materials in closelypacked piles or combustible materials on pallets, in racks or on shelves wherethe top of storage is greater than 12 feet (3658 mm) in height. When requiredby the fire code official, high-piled combustible storage alsoincludes certain high-hazard commodities, such as rubber tires. Group Aplastics, flammable liquids, idle pallets and similar commodities, where thetop of storage is greater than 6 feet (1829 mm) in height.Lower any high-hazard combustibles to below 6 feet in height.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
10367 | Using the format provided, a currentHMIS statement shall be submitted to the hazmat/high-piled 180 team forreview to assure you are within the MAQ's.Correctly fill out a new HMIS for allhazardous materials stored at your facility.The classification ofthe hazardous materials shall comply with the 2012 international fire codeclassifications system.It is highly advisable to seektechnical assistance in correctly completing the HMIS for the hazardousmaterial being stored at the facility.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
10368 | F7
10369 | NoData
10370 | F7
10371 | Make all code violation corrections prior to the re-inspection date noted on page 1 of the report.
10372 | Provide current audibility test documentation within the last 3 years for the fire alarm system.Test documentation must have one of two things to be acceptable. A) Must show each audibility device’s ambient decibel level and the decibel level when the device is active. The difference in DB level must fall within NFPA 72’s acceptable range for the device to pass the test. OR B) A document from their company on company’s letter head that has the following information – 1) Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all audibility devices passed the audibility test as required by NFPA 72.
10373 | Provide documentation for a current emergency egress light annual test.An approved licensed master electrician or licensed electrical service company shall test all emergency lighting systems annually. The battery units, whether of the acid or alkali type, shall be tested continuously for a minimum of 90 minutes.Failed devices shall be repaired or replaced as soon as possible. The test report / documentation shall have the date of the test, the master electrician, and/or company's certification number, and state that all devices passed the 90-minute test or if there were failed devices needing corrections.
10374 | Hydro test needed for FDC / standpipe. Systems must be tagged and report in binder
10375 | Kitchen ansul system needs semi annual inspection and tag. Report in binder
10376 | The existing fire lane must match the approved fire lane plans. Ensure that all curbs are painted red where required, and all signs are present in the right locations according to the fire lane plans. Also, within the red painted curbs the warning "FIRE LANE - TOW AWAY ZONE" shall be painted according to LSB 3.6.5.3.63.6.5.3.6 Marking of curbs:Curbs located between approved Fire Lane - Tow-Away Zone signs shall be painted RED or a RED stripe shall be placed along the pavement where there is no curb. These curbs shall also be conspicuously and legibly marked with the warning “FIRE LANE - TOW AWAY ZONE” in WHITE letters at least three (3) inches in height, at intervals not exceeding fifty (50) feet.Once the fire lane has been inspected and matches the approved plans, the inspecting code official will have it placed on the "Official Fire Lane List".
10377 | Information / Reminder:Ensure that at least 1/2 of all fire drills are of the obstructed type.
10378 | Gas leak test is needed.
10379 | The access gate needs a permit. Apply for access gate permit at City of Houston Permitting Center
10380 | Classroom doors in non-sprinkled "E" occupancies are classified as opening protectives and shall not be propped open with door stops / wedges to maintain the 1 hour fire rating of the egress corridor. Also, do not prop open corridor egress doors leading to stairwells. Classrooms in fully sprinkled building E is allowed to have door stops for classroom doors.
10381 | Renew the combustible waste permit.
10382 | Renew the assembly permit.
10383 | Keep fire Marshal’s Binder / Records Orderly. Remove old or expired copies. Remove duplicate copies. Keep old records in an archived binder or another location. Provide copies of all current life safety system test in the Fire Marshal’s Binder for review by the inspecting code official.
10384 | NoData
10385 | Met with Mrs. Maria Alam 02/22/21 on location for a complain on this location. While performing an Site Inspection with Mrs. Alam she informed me that she do have a plumbing Company on this location repairing their busted pipes due to the Winter Storm. While on location I called Mrs. Rosenna Alaniz @ 832-553-2159 the Originator of this complaint to get a clear understanding of this complaint, Mrs. Rosenna Informed me that this yellow/red tags is due to busted pipes from the Winter Storm once the ice melted the water entered the Alarm Panel shorting out the Panel and that Panel now need to be replaced. Mrs. Rosenna Informed me that her Company have present communicated with Mrs. Alam for bids to correct the Yellow/Red Tag by replacing the Alarm Panel.
10386 | NoData
10387 | NoData
10388 | NoData
10389 | NoData
10390 | NoData
10391 | NoData
10392 | NoData
10393 | NoData
10394 | NoData
10395 | NoData
10396 | Inspect and Service tag commercial kitchen hood system. Correct all red tag impairments immediately.
10397 | Provide certificate of flame resistance, it shall indicate the color for all decorative materials. 1. new curtains, new certificate or 2. new certificate showing retesting of flame resistance
10398 | Correct supervisory alert on fire alarm panel
10399 | Provide documentation/report for emergency light testing and all necessary repairs.
10400 | Provide documentation/report for fire damper testing and all necessary repairs.
10401 | Documentation required for the last intercom test. Performed within the last year.
10402 | Make all code violation corrections prior to the re-inspection date noted on page 1 of the report.
10403 | The annual fire alarm system test is required. Provide test documentation and a current annual blue inspection tag.
10404 | Provide current audibility test documentation within the last 3 years for the fire alarm system.Test documentation must have one of two things to be acceptable. A) Must show each audibility device’s ambient decibel level and the decibel level when the device is active. The difference in DB level must fall within NFPA 72’s acceptable range for the device to pass the test. OR B) A document from their company on company’s letter head that has the following information – 1) Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all audibility devices passed the audibility test as required by NFPA 72.
10405 | Provide documentation for a current emergency egress light annual test.An approved licensed master electrician or licensed electrical service company shall test all emergency lighting systems annually. The battery units, whether of the acid or alkali type, shall be tested continuously for a minimum of 90 minutes.Failed devices shall be repaired or replaced as soon as possible. The test report / documentation shall have the date of the test, the master electrician, and/or company's certification number, and state that all devices passed the 90-minute test or if there were failed devices needing corrections.
10406 | All fire extinguishers need an annual inspection / tag.
10407 | Check the fire extinguisher Hydrostatic test date log.Replace or test any fire extinguishers with a manufacturers date older than 2009, and update the fire extinguishers hydrostatic test log.
10408 | The kitchen ansul system needs the semi annual inspection
10409 | The class K extinguisher in the kitchen needs an annual inspection / tag.
10410 | Provide a door access key for the 911 Key box located by "Reserved Parking SEL Directors Sign" accessed from the faculty parking lot off Durham. The key that was in the 911 box didn't open the door.
10411 | The Fire Alarm Panel is showing trouble mode and must be repaired as soon as possible.
10412 | Provide sensitivity test for the fire alarm system
10413 | Provide a current Tx Certificate of operation for the Raypac Boiler #TX239769
10414 | Remove the overgrown vegetation that is growing into the electrical lines for the main building near the office entrance.
10415 | Keep fire Marshal’s Binder / Records Orderly. Remove old or expired copies. Remove duplicate copies. Keep old records in an archived binder or another location. Provide copies of all current life safety system test in the Fire Marshal’s Binder for review by the inspecting code official.
10416 | NoData
10417 | Extinguisher hidden, missed on last inspection - currently dated 5/19
10418 | NoData
10419 | Missing all grease filters. Inspection is past 6 months. Please replace all filters and have current inspection.
10420 | Missing spacer(s) in electrical panel
10421 | Extinguishers must be mounted and marked properly to easily identify
10422 | Extinguisher hidden on shelf. Please mount on back wall
10423 | Current 5yr gas test required
10424 | Current 5yr gas test required
10425 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs
10426 | Min. 36" in clearance must be maintained
10427 | NoData
10428 | NoData
10429 | NoData
10430 | Drop bar noted on one of the exit doors. Removed on site. Will follow up in 2 weeks to make sure exits remain clear during business hours.
10431 | It is the responsibility of the owner/person in charge to correct all violations.
10432 | NoData
10433 | Private fire hydrants are required to be tested every year by a qualified co.
10434 | All falcon locks where froze up and unable to be opened to test gates. Have gate co. replace falcon locks and test fire safety features (automatic function and failsafe function and pad locks) paint 911 boxes red.
10435 | NoData
10436 | Have a licensed fire protection company inspect and tag the fire extinguishers.
10437 | NoData
10438 | NoData
10439 | NoData
10440 | NoData
10441 | NoData
10442 | NoData
10443 | NoData
10444 | NoData
10445 | provide repairs to fire alarm listed on red tag dated 11/6/20.
10446 | Replace the inoperable rusted padlock with a replacement Knox or Falcon padlock.
10447 | Provide illuminated exit signs in the shop.
10448 | David Prez
10449 | FIRE ALARM STSYEM IS RED TAG AND FIRE SPRINKLER SYSTEM IS RED TAG. CORRECT BOTH SYSTEMS WITHIN 72 HOURS OF THIS NOTICE.
10450 | A NEW INSTALLATION TAG SHALL BE ATTACHED TO A NEW ALARM PANEL WHEN INSTALLED.
10451 | FIRE ALARM PANEL AND FIRE SPRINKLER SYSTEM SHALL BE MAINTAINED IN AN OPERATIVE CONDITION AT ALL TIMES AND SHALL BE REPLACED OR REPAIRED WHERE DEFECTIVE. BOTH FIRE ALARM PANEL AND FIRE SPRINKLER SYSTEM ARE RED TAGGED. THESE SYSTEMS SHALL BE CORRECTED WITHIN 72 HOURS OF THIS NOTICE.
10452 | CITATIONS WILL BE ISSUED WHEN ALL OTHER EFFORTS TO GAIN VOLUNATRY COMPLIANCE.
10453 | NoData
10454 | NoData
10455 | NoData
10456 | SEEK TECHNICAL ASSISTANCE PER ABOVE CODE TO CONFIRM WHATEVER FIRE PROTECTION NEEDS MAY BE NECESSARY TO MAKE THIS AREA OF BUILDING COMPLIANCE WITH ITS USE
10457 | NoData
10458 | NoData
10459 | NoData
10460 | NoData
10461 | NoData
10462 | NoData
10463 | NoData
10464 | NoData
10465 | NoData
10466 | NoData
10467 | NoData
10468 | NoData
10469 | NoData
10470 | No Violations found at the time of inspection.
10471 | Compliant:Fire Alarm 1/11/2021;Sprinkler 1/27/2021;Fire Extinguishers 11/2020
10472 | COMPLIANCE DATE: 30 CALENDAR DAYS
10473 | (k1) key box fire prevention permit is expired at this time. All up to date and current permits should be posted.
10474 | POST ALL ELEVATOR PERMITS AND INSPECTIONS TO ELEVATOR ACCORDING TO THIS CODE.
10475 | (k1) key box fire prevention permit is expired at this time. All up to date and current permits should be posted.
10476 | Label DOORS leading to roof hatch."ROOF ACCESS" OR "ROOF HATCH"
10477 | Post all up to date and current permits as required by this code.
10478 | Label DOORS leading to roof hatch."ROOF ACCESS" OR "ROOF HATCH"
10479 | Label DOORS leading to roof hatch."ROOF ACCESS" OR "ROOF HATCH"
10480 | Provide Documentation/Report and tag for the 5th Year FDC Hydrostatic test
10481 | NoData
10482 | NoData
10483 | NoData
10484 | NoData
10485 | NoData
10486 | NoData
10487 | NoData
10488 | NoData
10489 | Ensure all exit doors open outwards in the direction of egress travel.
10490 | As an assembly occupancy with an occupant load &gt;50 persons according to your Certificate of Occupancy:-Ensure that all exit doors are equipped with panic hardware with no additional locking devices except for at the main doors.See Report Item #3 for further requirements on locks at the main doors
10491 | Post the max occupant load, as indicated on your Certificate of Occupancy, near the main entry.
10492 | Only the main doors may have a keyed deadbolt in addition to the panic hardware meeting the following guidelines:1) It must be readily distinguishable as locked2) Place a sign on the door, in minimum 1" letters that reads: "This Door to Remain Unlocked When Building is Occupied"
10493 | AS PER CODELAST INSPECTION NOVEMBER 2018
10494 | LAST SPRINKLER RISER TEST---OCTOBER 2, 2018BRING UP TO CODE
10495 | LAST FIRE EXTINGUISHER INSPECTION---NOVEMBER 2018.BRING UP TO CODE
10496 | GASOLINE OR ANY FLAMMABLE LIQUIDS ARE NOT TO BE STORED INSIDE SCHOOL UNLESS IN APPROVED CABINETS
10497 | MISSING MULTIPLE FIRE EXTINGUISHER THROUGHOUT THE SCHOOL.REPLACE ALL MISSING FIRE EXTINGUISHER SOON AS POSSIBLE
10498 | ELEVATOR PERMIT EXPIRED 1ST QUARTER 2020BRING UP TO CODE
10499 | PLACE UPDATED PERMITS INSIDE FIRE MARSHAL BINDER
10500 | NoData
10501 | Please renew 911 Key Box (K1) and Access Gate (A4) permits which expired 2/1/20.
10502 | NoData
10503 | NoData
10504 | NoData
10505 | NoData
10506 | Renew permits, Access gate expired 1/7/21 and 911 Key Box 7/11/20.
10507 | NoData
10508 | Stairway's A & B on Floors 10,11,12 need to have stair side unlocked to enter the space.COMPLIANCE WITHIN 60 CALENDAR DAYS.
10509 | Mobility Impairment list needs to be updated every 6 months. (Last updated 4-6-2018.)Update Building Contacts list.COMPLIANCE WITHIN 60 CALENDAR DAYS.
10510 | Yellow Tag issues related to the Semi-Annual Test need to be identified and corrected.COMPLIANCE WITHIN 60 CALENDAR DAYS.
10511 | Fire Fighter phone Hand sets need to be checked. Units tested either did not function or were difficult to hear audio.Unable to located Fire Phone jacks on the Stair B side of the building. Have Fire Protection vendor Confirm if these connections are present. Provide a Technical Report on location and process to get the connections back in service.COMPLIANCE WITHIN 60 CALENDAR DAYS.
10512 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualFire Extinguishers- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
10513 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice.COMPLIANCE WITHIN 60 CALENDAR DAYS.
10514 | Garage Standpipe and Hose Cabinets are out of Service. Deficiencies need to be identified and system need to return to service ASAP.COMPLIANCE WITHIN 60 CALENDAR DAYS.
10515 | Floor # 3 Space entry doors that have mag locks are missing the City of Houston approval permit stickers that verify the system has been Permitted and approved. Contact Vendor that installed system and have them acquire the proper stickers.Building Department was contacted and system was permitted and approved.COMPLIANCE WITHIN 60 CALENDAR DAYS.
10516 | NoData
10517 | NoData
10518 | Floor plan has been submitted and approved.
10519 | GRB has an annual assembly permit
10520 | NoData
10521 | NoData
10522 | NoData
10523 | Owners responsiblity
10524 | Provide documentation showing compliance of emergency firefighting operation in every elevator located throughout condo community.
10525 | Provide documentation of compliant annual elevator inspections for all buildings in the condo community.
10526 | NoData
10527 | NoData
10528 | NoData
10529 | NoData
10530 | NoData
10531 | NoData
10532 | NoData
10533 | NoData
10534 | NoData
10535 | Do not decorate doors.
10536 | Fire alarm permit current. P2 permit not needed. Cancelled by inspector.
10537 | Compliance required within 60 calendar days Provide written action plan within 30 days for any items that cannot be corrected by the compliance date.
10538 | Maintain required celing clearance
10539 | Last gas test 5/29/19 - OK
10540 | Do not exceed the maximum allowable wall coverage
10541 | Provide instructions for fire alarm and intercom systems
10542 | Not due
10543 | Test dampers, correct deficiencies, and place report in binder
10544 | Last test 7/23/19 - OK
10545 | 9/29/19 - OK
10546 | Remove all curtains, drapes, fabrics, and 3D decorations that do not have FR certificates.
10547 | Last inspection 10/2019 - OK
10548 | New installation 3/15/2019 - OK
10549 | Drill log OK
10550 | Have egress lighting test performed, correct deficiencies, and place report in binder
10551 | Remove all combustible items currently stored in mechanical rooms.
10552 | Do not hang or display anything from ceilings.
10553 | Not due
10554 | 10/28/19 - Blue, OK
10555 | Last inspection 6/2019 HAVE ANSUL SYSTEM INSPECTED
10556 | Obstructed drills OK
10557 | 10/8/19 - Yellow Have all yellow tag conditions corrected
10558 | Place, "Roof Access" signs on all doors to rooms that contain roof access ladders.
10559 | Update evacuation maps. Maps must show separate perimeter doors for primary and secondary exits.
10560 | NoData
10561 | NoData
10562 | Provide exit signs.
10563 | Provide updated assembly permit. Attached is the permit renewal notice.
10564 | NoData
10565 | Provide documentation/report for audibility testing and all necessary repairs.
10566 | Provide documentation/report for emergency lighting system testing and all necessary repairs.
10567 | Provide documentation/report for fire damper testing and all necessary repairs.
10568 | Inspect and Service tag commercial kitchen hood system. Correct all red tag impairments immediately.Update: 2 Red Tags still need correction
10569 | Repair ventilation hoses for KILNS.
10570 | Provide certificate of flame resistance, it shall indicate the color for all decorative materials. 1. new curtains, new certificate or 2. new certificate showing retesting of flame resistanceUpdate: Black Curtain and Flags Certificate needed
10571 | NoData
10572 | NoData
10573 | Test report in binder is incomplete. Report must confirm audio and voice in each classroom.
10574 | Multiple lights failed during fire safety inspection. Have egress lighting tested and correct all deficiencies.
10575 | Compliance required within 60 calendar days. Update fire marshal binder (FMB). Use packet provided by inspector as a guide.
10576 | Label mechanical room door that leads to fire alarm panel.
10577 | Last sensitivity 3/24/17 - OK
10578 | Update extinguisher hydro log.
10579 | Replace missing ceiling tiles in second floor data room.
10580 | Last inspection 7/2018 HAVE ALL EXTINGUISHERS INSPECTED
10581 | Last audibility 12/9/17 - OK
10582 | Place boiler inspection and boiler operator permits in binder.
10583 | Last inspection 12/2018. HAVE ANSUL SYSTEM INSPECTED
10584 | Assembly, fire alarm, and fire lane permits not in binder. Update binder with required documentation
10585 | Update training log and place in binder.
10586 | Last gas test 6/13/18 - OK
10587 | Do not decorate doors.
10588 | Not enough obstructed drills documented. Obstruct at least half of all fire drills in 2019-2020.
10589 | Drills log OK.
10590 | Last inspection 1/2018 HAVE ALARM SYSTEM INSPECTED
10591 | Place curtain certificate in binder.
10592 | Do not exceed the maximum allowable wall coverage.
10593 | Do not hang anything from ceilings.
10594 | Some rooms are missing evacuation maps. Ensure that map design is consistent and that all rooms have evacuation maps.
10595 | Multiple fails documented in 6/22/18 test. Due for annual. Have system tested and document correction of all failures.
10596 | Supporting reference for requirement to add gate with panic hardware behind library.
10597 | P2 permit expires 2/6/20 - OK Fire alarm permit expires 10/27/19 - OK Fire Lane permit Project #10117531. Obtain copy and place in binder.
10598 | Maintain required ceiling clearance.
10599 | Training required annually. Keep documentation of training in Fire Marshal Binder
10600 | Place instructions for voice alarm/PA system in panel.
10601 | Supporting reference for requirement to add gate with panic hardware behind library. Fence is too close to allow for a safe dispersal area that is at least fifty feet from building. Unobstructed access to public way is required.
10602 | Last test 7/23/19 - OK
10603 | Inspector recommends that records of all employee safety training be in memo/letter form. The memo/letter should include the date, location, type of training received, whether any employees were absent from training, and the name & signature of the person conducting the training.
10604 | Label all buildings (including T-buildings) with designations listed on the Certificates of Occupancy.
10605 | Place "Roof Access" signs on doors to all rooms with roof access ladders.
10606 | Curtain certs issued 8/31/89 and 6/29/09.
10607 | Do not exceed the maximum allowable wall coverage.
10608 | Have all fire dampers tested and place report in binder. If any dampers fail, have them repaired.
10609 | Last drill 8/27/19 - OK
10610 | Boiler cert expires 10/27/19 - OK Update expired boiler operator permit
10611 | Do not decorate doors.
10612 | Compliance required within 60 calendar days.
10613 | Do not hang/suspend/display anything from ceilings.
10614 | Provide evacuation plan for inspector to review.
10615 | Per code.
10616 | New installation 7/12/18 Due for annual inspection
10617 | Last inspection 8/2018. Have all fire extinguishers inspected.
10618 | First sensitivity test due.
10619 | Obtain log from extinguisher company and place in binder.
10620 | Add one extinguisher to gym.
10621 | Yellow expanding foam in electrical rooms is not fire rated. Remove all yellow expanding foam and replace with an approved firestopping material.
10622 | Rear library exit continuity is interrupted by wrought iron fence. Install gate with panic hardware.
10623 | Evacuation maps are too broad. Update maps so that smaller portions of the school are shown.
10624 | Last gas test 6/20/17. OK, per fire code. State of Texas requires gas leak tests in schools to be conducted every two years.
10625 | Compliance required within 60 calendar days. Update fire marshal binder (FMB). Use packet provided by inspector as a guide.
10626 | Training required annually. Keep documentation of training in Fire Marshal Binder
10627 | Last test 6/29/18 - OK, but due this month.
10628 | Obtain FR certificates for all curtains and place in FMB.
10629 | FDC location is not obvious, and FDC sign isn't plainly visible. Relocate FDC sign so that it is closer to the street. Sign near driveway indicating FDC location may also be required.
10630 | Last inspection 6/2018 - YELLOW, NOT CORRECTED Have sprinkler system inspected and all yellow tag conditions corrected.
10631 | Have FDC hydro performed.
10632 | Drill log OK.
10633 | Have intercom system tested and place report in binder.
10634 | Assembly permit expired 4/23/18 Fire alarm permit expired 11/10/18 UPDATE EXPIRED PERMITS
10635 | Last gas test 7/9/18 - OK, but report/permit not in FMB.
10636 | Replace missing ceiling tile in library.
10637 | Provide instructions for fire alarm and intercom operation. Instructions must be located at the respective systems.
10638 | Last sensitivity 10/24/16 - OK
10639 | Fire/smoke dampers appear to be missing in wall cutouts for air balancing in mechanical rooms. Install dampers, or provide documentation that void/attic/horizontal flue space is 100% sprinklered.
10640 | Place log in fire marshal binder.
10641 | ANSUL system inspected 12/2018 - DUE
10642 | Inspector recommends that records of all employee safety training be in memo/letter form. The memo/letter should include the date, location, type of training received, whether any employees were absent from training, and the name & signature of the person conducting the training.
10643 | Pull station for ANSUL system in kitchen is blocked by metal shelving. Remove/relocate shelving.
10644 | Obstructed drills OK.
10645 | Do not exceed the maximum allowed wall coverage.
10646 | Have on-site fire hydrant flow tested and place report in FMB.
10647 | Evacuation maps are too broad. Update maps so that smaller sections of the school are shown.
10648 | Last inspection 2/2018 - DUE Have fire alarm system inspected.
10649 | Last audibility 9/16/17 - OK
10650 | Generator load bank report is out of date. Have new load bank performed and place report in FMB.
10651 | Last inspection 8/2018 - OK
10652 | Two certificates expire 7/12/19 One certificate expired 8/13/18 Boiler operator permits expired 12/31/18 Update all expired permits/certificates.
10653 | Do not hang or display anything from ceilings.
10654 | Maintain required ceiling clearance at all times.
10655 | Mount at least two additional extinguishers in library. Mount at least two extinguishers in gym.
10656 | Provide copy of emergency evacuation plan for inspector to review. Plan should include (at minimum) occupant notification procedure, evacuation procedure, refuge areas, and method for verifying that all occupants have exited the building.
10657 | Place permanent "Roof Access" signs on all mechanical rooms with stairs or ladders that lead to the roof.
10658 | Do not place decorative or teaching materials on doors. Windows (hallway and exterior) may be covered with metal blinds.
10659 | NoData
10660 | NoData
10661 | The owner/occupant shall be held responsible for thecorrection and abatement of all violations listed in this notice of violationsreport. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
10662 | Aisles must be kept according to the code paying special attention to keeping aisles clear of storage. Aislescannot be used for storage. Half of the aisle is always to remain clear at all times.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
10663 | The 911 key box, or Knox Box 3200 series hinged lid, shall be of an approvedtype listed in accordance with UL 1037, shall contain keys for immediateaccess for lifesaving or firefighting purposes, and be maintained in working condition at all times. Replace the rusted lock or the entire box according to LSB Standard 05.(SEE ATTACHED LSB STANDARD 05 FOR MORE INFORMATION.)COMPLIANCE:WITHIN 30 CALENDAR DAYS.
10664 | A minimumthree (3) inch transverse flue space and a minimum six (6) inch longitudinalflue space shall be maintained on high-piled double-row storage racks.FLUESPACES.Longitudinal flue space. The flue space between rows of storageperpendicular to the direction of loading.Transverse flue space. The space between rows of storage parallelto the direction of loading.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
10665 | NoData
10666 | NoData
10667 | NoData
10668 | Please renew Access Gate Permit (A4). Expired 2/7/21.
10669 | annual test needed for 2a:10bc fire extinguisher. Can be replace with 1a:10bc no annual test is needed for 1a:10bc fire extinguisher.
10670 | Luis Rojo 7137019857, inspection report is for 6819, 6825 and 6827 avenue c 77012.sign and return manager letter.
10671 | show copy of policy
10672 | test all smoke alarm and replace batteries as needed.
10673 | obtain or show proof current keybox permit. replace missing 911 falcon/knox lock. repair toggle switch or replace missing fob.
10674 | emergency lighting need repair 6825 corridor.
10675 | Permit Expired 2/6/2021, Unpaid Fees $267.53
10676 | NoData
10677 | NoData
10678 | NoData
10679 | NoData
10680 | NoData
10681 | NoData
10682 | NoData
10683 | NoData
10684 | NoData
10685 | NoData
10686 | NoData
10687 | NoData
10688 | NoData
10689 | NoData
10690 | NoData
10691 | NoData
10692 | NoData
10693 | NoData
10694 | NoData
10695 | NoData
10696 | NoData
10697 | NoData
10698 | NoData
10699 | NoData
10700 | NoData
10701 | NoData
10702 | NoData
10703 | NoData
10704 | Required to be tagged by a certified licensed fire protection technician.
10705 | Required two 4A 40BC extinguishers. Mounted.
10706 | Post or have readily available upon request the Certificate of Occupancy for this location.
10707 | Purchase and post the LPG Storage permit on location.
10708 | NO VIOLATIONS FOUND
10709 | NoData
10710 | NoData
10711 | NoData
10712 | NoData
10713 | NoData
10714 | NoData
10715 | NoData
10716 | NoData
10717 | NoData
10718 | NoData
10719 | NoData
10720 | NoData
10721 | NoData
10722 | NoData
10723 | NoData
10724 | NoData
10725 | NoData
10726 | NoData
10727 | NoData
10728 | NoData
10729 | NoData
10730 | NoData
10731 | NoData
10732 | NoData
10733 | NoData
10734 | NoData
10735 | NoData
10736 | NoData
10737 | NoData
10738 | NoData
10739 | NoData
10740 | NoData
10741 | NoData
10742 | NoData
10743 | NoData
10744 | NoData
10745 | NoData
10746 | NoData
10747 | NoData
10748 | NoData
10749 | NoData
10750 | NoData
10751 | NoData
10752 | NoData
10753 | NoData
10754 | NoData
10755 | NoData
10756 | NoData
10757 | 109.2 Owner/occupant responsibility. Correction and abatement of violations of this code shall be the responsibility of the owner. If an occupant creates, or allows to be created, hazardous conditions in violation of this code, the occupant shall be held responsible for the abatement of such hazardous conditions.
10758 | 3201.3 Construction documents. At the time of building permit application for new structures designed to accommodate high-piled storage or for requesting a change of occupancy/use, and at the time of application for a storage permit, plans and specifications shall be submitted for review and approval. In addition to the information required by the International Building Code, the storage permit submittal shall include the information specified in this section. Following approval of the plans, a copy of the approved plans shall be maintained on the premises in an approved location. The plans shall include the following: 1. Floor plan of the building showing locations and dimensions of high-piled storage areas. 2. Usable storage height for each storage area. 3. Number of tiers within each rack, if applicable. 4. Commodity clearance between top of storage and the sprinkler deflector for each storage arrangement. 5. Aisle dimensions between each storage array. 6. Maximum pile volume for each storage array. 7. Location and classification of commodities in accordance with Section 3203. 8. Location of commodities which are banded or encapsulated. 9. Location of required fire department access doors. 10. Type of fire suppression and fire detection systems. 11. Location of valves controlling the water supply of ceiling and in-rack sprinklers. 12. Type, location and specifications of smoke removal and curtain board systems. 13. Dimension and location of transverse and longitudinal flue spaces. 14. Additional information regarding required design features, commodities, storage arrangement and fire protection features within the high-piled storage area shall be provided at the time of permit, when required by the fire code official.Compliance: 30 calender days.
10759 | LSB2020.4.3.2.3.3.1 Electrically Powered GatesThe “9-1-1” Box is provided with an electrical switch (toggle or micro switch with button). Moving the toggle switch to the “Up” position will cause the gate to swing open towards the project or roll to a fully open position. The micro-switch will automatically activate once the hinged lid on the “9-1-1” Box is opened (see Appendix G). The gate shall remain open until the toggle switch is returned to its original position.Compliance: 30 calendar days.
10760 | 1011.6.2 Exit sign illumination. The face of an exit sign illuminated from an external source shall have an intensity of not less than 5 footcandles (54 lux).Compliance: 30 calendar days.
10761 | 105.3.5 Posting the permit. Issued permits shall be kept on the premises designated therein at all times and shall be readily available for inspection by the fire code official.Compliance: 30 calendar days.
10762 | NoData
10763 | NoData
10764 | NoData
10765 | NoData
10766 | NoData
10767 | NoData
10768 | NoData
10769 | Mount the class K fire extinguisher located on the ground in the kitchen area.
10770 | Correct the yellow tagged sprinkler deficiencies.
10771 | Repair or replace the inoperable emergency illumination.
10772 | Its the owner/occupant responsibility to correct all fire code violations.
10773 | Must remove, clean up, and organize combustibles in the second story loft up the stairs.
10774 | NoData
10775 | NoData
10776 | No storage allowed
10777 | 2A10 b/c: tag and inspected needs to be in your Boiler room
10778 | Smoke detector must be in the mechanical room
10779 | A gas test is required at your location make sure your plumber pull a permit from the city .
10780 | NoData
10781 | Repair or replace the inoperable emergency illumination on the exit signs.
10782 | Ensure the second exit in the dining area is unlocked while the building is occupied.
10783 | Have vent hoods cleaned by a professional cleaning service. Ensure date of cleaning sticker is placed on the vent hoods.
10784 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a gas test permit.
10785 | Renew the fire prevention assembly permit before the end of 02/2021.
10786 | remove all trash and rubbish such as trash bags, paper and boxes inside the garage shop and any other trash that would create a fire hazard
10787 | provide and install a metal can with a metal lid to store oily rags ,
10788 | service all fire extinguishers with a certified company and tag
10789 | remove all spilled waste oils on the pallets and ground area
10790 | NoData
10791 | NoData
10792 | NoData
10793 | apply for permit if storing more than 55gallons of waste oil at 1002 Washington fire permits section type tier (2)
10794 | Owner's responsibility. Comply with the above fire code.
10795 | The fire alarm panel is red tagged dated 3/9/2021. Have the fire alarm system serviced to achieve compliance status within 72 hours. The sprinkler system to the parking garage is red tagged. Have the sprinkler system serviced to achieve compliance status.Initiate a in house fire watch until both fire protection systems are returned to compliant status.In house fire watch assignment agreement form signed.
10796 | NoData
10797 | NoData
10798 | NoData
10799 | NoData
10800 | NoData
10801 | NoData
10802 | FYI the annual inspection for the fire extinguishers will be due at the end of April 2021.
10803 | FYI the annual inspection for the fire alarm panel will be due at the end of April 2021.
10804 | An emergency lighting test must be performed on the fire alarm system.
10805 | FYI the annual inspection for the sprinkler system will be due at the end of April 2021.
10806 | One red fire extinguisher must be placed inside of the kitchen and one must be placed inside of electrical room #S223.
10807 | All elevators must have an annual inspection performed on them.
10808 | NoData
10809 | NoData
10810 | NoData
10811 | NoData
10812 | NoData
10813 | NoData
10814 | NoData
10815 | NoData
10816 | NoData
10817 | NoData
10818 | NoData
10819 | NoData
10820 | NoData
10821 | NoData
10822 | NoData
10823 | NoData
10824 | NoData
10825 | NoData
10826 | NoData
10827 | NoData
10828 | NoData
10829 | Have a licensed fire protection company service and tag the fire extinguisher located in the breaker room.
10830 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a gas test permit.
10831 | Repair or replace the stand alone emergency lighting and the exit sign illumination.
10832 | Clear and maintain space in the breaker room.
10833 | Ensure the gates on the patio are unlocked while the building is occupied.
10834 | NoData
10835 | The business shall go through the process of completing the automatic fire sprinkler system and ensuring it has been approved and in working order.
10836 | The installation of the fire alarm system is to be completed. The business shall submit plans for their fire alarm system for approval through the building department. The business shall also provide a plan of action including dates of plan submittal, installation, and final completion to the fire code official. The plan of action may be revised as necessary.
10837 | The business shall obtain a Certificate of Occupancy by application through the Building Department.
10838 | The building is not to be occupied or open to the public without a fire watch from HFD inspectors per the Fire Marshal. After plan submittal, installation, and an approved fire alarm system is in working order, the fire watch may be discontinued. At NO time shall the basement level of the building be occupied (even with fire watch) until the building has an approved fire alarm system, approved automatic fire sprinkler system, and the building has been issued a Certificate of Occupancy.
10839 | NoData
10840 | NoData
10841 | NoData
10842 | Have a licensed fire protection company service and tag the class K fire extinguisher.
10843 | The vent hood suppression system is due for service before the end of 03/2021. Ensure a sticker with the date of vent hood cleaning is placed on the vent hood.
10844 | Remove hanging displays from the ceiling.
10845 | Remove the inoperable vent hood suppression pull station.
10846 | Repair or replace the emergency illumination.
10847 | Post the occupant load (125).
10848 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a gas test permit.
10849 | Ensure the side exit is unlocked while the building is occupied. Repair the hardware if necessary.
10850 | NoData
10851 | NoData
10852 | NoData
10853 | NoData
10854 | NoData
10855 | NoData
10856 | NoData
10857 | NoData
10858 | NoData
10859 | NoData
10860 | NoData
10861 | NoData
10862 | NoData
10863 | NoData
10864 | NoData
10865 | NoData
10866 | NoData
10867 | NoData
10868 | NoData
10869 | NoData
10870 | NoData
10871 | NoData
10872 | NoData
10873 | NoData
10874 | NoData
10875 | NoData
10876 | NoData
10877 | NoData
10878 | NoData
10879 | NoData
10880 | NoData
10881 | NoData
10882 | NoData
10883 | NoData
10884 | 3903 Sherwood Ln. key box (k1) permit has expired 02/2019.
10885 | NoData
10886 | NoData
10887 | NoData
10888 | NoData
10889 | I arrived on location to find 6 individual buildings in the apartment community. Three buildings have a red tagged fire alarm system and no water pressure in the sprinkler system. The remaining three buildings have no water pressure in the sprinkler system. I started an intervention form for an standby. I also initiated an in house fire watch agreement form.
10890 | NoData
10891 | NoData
10892 | Repair ASAP.
10893 | NoData
10894 | Please repair sprinkler system in 72 hours, maintain a fire watch on building #6 until all repairs are completed.
10895 | NoData
10896 | NoData
10897 | NoData
10898 | FIRE ALARM PERMIT EXPIRED 10-31-2019
10899 | NoData
10900 | NoData
10901 | NoData
10902 | The owner is responsible for correcting all violations and obtaining all permits.
10903 | Need to purchase a Hot Works permit for welding taking place at the business..
10904 | The address to obtain the required permits is as follows, Houston Permitting Center is 1002 Washington Avenue, Houston Tx., 77002. Phone number is 832-394-9000.
10905 | Need to purchase a Flammable/Combustible liquid permit for the container of waste oil located on business property.
10906 | NoData
10907 | FAILURE TO SERVICE FIRE EXTINGUISHER 7-18 AND FIRE ALARM PANEL- HAS TROUBLE LIGHT ON
10908 | NoData
10909 | FIRE PANEL NEED SERVICE. HAS TROUBLE SIGNAL. 6-17-2020
10910 | NEED SERVICE . 7-2018 LAST DATE
10911 | FAILURE TO SERVICE FIRE EXTINGUISHERS 9-19
10912 | NoData
10913 | NEED SERVICE. 9-19 LAST DATE
10914 | NoData
10915 | Facility has had a number of false alarms. In an attempt to keep facility safe for its occupants, facility management has hired a disinfecting company to keep facility cleanfrom possible germs and bacteria accumulation. Allis done in the interestof reducing possible Covid-19 transferor exposure. During the process, the disinfecting equipment has triggered accidentalautomatic alarms witch has caused an emergency response from emergency personnel. Moving forward, the Fire Alarm will be put in test mode while disinfecting process is initiated. There are no occupants during this process. Once the process is complete, the Fire Alarm panel will be put back in Normal Operating Mode. If nuisance alarms continue, facility will be issued a citation.
10916 | NoData
10917 | NoData
10918 | Repair the inoperable emergency illumination on the exit signs.
10919 | Ensure emergency fuel disconnect is properly installed and labeled.
10920 | Provide warning sign for fueling station.
10921 | Have a licensed fire protection company perform an annual inspection on the fire sprinkler system.
10922 | Provide a knox box mounted to the pole near your access gate like the your approved plans show with the keys to the facility in the box. Compliance by 3-5-2021
10923 | All doors leading into your high piled storage area shall have locks that are keyed the same. Repair all doors that will not open or the lock is malfunctioning. Compliance by 3-5-2021
10924 | Provide at least a 3ft. clearance around all electrical equipment.Compliance by 3-5-2021
10925 | Replace all missing or damaged ceiling tiles on the second floor and throughout the facility.Compliance by 3-5-2021
10926 | Have qualified fire door company perform annual drop test on all fire doors.Compliance by 3-5-2021
10927 | Have qualified fire sprinkler/ alarm company address all yellow tag issues and bring both systems into compliance.Have sprinkler company add the correct information on your hydraulic plates per NFPA 13 Figure A 24.5. (Info provided)Compliance by 3-5-2021
10928 | Have qualified fire extinguisher company mount extinguishers on all forklifts powered by fuel or propane and perform annual testing then appropriate tags.Have this company address your fire hose cabinets and service or remove.Compliance by 3-5-2021
10929 | All fire extinguishers shall be mounted from the hardware provide and not on floors or tables.Compliance by 3-5-2021
10930 | After bringing your warehouse back into compliance per your approved high piled plans, make sure that there are no dead end aisles.Compliance by 3-5-2021
10931 | Repair or replace all emergency lighting not working or broken in your facility and provide documentation that they are working at that time.Compliance by 3-5-2021
10932 | All doors leading into your high piled area shall have the letters HFD on the upper left hand corner on the outside of the doors per your approved plans.Compliance by 3-5-2021
10933 | Provide documentation from an approved alarm company that your large fans in your warehouse are wired to the fire alarm panel and will automatically shut off when the system goes into alarm.Compliance by 3-5-2021
10934 | Review your approved high piled floor plans and bring the warehouse back to the approved floor layout with aisle spacing.Compliance by 3-5-2021
10935 | Apply for a Lp-gas permit for the propane that you store on site. You can get this application on the City of Houston web page under fire permits.Compliance by 3-5-2021
10936 | All exits lights shall be illuminated.Compliance by 3-5-2021
10937 | NoData
10938 | Ensure exits are free from obstructions.
10939 | Have a licensed fire protection company perform an annual fire alarm inspection.
10940 | Provide FDC sign next to the FDC.
10941 | Obtain the following Fire prevention permits: Flammable liquids, Fuel dispense, LPG, Cryogenic fluids, Key box, Access gate.
10942 | Ensure exits are unlocked while the building is occupied.
10943 | NoData
10944 | 12/2020 - OK
10945 | 3/27/2020 - OK
10946 | 3/2021 - OK
10947 | 8/31/2020 - OK
10948 | 4/28/2020 - OK
10949 | Obstructed drills OK.
10950 | Monthly drills conducted. Log OK
10951 | 4/26/2018 - OK
10952 | Criminal Justice classroom layout blocks secondary egress from Cosmetology. Rearrange CJ classroom to ensure exit is never obstructed.
10953 | Correct all violations within 60 calendar days.
10954 | 1/3/2020 - Have fire alarm system inspected.
10955 | 4/15/2017 - Have audibility test performed and correct any deficiencies.
10956 | Table blocking ANSUL pull in culinary (enclosed room)
10957 | Remove hand sanitizer bottles from carpeted Cosmetology classroom, or remove carpet from classroom.
10958 | Replace missing ceiling tile in IT classroom.
10959 | Cosmetology maps show one exit for both routes. Update maps. Primary and secondary routes must use different exits (including hallways/corridors).
10960 | Add at least three "Roof Access" signs in Film & Photo leading to upstairs roof access ladder.
10961 | 6/12/2020 - Passed, but multiple batteries currently not working. Replace non-working batteries.
10962 | NoData
10963 | NoData
10964 | 10/28/2020 - YellowCorrected 12/17/2020 - OK
10965 | 3/2021 - OK
10966 | 8/31/2020 - OK
10967 | 4/30/2020 - OK
10968 | Obstructed drills OK.
10969 | Monthly drills conducted. Log OK
10970 | 3/24/2017 - OK
10971 | 5/1/2020 - OK
10972 | 10/2019 - Have all fire extinguishers inspected.
10973 | Remove all items stored in area between rooms 114 and 115 that obstruct access to exit door.
10974 | Correct all violations within 60 calendar days.
10975 | 12/9/2017 - Have audibility test performed and correct any deficiencies.
10976 | Remove brown, 3-outlet extension cord from upstairs library.
10977 | Maps in rooms 114 and 115 do not match actual primary and secondary egress routes used during evacuation. Update maps.
10978 | Remove fabric from all bulletin boards.Remove all 3D decorations.
10979 | NoData
10980 | NoData
10981 | The standpipe hose valves located on the occupant side of levels 44 and 45 need to comply with the above code and NFPA 14. The Horizontal standpipe system, hose valves and hose valve cabinets need to be approved by HFD plans checking.Compliance in 30 days.
10982 | NoData
10983 | NoData
10984 | NoData
10985 | Please visually inspect all draft stops for solid construction.
10986 | Last Gas Test - 02/18/2015Please has gas meter tested for leaks - HFS A2.1.1
10987 | Bring all fire exstiguishers up to current standard compliance.
10988 | Comply with IFC 2012 506.3 Install an Fire Depository Box
10989 | PERMIT REQUIRED PER ABOVE
10990 | NoData
10991 | NoData
10992 | NoData
10993 | NoData
10994 | NoData
10995 | FACP was repaired and back in service by Fire Professional Services on 03/13/21
10996 | NoData
10997 | A4,K1 permits are expired. Expired on 2/20/2021. Amount owed for permits 535.06 Please pay for permits within 10 days of this notice. If more information is needed about permits contact the Fire Prevention Permit Office.
10998 | NoData
10999 | NoData
11000 | NoData
11001 | NoData
11002 | remove all combustible materials such as old boxes, ,plastic trash containers and any other trash that would create a fire hazard
11003 | provide and install a small metal can with a metal lid for storage of oily rags
11004 | remove all waste oil on wood pallets and ground area that is creating a fire hazard
11005 | apply for a flammable and combustible liquids permit at 1002 Washington fire permit section if storing more than 55 gallons of waste oils combustible liquids.
11006 | NoData
11007 | Obtain and post Certificate of Occupancy [104.1(9)]
11008 | NoData
11009 | Have qualified gate company provide a manual pull switch on the access gate in the event of a power failure the gate can be manually opened.Compliance by 3-12-2021
11010 | Lower all plastic pails, totes, and bottles to 6 ft. or lower in the warehouse and maintain storage at this height until approved for high piled storage.Compliance by 3-12-2021
11011 | Provide stickers showing the direction and color coded product flowing through your outside piping coming form the tank farm.Compliance by 3-12-2021
11012 | Replace the faded 704 placards on your outside above ground storage tanks.Compliance by 3-12-2021
11013 | Submit a Hazardous Materials Inventory Statement using the guidelines provided.Compliance by 3-12-2021
11014 | Repair or replace all emergency lights in your facility that are not working and provide documentation that they have been tested and repaired if not working.Compliance by 3-12-2021
11015 | Have two knox box's installed on the side access gate and outside the far warehouse door with access keys to be placed inside during my follow up inspection. Information on the knox box will be provided.Compliance by 3-12-2021
11016 | Apply for a LP-Gas permit on the City of Houston web site under fire permit.Compliance by 3-12-2021
11017 | 9/2020 - OK
11018 | 7/9/2020 - Blue, OK
11019 | New installation 3/21/2018Voice evac system.
11020 | No ANSUL system. C of O issued under 1972 codes. Inspector unable to find reference to whether or not kitchen hood suppression system is required. Completed C of O implies that no suppression system is required, but this may change after more code research.
11021 | 9/18/2020 - OK
11022 | 6/4/2019 - OK
11023 | Obstructed drills OK.
11024 | Drills conducted monthly. Log OK.
11025 | 7/17/2020 - OK
11026 | Add two extinguishers to cafeteria.
11027 | Correct all violations within 60 calendar days.
11028 | Remove all fabric from bulletin boards.Remove all 3D decorationsRemove black sheets/curtains from back of stage.
11029 | Fire extinguisher found to be on the floor but was placed back on appropriate bracket.
11030 | It is the responsibility of the owner/person in charge to correct all violations.
11031 | Owner's responsibility. Comply with the above fire code.
11032 | The fire alarm system has been red tagged dated 3./8/2021.The sprinkler system has also been red tagged and have no water pressure.Have the fire alarm and sprinkler systems repaired to compliant status.A continuous in house fire watch shall be implemented 24 hours 7 days a week until both systems have been repaired.Sign Fire Watch Assignment Agreement form.
11033 | NoData
11034 | NoData
11035 | Shane (license #2283835) with Texas Fire Pros contacted me today and advised the FACU has been "red tagged". The FACU is no longer communicating with the monitoring company and will not alert locally at this time. This occupancy has a Certificate of Occupancy and is required to maintain the fire protection systems in working condition at all times. Contact a licensed fire protection company to repair or replace the inoperable system. Within 72 hours a plan of action must be submitted to the Fire Inspector. A TEMPORARY in house fire watch will be established on 03/16/21 at 1300 hrs. The temporary in house fire watch will continue until the FACU is repaired/replaced/properly tagged, the building is evacuated, or it is upgraded to a Fire Marshal's standby.
11036 | Shane (license #2283835) with Texas Fire Pros contacted me today and advised the FACU has been "red tagged". The FACU is no longer communicating with the monitoring company and will not alert locally at this time. This occupancy has a Certificate of Occupancy and is required to maintain the fire protection systems in working condition at all times. Contact a licensed fire protection company to repair or replace the inoperable system. Within 72 hours a plan of action must be submitted to the Fire Inspector. A TEMPORARY in house fire watch will be established on 03/16/21 at 1300 hrs. The temporary in house fire watch will continue until the FACU is repaired/replaced/properly tagged, the building is evacuated, or it is upgraded to a Fire Marshal's standby.
11037 | 8/2020 - OK
11038 | 4/28/2020 - REDCorrected 5/8/2020 - OK
11039 | 9/28/2020 - OK
11040 | 8/6/2020 - YELLOWCorrected 12/21/2020 - OK
11041 | 7/24/2020 - Blue, OK
11042 | 3/2021 - OK
11043 | 8/31/2020 - OK
11044 | 3/7/2020 - OK
11045 | Obstructed drills OK
11046 | Monthly drills conducted. February missed due to freeze. Log OK.
11047 | 10/24/2016 - OK
11048 | 5/1/2020 - OK
11049 | Add extinguishers to the following locations:+2 - Library+2 - Cafeteris+2 Gym
11050 | Correct all violations within 60 calendar days.
11051 | 9/16/2017 - Have audibility performed and correct any deficiencies.
11052 | Have annual flow test performed on private hydrants. Provide results for residual PSI test performed within the last 5 years.
11053 | Arrived on scene to find the fire alarm and sprinkler system red tagged as of January 2021.I issued 72 hours Notice to have both fire systems returned to compliance or to provide a plan of action. I notified management to initiate a 24 hours fire watch of the entire complex until the fire systems are returned to compliance status.Visited location on 2/8/2021 to find fire alarm panel had been replaced. A white service tag is attached dated 2/6/2021 replacing the red tag dated 11/25/2020.
11054 | Exposed wiring in Wood Shop where clock used to be needs cover plate.
11055 | Light fixtures must be protected with covers or plastic sleeves. - Light cover needed in the weight room storage area- Light cover needed in room under stairway- Protect exposed light fixtures in the Garage
11056 | Areas of refuge (including classroom / other when used in a lockdown / intruder situation, fire drill, shelter in place, etc.), must have some form of communication system or device(s) that are working order. Testing of such devices should be done on an annual basis.Such devices may be in the form of cell phones, two-way hand-held radios, an overhead built in intercom system, or hard-wired telephones in every room normally occupied by students.Provide dated documentation on school letterhead stating the type of devices that the school uses for drills of all types, and that all devices have been tested and all are in proper working condition.
11057 | Provide documentation for a current emergency egress light annual test.An approved licensed master electrician or licensed electrical service company shall test all emergency lighting systems annually. The battery units, whether of the acid or alkali type, shall be tested continuously for a minimum of 90 minutes.Failed devices shall be repaired or replaced as soon as possible. The test report / documentation shall have the date of the test, the master electrician, and/or company's certification number, and state that all devices passed the 90-minute test or if there were failed devices needing corrections.
11058 | Skybox Room" located on the second floor by the elevator room has excessive storage that is not orderly, has not distinguishable egress paths, and is blocking the exit doors from the room. - Remove excessive fire load storage- Make sure storage is orderly and stable- Keep minimum of 3ft wide distinguishable egress paths clear from obstruction- maintain storage height at least 24" below the ceiling.
11059 | Maintain minimum storage height below ceilings as stated in the above code.
11060 | Remove combustible storage from all electrical, mechanical, and boilers rooms. Also includes the elevator room.
11061 | The lighting balcony has many code violations in regards to multiplug adapters, power tap / strips, and extension cords. Multiplug adapters / power strips must be UL 1363 approved (stamped) and meet NFPA 70. - Remove any unapproved plugs / strips/ etc. that do not have some type of UL 1363 notation on it. Power strips must plug directly into a fixed / permanent wall outlet and cannot be daisy chained (plugged into each other). - Do not plug a power strip or multiplug adapter into another power strip or multiplug adapter. - Remove any extension cords that have multiplug female ends. - Remove any extension cords that are attached or affixed to permanent lighting fixtures that are being used as permanent wiring.
11062 | The lighting balcony has many code violations in regards to multiplug adapters, power tap / strips, and extension cords. Multiplug adapters / power strips must be UL 1363 approved (stamped) and meet NFPA 70. - Remove any unapproved plugs / strips/ etc. that do not have some type of UL 1363 notation on it. Power strips must plug directly into a fixed / permanent wall outlet and cannot be daisy chained (plugged into each other). - Do not plug a power strip or multiplug adapter into another power strip or multiplug adapter. - Remove any extension cords that have multiplug female ends. - Remove any extension cords that are attached or affixed to permanent lighting fixtures that are being used as permanent wiring.
11063 | The lighting balcony has many code violations in regards to multiplug adapters, power tap / strips, and extension cords. Multiplug adapters / power strips must be UL 1363 approved (stamped) and meet NFPA 70. - Remove any unapproved plugs / strips/ etc. that do not have some type of UL 1363 notation on it. Power strips must plug directly into a fixed / permanent wall outlet and cannot be daisy chained (plugged into each other). - Do not plug a power strip or multiplug adapter into another power strip or multiplug adapter. - Remove any extension cords that have multiplug female ends. - Remove any extension cords that are attached or affixed to permanent lighting fixtures that are being used as permanent wiring.
11064 | The lighting balcony has many code violations in regards to multiplug adapters, power tap / strips, and extension cords. Multiplug adapters / power strips must be UL 1363 approved (stamped) and meet NFPA 70. - Remove any unapproved plugs / strips/ etc. that do not have some type of UL 1363 notation on it. Power strips must plug directly into a fixed / permanent wall outlet and cannot be daisy chained (plugged into each other). - Do not plug a power strip or multiplug adapter into another power strip or multiplug adapter. - Remove any extension cords that have multiplug female ends. - Remove any extension cords that are attached or affixed to permanent lighting fixtures that are being used as permanent wiring.
11065 | The lighting balcony has many code violations in regards to multiplug adapters, power tap / strips, and extension cords. Multiplug adapters / power strips must be UL 1363 approved (stamped) and meet NFPA 70. - Remove any unapproved plugs / strips/ etc. that do not have some type of UL 1363 notation on it. Power strips must plug directly into a fixed / permanent wall outlet and cannot be daisy chained (plugged into each other). - Do not plug a power strip or multiplug adapter into another power strip or multiplug adapter. - Remove any extension cords that have multiplug female ends. - Remove any extension cords that are attached or affixed to permanent lighting fixtures that are being used as permanent wiring. The Ampacity of the extension cords that are allowed to be used and are not of permanent wiring shall not be less than the portable appliance supplied by the cord.
11066 | The lighting balcony has many code violations in regards to multiplug adapters, power tap / strips, and extension cords. Multiplug adapters / power strips must be UL 1363 approved (stamped) and meet NFPA 70. - Remove any unapproved plugs / strips/ etc. that do not have some type of UL 1363 notation on it. Power strips must plug directly into a fixed / permanent wall outlet and cannot be daisy chained (plugged into each other). - Do not plug a power strip or multiplug adapter into another power strip or multiplug adapter. - Remove any extension cords that have multiplug female ends. - Remove any extension cords that are attached or affixed to permanent lighting fixtures that are being used as permanent wiring. The Ampacity of the extension cords that are allowed to be used and are not of permanent wiring shall not be less than the portable appliance supplied by the cord.
11067 | The lighting balcony has many code violations in regards to multiplug adapters, power tap / strips, and extension cords. Multiplug adapters / power strips must be UL 1363 approved (stamped) and meet NFPA 70. - Remove any unapproved plugs / strips/ etc. that do not have some type of UL 1363 notation on it. Power strips must plug directly into a fixed / permanent wall outlet and cannot be daisy chained (plugged into each other). - Do not plug a power strip or multiplug adapter into another power strip or multiplug adapter. - Remove any extension cords that have multiplug female ends. - Remove any extension cords that are attached or affixed to permanent lighting fixtures that are being used as permanent wiring. The Ampacity of the extension cords that are allowed to be used and are not of permanent wiring shall not be less than the portable appliance supplied by the cord.
11068 | Fire rated caulk is needed where any pipe or conduit enters the wall or ceiling tile. Fire rated caulk is needed where the walls touch the ceilings (any gaps found). Provide fire rated caulk as noted above in all the following areas throughout the building:- Weight room / fill gaps above the electrical boxes where conduit enters the ceiling- Wood Shop / electrical conduit into ceilingCeiling tile replaced or put back in position:- I7 / Hallway ceiling tile replaced- I4 Janitors Closet
11069 | No hanging decorations are allowed from tile ceilings:- West hallway (floor 1) near room 213- Also in room 214Maintain throughout whole school wherever found.
11070 | Update the master fire drill log and use documentation that shows obstructed / non-obstructed drills. At least 1/2 of all monthly fire drills shall be of the obstructed type.
11071 | Provide documentation for a gas leak test permitted by the City of Houston
11072 | The boiler must be certified with TDLR (Texas Department of Licensing and Registration). Contact TDLR for the steps necessary to get the boiler licensed.
11073 | Make sure the current Elevator Permit is available. Permit should be posted within 10ft of elevator call buttons.
11074 | Renew the expired Assembly Permit / P2 that expired on 7/18/20
11075 | The scope of the inspection.
11076 | Keep fire Marshal’s Binder / Records Orderly. Remove old or expired copies. Remove duplicate copies. Keep old records in an archived binder or another location. Provide copies of all current life safety system test in the Fire Marshal’s Binder for review by the inspecting code official.
11077 | NoData
11078 | NEED CURRENT ANNUAL INSPECTION ON FIRE EXTINGUISHERS
11079 | KEEP ALL EXIT DOORS ACCESSIBLE AT ALL TIMES
11080 | NEED TO REVIEW COPY OF APPROVD PLANS THAT WERE SUBMITTED TO CITY FOR HIGH PILE STORAGE APPROVAL. KEEP A SET ON SITE FOR FUTURE VISITS BY CODE OFFICIALS.
11081 | MOVE DUMPSTER 10FT MIN FROM BUILDING
11082 | KEEP STORAGE CLEAR OF ELECTRICAL EQUIPMENT PER ABOVE CODE
11083 | NoData
11084 | P2 permit expired
11085 | Provide Electrical Spacers (one in each room) for the 3rd floor and 2nd floor Electrical Room Panels.
11086 | 1) Provide and maintain visibility of Fire Extinguisher inside Garage Storage Room. 2) Replace missing Fire Hose/Fire Extinguisher Sign for 2nd floor Cabinet adjacent to Stair "B").
11087 | NoData
11088 | Replace or Repair ground floor Emergency Light (Stair "A").
11089 | Provide bright Red Paint for Key Box.
11090 | Provide current update for the Emergency Contact List and the Mobility Impaired List.
11091 | Provide Electrical Room sign for 2nd floor east side Electrical Room.
11092 | 1) Provide repair for holes on wall ( sheetrock) inside Fire Command Room. 2) Maintain closure of ceiling access panel inside 2nd floor Janitor Closet.
11093 | Throughout Property.
11094 | Provide Current Annual Key Box Permit.
11095 | NoData
11096 | NoData
11097 | NoData
11098 | NoData
11099 | 24" clearance must be maintained between ceiling and combustible materials (Non-sprinkled building)
11100 | Building identification needs to be clearly marked and legible from main street side
11101 | Commercial Kitchen hood requires minimum 6-MONTH inspection for buisness operations. Last performed: 4/19
11102 | Commercial Kitchen hood has excessive grease buildup, requires cleaning
11103 | Proof of current 5 year gas test required to be on site
11104 | Plumber must pull permit prior to performing gas test to be acceptable
11105 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs. Illumination for power outage not adequate
11106 | Obtain and post Certificate of Occupancy [104.1(9)]. Current yellow application receipt also acceptable
11107 | Lint removal behind dryer must be done daily
11108 | Flammable fuel needs to be put in a flammable cabinet
11109 | Fail-safe needed on gates
11110 | label fuse boxes with number and straps on doors
11111 | Need cover plates on all electrical sockets that are missing or damage .
11112 | All sheet rock that's damage are missing needs to be replaced .
11113 | Need to be placed on the entrance gate
11114 | They need to be put in place
11115 | All permits must be on location
11116 | Need at the entrance gate with lights .
11117 | Remove security grill
11118 | Both permits expire on March 20, 2021. The store manager, Kelly H. Thomas, is aware of the pending expiration and has notified corporate to renew both permits.
11119 | It is the owner/occupants responsibility to correct any fire code violations and make sure all fire permits are current. This storage facility has eight buildings. Buildings 1-7 are considered S1 occupancies and building 8 is the living quarters/office which is considered a R2 occupancy.
11120 | Ensure exits are unlocked while the building is occupied.
11121 | Limited spraying spaces shall comply with sections 2404.9.1 through 2404.9.4 or spray booth will need to be brought up to code.
11122 | Internally illuminated exit signs are required to be UL924 compliant.
11123 | Ensure exits are clear of obstructions.
11124 | Proper ventilation is required.
11125 | Limited spraying spaces shall comply with sections 2404.9.1 through 2404.9.4 or spray booth will need to be brought up to code.
11126 | Limited spraying spaces shall comply with sections 2404.9.1 through 2404.9.4 or spray booth will need to be brought up to code.
11127 | Limited spraying spaces shall comply with sections 2404.9.1 through 2404.9.4 or spray booth will need to be brought up to code.
11128 | Limited spraying spaces shall comply with sections 2404.9.1 through 2404.9.4 or spray booth will need to be brought up to code.
11129 | Internally illuminated exit signs are required to be UL924 compliant.
11130 | remove all wear out old tires that are creating a fire hazard nuisance .
11131 | remove all use tires that are creating a fire hazard for the public residence located also in the rear next to the waste old tire storage
11132 | Arrived on scene to find the fire alarm and sprinkler system red tagged as of January 2021.I issued 72 hours Notice to have both fire systems returned to compliance or to provide a plan of action. I notified management to initiate a 24 hours fire watch of the entire complex until the fire systems are returned to compliance status.Visited location on 2/8/2021 to find fire alarm panel had been replaced. A white service tag is attached dated 2/6/2021 replacing the red tag dated 11/25/2020. Visited location on 3/16 2021 to find the fire alarm and sprinkler systems had been repaired with white service tags replacing the red tags that were attached. Both system as 3/16/2021 are compliant, supporting documentation and photos are attached. The in house fire watch may be discontinue as of 3/16/2021.
11133 | NoData
11134 | NoData
11135 | NoData
11136 | NoData
11137 | NoData
11138 | NoData
11139 | NoData
11140 | NoData
11141 | NoData
11142 | NoData
11143 | NoData
11144 | NoData
11145 | NoData
11146 | annual test needed for 2:10bc fire extinguisher. can be replace with 1a:10bc no annual tested is need for 1a:10bc fire extinguisher
11147 | Luis rojo 7137019857, inspection report is for 6819, 6825, 6827 avenue c. sign and return manager letter.
11148 | show copy of policy
11149 | test all smoke alarm and replace batteries as needed.
11150 | obtain or show proof of current keybox permit. replace missing 911 falcon/knox lock. repair toggle switch or replace missing fob.
11151 | NoData
11152 | NoData
11153 | NoData
11154 | No violations found at this time.
11155 | NoData
11156 | NoData
11157 | NoData
11158 | Renew Public Assembly Permit within 10 Business days.
11159 | NoData
11160 | PLEASE RE-NEW "OPEN FLAMES / CANDLES" PERMIT WITHIN 10 BUSINESS DAY ... BY 01/17/20 COH - PERMIT OFFICE 1002 WASHINGTON AVE. HOUSTON, TX 77002
11161 | PLEASE RE-NEW "PUBLIC ASSEMBLY" PERMIT WITHIN 10 BUSINESS DAY ... BY 01/17/20 COH - PERMIT OFFICE 1002 WASHINGTON AVE. HOUSTON, TX 77002
11162 | Renew Public Assembly Permit within 10 Business days
11163 | NoData
11164 | PLEASE RE-NEW "OPEN FLAMES / CANDLES" PERMIT WITHIN 10 BUSINESS DAY ... BY 01/17/20 COH - PERMIT OFFICE 1002 WASHINGTON AVE. HOUSTON, TX 77002
11165 | PLEASE RE-NEW "PUBLIC ASSEMBLY" PERMIT WITHIN 10 BUSINESS DAY ... BY 01/17/20 COH - PERMIT OFFICE 1002 WASHINGTON AVE. HOUSTON, TX 77002
11166 | NoData
11167 | PLEASE RE-NEW "OPEN FLAMES / CANDLES" PERMIT WITHIN 10 BUSINESS DAY ... BY 01/17/20 COH - PERMIT OFFICE 1002 WASHINGTON AVE. HOUSTON, TX 77002
11168 | PLEASE RE-NEW "PUBLIC ASSEMBLY" PERMIT WITHIN 10 BUSINESS DAY ... BY 01/17/20 COH - PERMIT OFFICE 1002 WASHINGTON AVE. HOUSTON, TX 77002
11169 | NoData
11170 | Have all Fire Extinguishers serviced, and provide with current service tags.
11171 | Have Kitchen Fire Suppression / Ansul System serviced, and provided with a current service tag. System must be serviced every 6 months.
11172 | Have Certificate of Occupancy posted near Main Entrance of Business
11173 | Have "EXIT" @ Main entrance serviced, ensuring back-up power is available.
11174 | NoData
11175 | NoData
11176 | NoData
11177 | NoData
11178 | NoData
11179 | NoData
11180 | NoData
11181 | Sharla WilliamsNO VIOLATIONS FOUND AT THIS TIME.
11182 | UP TO DATE: 3/2021
11183 | UP TO DATE: 3/2021
11184 | Provide annual test and service tag for fire alarm system.
11185 | Provide annual test and service tag for sprinkler system.
11186 | Provide signage "Sprinkler Riser" on back door
11187 | NoData
11188 | NoData
11189 | NoData
11190 | NoData
11191 | NoData
11192 | NoData
11193 | Compliance: Immediately.
11194 | NoData
11195 | Compliance: 30 calendar days.
11196 | Compliance: 30 calendar days.
11197 | Compliance: 30 calendar days.
11198 | NO VIOLATIONS TO FACILITY AT THIS TIME. ALL FIRE PREVENTIVE MEASURES ARE IN PLACE.
11199 | NoData
11200 | NoData
11201 | NoData
11202 | Have all fire extinguishers inspected and tested. The most recent service tag is dated March 2019. Must be done annually.
11203 | Have the fire alarm system inspected and tested. Most recent tag is dated 9/23/16. Must be done annually. Repair any impairments that would cause a yellow or red tag.
11204 | Have the FDC inspected and tested. Did not find tag related to inspection and test. If performed within the past 5 years, inspection and testing does not need to be performed, but proof of this service must be provided. Repair any impairments that would render a yellow or red tag.
11205 | Have the kitchen suppression system inspected and tested. Most recent tag is dated March 2019. Must be done every 6 months. Repair any impairments that would cause a yellow or red tag.
11206 | Have the Class K fire extinguisher inspected and tested. Most recent tag is dated March 2019. Must be done annually.
11207 | Have the fire pump inspected and tested. Most recent tag is dated January 2020. Must be done annually. Repair any impairments that would render a yellow or red tag.
11208 | NoData
11209 | NoData
11210 | NoData
11211 | RE-ENTRY CALL BOXES MUST BE PROPERLY OPERATIONAL TO ALLOW ENTRY AND IDENTIFICATION AT ANY TIME
11212 | REPAIR GARAGE STANDPIPES
11213 | ENSURE ROOF ACCESS IS PROPERLY LABELED
11214 | ENSURE ALL KEYS ON ALL SETS ARE FUNCTIONAL AND PROPERLY LABELED.MOBILITY IMPAIRED LIST MUST BE UPDATED EVERY 6 MONTHS.ENSURE MAPS ARE PROPERLY LABELED IN ACCORDANCE WITH LSB 6 SECTION 6.3.6
11215 | CORRECT ALL OPEN ELECTRIC/ELECTRONIC PANELS AND JUNCTION BOXES
11216 | ENSURE ALL PENETRATIONS TO MECHANICAL/ELECTRICAL ROOMS ARE PROPERLY SEALED
11217 | COORECT ALL MALFUNCTIONING STAIRWAY DOORS
11218 | MAKE REQUIRED REPAIRS TO RETURN GARAGE STAND PIPE TO FULL SERVICE. REMOVE HOSES FROM NONOPERATIONAL STANDPIPE AND LABEL OUT OF SERVICE UNTIL REPAIRS ARE COMPLETED.
11219 | REMOVE UNAPPROVED LOCK FROM GARAGE 911 KEY BOX AND REPLACE WITH APPROVED LOCK
11220 | ENSURE ALL STAIRWAY SIGNS HAVE CORRECT INFORMATION AND APPEAR IN ACCORDANCE WITH APPENDIX H
11221 | ENSURE ALL EXIT SIGNS IN BUILDING AND GARAGE ARE PROPERLY ILLUMINATED
11222 | NoData
11223 | NoData
11224 | APPROVED CONSTRUCTION DOCUMENTS BY THE HAZMAT HIGH-PILED TEAM INCLUDING FINAL ON-SITE MUST BE PRESENTED BY THE FACILITY ON OR BEFORE THE DATE OF 02/10/2020. FACILITY WAS NOTIFIED TO OBTAIN THE APPROVED PLANS ON 02/01/2017 AND HAS NOT ACOMPLISHED THE REQUEST. IF THE FACILITY FAILS TO PRESENT APPROVED PLANS BY THE SET DATE THE PROCESS OF LOWERING I-IV COMMODITIES BELOW TWELVE FEET AND HIGH HAZARD COMMODITIES BELOW SIX FEET MUST BEGIN IMMEDIATELY AFTER 02/10/2020.
11225 | PLANS SHALL BE SUBMITTED TO THE BUILDING DEPARTMENT AND THE HAZMAT/HIGH-PILED STORAGE TEAM FOR REVIEW AND APPROVAL FOR THE FACILITY TO BE ALLOWED TO STORE HAZARDOUS MATERIAL ABOVE THE MAXIMUM ALLOWABLE QUANTITY. ACQUIRING THE EXPERTISE OF A FIRE PROTECTION ENGINEER FOR THIS PROCESS IS ADVISABLE. PLANS SHALL BE RE-SUBMITTED WITHIN 30 CALENDAR DAYS. WITHOUT APPROVAL BY THE HAZMAT/HIGH-PILED TEAM, ANOTHER OPTION IS FOR ALL HAZARDOUS MATERIAL QUANTITIES TO BE LOWERED BELOW MAXIMUM ALLOWABLE QUANTITIES. COMPLIANCE FOR LOWERING QUANTITIES TO WITHIN ACCEPTABLE LIMITS IS EXPECTED WITHIN 30 CALENDAR DAYS IF THIS OPTION IS DETERMINED TO BE ACCEPTED.
11226 | A COPY OF THE CERTIFICATE OF OCCUPANCY SHALL BE POSTED ON SITE. COMPLIANCE: 30 CALENDAR DAYS
11227 | CURRENT FIRE PERMITS SHALL BE POSTED ON SITE. COMPLIANCE: 30 CALENDAR DAYS
11228 | A SPRINKLER EVALUATION SHALL BE PROVIDED IN ORDER TO DETERMINE WHETHER THE PRODUCTS STORED ON THE PREMISES ARE ADEQUATELY PROTECTED BY THE CURRENT CONFIGURATION. THE CITY OF HOUSTON REQUIRES THAT SAID EVALUATION BE CONDUCTED BY A MINIMUM NICET LEVEL III TECHNICIAN OR A LICENSED FIRE PROTECTION ENGINEER. COMPLIANCE: 30 CALENDAR DAYS.
11229 | THE FIRE EXTINGUISHERS ON THE FUEL POWERED FORKLIFTS SHALL BE INSPECTED ANNUALLY. COMPLIANCE: 30 CALENDAR DAYS
11230 | REPAIR / REPLACE ANY EXIT SIGN NOT WORKING. COMPLIANCE: 30 CALENDAR DAYS
11231 | PLANS SHALL BE SUBMITTED TO THE BUILDING DEPARTMENT AND THE HAZMAT/HIGH-PILED STORAGE TEAM FOR REVIEW AND APPROVAL FOR THE FACILITY TO BE ALLOWED TO STORE CLASS I-IV COMMODITIES ABOVE 12 FT. IN HEIGHT IN AN AREA GREATER THAN 2500 SQ.FT. OR HIGH-HAZARD COMMODITIES OVER 6 FT. IN HEIGHT IN AN AREA GREATER THAN 500 SQ. FT. ACQUIRING THE EXPERTISE OF A FIRE PROTECTION ENGINEER FOR THIS PROCESS IS ADVISABLE. IF THIS OPTION IS ACCEPTED COMPLIANCE IS EXPECTED WITHIN 90 DAYS. WITHOUT APPROVAL BY THE HAZMAT/HIGH-PILED TEAM, ANOTHER OPTION IS FOR ALL CLASS I-IV COMMODITIES TO BE LOWERED AND MAINTAINED AT A HEIGHT OF NO MORE THAN 12 FT. AND HIGH-HAZARD COMMODITIES AT A HEIGHT OF NO MORE THAN 6 FT. IT SHOULD BE NOTED THAT THE HOUSTON FIRE CODE DOES ALLOW UP TO 2500 SQ. FT. IN TOTAL AREA OF COMBUSTIBLE I-IV COMMODITIES AND 500 SQ. FT. IN TOTAL ARE OF HIGH-HAZARD COMMODITIES IN BUILDINGS WITH AN APPROVED SPRINKLER SYSTEM. COMPLIANCE FOR LOWERING COMMODITIES TO WITHIN ACCEPTABLE LIMITS IS EXPECTED WITHIN 30 CALENDAR DAYS IF THIS OPTION IS DETERMINED TO BE ACCEPTED. SEE ATTACHED DOCUMENT CONTAINING DETAILS FOR THE PLAN SUBMITTAL PROCESS.
11232 | USING THE FORMAT PROVIDED, A CURRENT HMIS STATEMENT SHALL BE SUBMITTED TO THE HAZMAT/HIGH-PILED TEAM FOR REVIEW. THE HMIS FORM AND INSTRUCTIONS ON HOW TO FILL OUT THE FORM CAN BE FOUND AT THE CITY OF HOUSTON WEB SITE HTTP://WWW.HOUSTONTX.GOV/FIRE/FORMS/HMIS COMPLIANCE: 30 CALENDAR DAYS.
11233 | An approved automatic extinguishing system is required on the spray booth.
11234 | NoData
11235 | NoData
11236 | Plans are required to be submitted to the building department.
11237 | Submit plans to the building department.
11238 | Submit plans to the building department.
11239 | NoData
11240 | NoData
11241 | NoData
11242 | NoData
11243 | Fire dept. unable to gain access to hydrant. Hydrant needs to be accessed from street. Fence around hydrant leaving a minimum 3 foot clearance.
11244 | Manual gate near bldg. 11 needs new falcon lock and key to pad lock for 911 box. Manual gate near bldg. 12 needs key for padlock and another 911 box installed on inside of gate with key to pad lock (Fire trucks unable to turn around and must exit this gate). Automatic gate near bldg. 2 needs new failsafe lock and key for 911 box. This gate needs to be widened the width of the driveway. Fire trucks unable to access due to sharp turn and narrow gate. Main gate needs new falcon lock and two new pad locks for failsafes. Repair failsafe on exit side.Paint all boxes red and lube all locks
11245 | NoData
11246 | SEVERAL REMINDERS AND EXTRA TIME ALLOWED TO PAY FOR b1 PERMIT; STILL REMAINS UNPAID. ADD RE-INSPECTION FEE AND MUST BE PAID IN 10 DAYS
11247 | NoData
11248 | NoData
11249 | NoData
11250 | NoData
11251 | NoData
11252 | NoData
11253 | K1 permit is expired. Expired on 2/20/2021. Amount owed for permit 267.53 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
11254 | Have a licensed fire protection company service and tag the extinguisher located on the welding apparatus.
11255 | Repair the emergency illumination located on the exit sign at the shipping entrance.
11256 | Obtain and post the following permits from the Houston Permitting Center located at 1002 Washington Ave. Houston, TX. : Access gate, Key box, and Industrial oven permit. In addition, obtain the Cryogenic liquid permit or move the container outside.
11257 | NoData
11258 | NoData
11259 | NEED TO ADD A (LOCK OUT/ TAG OUT KIT) TO EVERY ELEVATOR ROOM
11260 | Need installation tag on fire pump
11261 | NEED A 911BOX AT FRONT ENTRY, ALL STAIRWELL (STREET ENTRIES), ALL SUITS (BUSINESS), AND GARAGE DOOR ACCESS.
11262 | NEED MORE OBVIOUS ADDRESS ON BUILDING
11263 | NEED TO SETUP THE FIRE DEPOSITORY BOX AS PER LSB STANDARD 6.NEED TO GET A PERMIT FOR THE KEY BOXES (K1)
11264 | NoData
11265 | NoData
11266 | NoData
11267 | Have a licensed fire protection company perform an annual fire sprinkler inspection and correct any deficiencies.
11268 | Have a licensed fire protection company perform a 5 year FDC test and correct any deficiencies.
11269 | NoData
11270 | NoData
11271 | NoData
11272 | NoData
11273 | F7 permit expired
11274 | alarm 7/20; extinguisher 1/20
11275 | fire extinguishers expired last tested Jan 2020
11276 | NoData
11277 | Must place "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED" on the two glass doors missing the sign.
11278 | Remove all combustibles materials such as wood, paper, and plastics from inside the electrical/water heater room.
11279 | Must label "Electrical Room" on the door leading into the main electrical room.
11280 | Must have a gas test performed by a licensed plumber at least every 5 years. Last gas test performed in 2013. The licensed plumber must obtain a gas test permit prior to performing the gas test from the City of Houston Permitting Center.
11281 | The owner/occupant is responsible for correcting all fire code violations and renewing all expired permits prior to follow up inspection.
11282 | The red portable fire extinguisher must have a current inspection tag that details when the inspection took place. Move the red portable fire extinguisher that is in the front of the restaurant and more toward the middle of the restaurant. There is too much separation between that fire extinguisher and the other side of the restaurant.
11283 | Must have a gas test permit prior to performing the gas test. A gas test permit can be purchased from the City of Houston Permitting Center.
11284 | The ANSUL commercial kitchen hood suppression system must have an inspection tag of when the system was inspected. Also the kitchen vent hoods, exhaust ducts, exhaust fans, and all appurtenances shall be cleaned and inspected by approved personnel and in accordance with manufacturer's guidelines, as often as necessary to insure against excess grease accumulations. Currently there is excess grease accumulation at this time which can pose a fire danger.
11285 | The silver class K portable fire extinguisher must have a current inspection tag that indicates when it was inspected.
11286 | NoData
11287 | NoData
11288 | remove all combustible materials such as old boxes, ,plastic trash containers and any other trash that would create a fire hazard
11289 | provide and install a small metal can with a metal lid for storage of oily rags
11290 | remove all waste oil on wood pallets and ground area that is creating a fire hazard
11291 | apply for a flammable and combustible liquids permit at 1002 Washington fire permit section if storing more than 55 gallons of waste oils combustible liquids.
11292 | NoData
11293 | Must place approved spacers inside the electrical panels that have open breakers.
11294 | Test and repair all exit signs and emergency lights that need repair.
11295 | This is the location where the Public Assembly Permit and the Gas test permit will be obtained.
11296 | Must renew the expired P2/Public Assembly permit prior to my follow up inspection.
11297 | NoData
11298 | NoData
11299 | NoData
11300 | NoData
11301 | NoData
11302 | NoData
11303 | NoData
11304 | NoData
11305 | NoData
11306 | NoData
11307 | Repair the inoperable emergency illumination on the exit signs.
11308 | Obtain a flammable liquids permits for the diesel fuel in the generator. Obtain an access gate permit and a key box permit or lock and chain the access gates in the open position. Permits can be obtained at the Houston Permitting Center at 1002 Washington Ave. Houston TX.
11309 | Show proof that Fire hydrants have had annual inspections.
11310 | Need failsafe pins in all automatic swing gates.
11311 | Need hydrant signs on gates indicating number of hydrants inside property.
11312 | Need key box and access gate permits.
11313 | Label boiler room.
11314 | Information only.
11315 | NoData
11316 | NoData
11317 | NoData
11318 | NoData
11319 | Renew Public Assembly Permit within 10 Business days
11320 | NoData
11321 | NoData
11322 | NoData
11323 | NoData
11324 | NoData
11325 | NoData
11326 | NoData
11327 | Portable Fire Extinguisher(s) annual maintenance Dt: 3/21
11328 | Annual Fire alarm test Dt: 2/4/21
11329 | Annual Sprinkler system (wet) test Dt: 2/5/21
11330 | 5-year hydro/flow test Dt: 7/21/16
11331 | NoData
11332 | No missing spacers allowed in electrical panels
11333 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs
11334 | Fire protection equipment must be identified, please add permanent labeling for "Riser Room"
11335 | NoData
11336 | NoData
11337 | NoData
11338 | NoData
11339 | NoData
11340 | NoData
11341 | NoData
11342 | NoData
11343 | NoData
11344 | NoData
11345 | NoData
11346 | NoData
11347 | NoData
11348 | NoData
11349 | NoData
11350 | NoData
11351 | Firetron is currently making repairs to the system.
11352 | NoData
11353 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
11354 | NoData
11355 | NoData
11356 | NoData
11357 | NoData
11358 | secure lpg gas container mounted on fork lift with matel straps that are provide for the lpg container in order to keep it secured in case of fire and possibly injuring fire fighters and any personnel
11359 | repair all emergency lights that are not working as well as all electrical exit sign also
11360 | provide metal chains or other approve device to keep compress gas bottles use for cutting and welding from falling down and injuring any personnel ,plus replace missing metal caps to keep values from breaking if they were to fall down and going through metal and brick walls like sky rockets due to heavy gas compress pressure.
11361 | remove all plastic gas containers and replace with an approved u,l or f.m listed metal gas container for storing gasoline under (5) gallons inside of garage shop or apply for a flammable liquid permit if storing more than (5)gallons in an approved storage metal cabinet.
11362 | NoData
11363 | NoData
11364 | NoData
11365 | provide and install a metal insert that is missing inside main electrical box where a breaker is missing or use to be to prevent an electrical sock while using other other breakers
11366 | check all exit lite signs to assure that they are in working conditions
11367 | NoData
11368 | provide and install a plain exit sign on exit door with no sign to I.D.
11369 | NoData
11370 | remove all combustibles such as plastics ,paper boxes lumber ,wood and any other combustible trash away from rear electrical panels
11371 | apply for a cutting and welding permit from fire permit section 1002 washington
11372 | apply for the storage of flammable and combustible liquids storage permit for waste oil or transmission over 60 gallons or reduce to one (55) gallon barrel at 1002 Washington permits section
11373 | provide and install sign on middle part of exit doors
11374 | NoData
11375 | NoData
11376 | alarm 7/20; extinguisher 1/20
11377 | fire extinguishers expired last tested Jan 2020
11378 | NoData
11379 | NoData
11380 | Please have the chain removed on the fire department access gate located on the furthest south gate off Hollister. Provide access for 911 emergencies. Provide a key to be placed in 911 box. Secure the 911 box with a Fire Dept. Falcon Lock. Which can be purchased by access control gate companies. Contact a professional gate company for code compliance
11381 | NoData
11382 | NoData
11383 | Please renew Access Gate (A4) and Key Box (K1) permits. Both permits expired 1/25/21.
11384 | Check all units to make sure that the smoke alarms are in the required areas.
11385 | Smoke detectors are required in every room used for sleeping and in the hallway immediately outside any room used for sleeping.
11386 | Spacers are missing in the electrical panels
11387 | Audit each apartment unit and ensure that all smoke detectors are the required locations.
11388 | Natural Gas Test is required every 5 years.
11389 | NoData
11390 | PROVIDE SOME CLEAR AISLES IN WAREHOUSE 3 NEAR THE DEAD END AISLES. COMPLIANCE WITHIN 30 DAYS.
11391 | DUMPSTER SHALL BE MOVED A MINIMUM OF 10 FEET AWAY FROM BUILDING OPENINGS. COMPLIANCE WITHIN 30 DAYS.
11392 | PROVIDE A TURN AROUND OR WALK THROUGH AT THE END OF ALL AISLES THAT ARE 50 FEET OR GREATER IN LENGTH IN WAREHOUSE 3 AND THROUGHOUT THE FACILITY. COMPLIANCE WITHIN 30 DAYS.
11393 | COMPLIANCE WITHIN 30 DAYS.
11394 | REPAIR OR REPLACE ALL EXIT LIGHTS NOT ILLUMINATED THROUGHOUT YOUR FACILITY. COMPLIANCE WITHIN 30 DAYS.
11395 | REMOVE ALL PALLETS AND OTHER OBJECTS BLOCKING ACCESS TO ALL EGRESS DOORS IN THE REAR OF WAREHOUSE 3 AND THROUGHOUT YOUR FACILITY. IMMEDIATE COMPLIANCE REQUIRED.
11396 | HAVE AN APPROVED ALARM COMPANY PERFORM ANNUAL INSPECTION ON ALARM PANEL. IMMEDIATE COMPLIANCE REQUIRED.
11397 | PROVIDE A APPROVED FACE PLATE FOR ALL OPEN ELECTRICAL ON WAREHOUSE POLES AND THROUGHOUT THE WAREHOUSE AND OFFICE AREA. COMPLIANCE WITHIN 30 DAYS. OPEN ELECTRICAL IN WAREHOUSE 3 THAT WAS POINTED OUT DURING GENERAL INSPECTION SHALL BE COVERED BY 2-27-2014.
11398 | PROVIDE A COPY OF APPROVED PLANS AND MAINTAIN THOSE PLANS ON SITE AT ALL TIMES. IMMEDIATE COMPLIANCE REQUIRED.
11399 | MOVE ALL EMPTY PALLETS DOWN TO 6 FEET MAX. COMPLIANCE WITHIN 30 DAYS.
11400 | REPAIR OR REPLACE ALL EMERGENCY EXIT LIGHTS THROUGHOUT YOUR FACILITY. COMPLIANCE WITHIN 30 DAYS.
11401 | APPLY FOR LP-GAS PERMIT AT 1002 WASHINGTON AVE. COMPLIANCE WITHIN 30 DAYS.
11402 | AN APPROVED FIRE DOOR COMPANY SHALL PROVIDE THE ANNUAL DROP TEST ON ALL FIRE DOORS IN THE WAREHOUSE. COMPLIANCE WITHIN 30 DAYS.
11403 | NEED TO ADD A (LOCK OUT/ TAG OUT KIT) TO EVERY ELEVATOR ROOM
11404 | Need installation tag on fire pump
11405 | NEED A 911BOX AT FRONT ENTRY, ALL STAIRWELL (STREET ENTRIES), ALL SUITS (BUSINESS), AND GARAGE DOOR ACCESS.
11406 | NEED MORE OBVIOUS ADDRESS ON BUILDING
11407 | NEED TO SETUP THE FIRE DEPOSITORY BOX AS PER LSB STANDARD 6.NEED TO GET A PERMIT FOR THE KEY BOXES (K1)
11408 | Please renew the K1, key box permit.Expired 2/28/2021.
11409 | NoData
11410 | Ensure SDS forms are available on site or accessible on the internet. Fill out the HMIS.
11411 | Replace the rusted, inoperable padlock on the key box with a Knox padlock or Falcon padlock.
11412 | Ensure excess flammable liquids are stored correctly.
11413 | Provide a protected enclosure for spare LPG cylinders.
11414 | Repair or replace inoperable emergency illumination on the exit signs.
11415 | Ensure SDS forms are available on site or accessible on the internet. Fill out the HMIS.
11416 | Renew the expired Hot works and flammable liquids permits. Obtain a cryogenic liquids permit. Obtain an LPG permit or limit amount of storage to <125 Water Gallons per building.
11417 | Ensure exits are unlocked (from the egress side) while the building is occupied.
11418 | NoData
11419 | Make all required repairs to the fire protection systems. Maintain current 24hr self-fire watch.
11420 | NoData
11421 | MOVE ALL EMPTY PALLETS DOWN TO 6 FEET MAX. COMPLIANCE WITHIN 30 DAYS.
11422 | REPAIR OR REPLACE ALL EMERGENCY EXIT LIGHTS THROUGHOUT YOUR FACILITY. COMPLIANCE WITHIN 30 DAYS.
11423 | PROVIDE A COPY OF APPROVED PLANS AND MAINTAIN THOSE PLANS ON SITE AT ALL TIMES. IMMEDIATE COMPLIANCE REQUIRED.
11424 | APPLY FOR LP-GAS PERMIT AT 1002 WASHINGTON AVE. COMPLIANCE WITHIN 30 DAYS.
11425 | AN APPROVED FIRE DOOR COMPANY SHALL PROVIDE THE ANNUAL DROP TEST ON ALL FIRE DOORS IN THE WAREHOUSE. COMPLIANCE WITHIN 30 DAYS.
11426 | NoData
11427 | Remove dumpster/skid blocking access gates for fire department access.
11428 | Fail-safes on all access gates need to be repaired.
11429 | Continue fire watch for buildings affected with sprinkler piping damage
11430 | NoData
11431 | NoData
11432 | Please renew the A4, access gate permit.Expired 11/16/2020.
11433 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
11434 | Owner's responsibility. Comply with the above fire code.
11435 | The fire alarm and sprinkler systems to the entire apartment community is non compliant with IFC.The fire alarm systems has been red tagged to all 5 buildings dated 9/30/2020.The sprinkler systems are inoperable to buildings 1, 2, 4 and 5 of apartment community.The parking garage standpipe system in building 2 is red tagged.Have the fire protection systems in entire apartment community repaired immediately to achieve compliant status.Initiate a 24 hrs. 7 days in house fire watch until the fire protection systems ( F/A and Sprinkler) have attained a compliance status. The Fire Marshal's office may alter fire watch agreement at their discretion.Fire watch assignment agreement signed.
11436 | Please renew the A4, access gate permit.Expired 2/23/2021.
11437 | NoData
11438 | NoData
11439 | NoData
11440 | NoData
11441 | Electrical Boxes: 1. Electrical panel/box and rooms shall be visibly, legibly and durably marked as required in this section to indicate the unit it services. 2012 I.F.C. 605.3.1
11442 | NoData
11443 | All shrubs must be cleared 3 ft. away from all electrical panels.
11444 | Dead Fronts: Repair or replace dead front cover plates as required by the electrical code. 1. Repair or replace exposed wiring and illegal taps as required by the electrical code. 2. Contact the City of Houston Building Department in regard to any electrical code requirement and permitting questions.
11445 | Draft Stops: 1. Draft stops shall be provided and maintained as required. Draft stops shall be spot checked in accordance with your normal inspection procedures. When draft stops have been altered, damaged, breached or penetrated the notice of violation should include instructions to have a responsible contractor inspect all draft stops in the complex and itemize repairs made for each building and include a statement on their letterhead that all draft stops have been inspected and have been repaired or replaced to the required fire-resistance-rated construction required in accordance with the Houston Fire and Building Codes. (Note: At the very least they are required to obtain a repair permit thru one stop at Building Department) Occupancies in Group R-2 that do not exceed four stories in height, the attic space shall be subdivided by draft stops into areas not exceeding 3,000 square feet or above every two dwelling units, whichever is smaller. Provide site map or blue prints indicating the location of the attic access and the draft stops. Attic access shall be provided for the follow up inspection. Draft stops have been provided and shall be maintained as required. Doors have been provided in the draft stops for access, these doors are required to be closed at all times, if doors do not stay in the closed positions repairs or replacement shall be made.
11446 | Please place inside key box a copy of the master lock key that unlocks manual pull release.
11447 | please remove all extra storage and lint from room located behind dryers.
11448 | NoData
11449 | Hydrant Signs: 1. All-weather 18" X 18" H.F.D. signs shall be provided as per this section. 2. For complexes without any fire hydrants, the number "0" shall be placed under the letters HFD
11450 | NoData
11451 | NoData
11452 | NoData
11453 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
11454 | The Fire Alarms in each building Annual Inspection tag is out of date by more than a year. Perform the Fire Alarm Annual Inspection as required by code.
11455 | Make Repairs to the Fire Alarm SystemMaintain Self-Fire Watch until the repairs are made and the fire alarm system is back in service.
11456 | Fire alarm panel shows trouble. Correct trouble issues.
11457 | Make sure all emergency lights are working. Found one in stairway and near room 312 not working.
11458 | NoData
11459 | NoData
11460 | NoData
11461 | NoData
11462 | NoData
11463 | NoData
11464 | NoData
11465 | NoData
11466 | NoData
11467 | Have a licensed fire protection company perform an annual inspection on the fire alarm.
11468 | Have a licensed fire protection company perform an annual inspection on the fire sprinkler system.
11469 | A fail safe is required on the access gates.
11470 | Provide a switch in the key box that will open the access gate.
11471 | Repair the inoperable emergency illumination on the exit signs.
11472 | Ensure SDS are readily available on site or on the internet. Fill out and return the HMIS form.
11473 | Obtain a Hot works permit, and an LPG permit at the Houston Permitting Center located at 1002 Washington Ave. Houston TX. A compressed gas permit isn't required for the amount stored/used on the property.
11474 | NoData
11475 | NoData
11476 | NoData
11477 | NoData
11478 | NoData
11479 | NoData
11480 | NoData
11481 | NoData
11482 | NoData
11483 | NoData
11484 | NoData
11485 | NoData
11486 | NoData
11487 | NoData
11488 | NoData
11489 | NoData
11490 | NoData
11491 | NoData
11492 | NoData
11493 | NoData
11494 | NoData
11495 | NoData
11496 | Exit signs in Tommy's, café 54 and level 21 by stair B are not illuminated. Correct per code.Compliance in 60 days.
11497 | Mount fire extinguisher per code.
11498 | Exit signs in Tommy's, café 54 and level 21 by stair B are not illuminated. Correct per code.Compliance in 60 days.
11499 | Provide a compliance letter from the buildings fire alarm contractor if building has wired communication and is not required to have radio coverage. If building does not have an existing wired communication system then the building is required to be equipped with emergency responder radio coverage per code.
11500 | Have fire extinguisher inspected per code.
11501 | Lower storage height in kitchen per code.
11502 | This is a 72 hour notice to correct the restricted re-entry doors in stairway A and B. The phones need to dial a constantly attended station that is able to unlock the doors. IF after 72 hours the doors are not corrected they will be unlocked and remain unlocked until re-entry has been corrected per code.
11503 | Add 704 diamond to the gate leading to the generator room.
11504 | Provide secondary containment for all diesel fuel per code.
11505 | Update the 4 binders to make a total of 5. Ensure the mobility impaired lists are updated.Compliance in 60 days.
11506 | Add the swipe cards to the key sets per code. Check master key on key rings. Key did not work on level 15 electrical room.Compliance in 60 days.
11507 | Remove multiplug adapter per code.
11508 | Return the above locations to their fire resistance rating per code.
11509 | Correct the fire doors on level 9B and Level 6B so they close and latch from the open position per code.
11510 | Add test connection sign to the roof level standpipe connection per code.
11511 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriateinspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualEmergency radio coverage- AnnualFire Extinguishers- AnnualDry pipe partial- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualDry pipe full- 3 YearFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearClean agent – Semi-annualKitchen Hood System- Semi-annualBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
11512 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. • Present Permits that apply to facility Address listed • on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS.
11513 | NoData
11514 | Amount Due: $267.53
11515 | Amount Due: $267.53
11516 | NoData
11517 | NoData
11518 | Owner's responsibility. Comply with the above fire code.
11519 | 911 Key box is required outside of the main entrance (front door) as per COH - LSB Standard # 5.
11520 | Sprinkler heads busted at the home plate entrance of the diamond lot.2 domestics water lines in Union Station1- hose line at the left field gate. All repairs have been made
11521 | H3 permit is expired. Expired on 2/26/2021. Amount owed 267.53 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
11522 | repaired is needed for multiple sensor problem due to the freeze. Spoke to manager Ashley and Jeff Roberson 7144929308, they are aware of the problem and have schedule for repair.
11523 | NoData
11524 | NoData
11525 | NoData
11526 | It is the owner/occupants responsibility to correct all violations. Reinspection fees or citations can be issued if the violations are not corrected prior to the follow up date.
11527 | Spare LPG cylinders are not allowed to be stored inside the occupancy. Remove the cage/cylinders and ensure it is located at least 10 feet from a building opening.
11528 | The exit sign above the front door did not properly illuminate under battery back up power when tested. Repair or replace the exit sign so that it is properly illuminated under battery back up power in case of a loss of power to the building.
11529 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
11530 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES. KEEPEMERGENCY EVAC PLANS UPDATED AND TRAIN QUARTERLY.
11531 | NoData
11532 | NoData
11533 | NoData
11534 | NoData
11535 | Please renew Access Gate and Key Box Permits, both have expired.
11536 | Please renew Access Gate permit, expired 2/27/21.
11537 | NoData
11538 | P2 permit is expired. Expired on 12/17/2020. Amount owed for permit 266.80 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
11539 | ALL FIRE EXTINGUISHERS NEED TO BE MOUNTED
11540 | ALL EXIT SIGNS NEED TO BE ILLUMINATED
11541 | FIRE PUMP NEEDS SERVICED AND TAGGED
11542 | NEED TO UPDATE ALL 5 SETS OF KEYS
11543 | NoData
11544 | Ensure all fire extinguishers have a current service tag from a licensed fire protection company. Fire extinguishers are required to be serviced annually.
11545 | Ensure the fire extinguishers are properly hung using a wall mount, and are mounted with the bottom being a minimum of 4 inches off the floor, and the top being at a max height of 5 feet off the floor.
11546 | Discontinue all open burning.
11547 | Ensure all electronic access gates, both swinging and sliding, have a 911 box with a toggle switch or micro switch that allows for electronic access to the premises by emergency crews. Ensure the front sliding gate has a manual fail safe box that will allow for emergency crews to gain access to the premises in the event a power failure does not allow the gate to open electronically. The locks found on the existing 911 boxes are acceptable locks.
11548 | NoData
11549 | Replace the missing fire extinguisher in the office and provide one extinguisher in the second floor break room. Both extinguishers should have a minimum rating of 2:A 10:BC.
11550 | The following permit must be obtained through the Houston Permitting Center at: 1002 Washington Ave Houston, Tx 77002 832-394-8811 A4 - access gate permit for one (1) gate
11551 | Keys to allow HFD to access the gates and facility must be placed inside the 911 key box for life-safety emergencies.The locks to 911 key box must be serviced or replaced.Gates must be maintained and operable to allow HFD personnel access to the facility.Compliance within 30 days.
11552 | Exit sign must serviced and operableCompliance within 30 days.
11553 | Keys to allow HFD to access the gates and facility must be placed inside the 911 key box for life-safety emergencies.The locks to 911 key box must be serviced or replaced.Gates must be maintained and operable to allow HFD personnel access to the facility. Compliance within 30 days.
11554 | ENSURE A CURRENT EMERGENCY PLAN IS MAINTAINED ON THE PREMISES AT ALL TIMES.COMPLIANCE WITHIN 30 DAYS.
11555 | THE REQUIRED FIRE-RESISTANCE RATING OF FIRE-RESISTANCE-RATED CONSTRUCTION SHALL BE MAINTAINED. SUCH ELEMENTS SHALL BE PROPERLY REPAIRED, RESTORED OR REPLACED WHEN DAMAGED, ALTERED, BREACHED OR PENETRATED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
11556 | NoData
11557 | NoData
11558 | NoData
11559 | NoData
11560 | NoData
11561 | NoData
11562 | NoData
11563 | NoData
11564 | NoData
11565 | NoData
11566 | NoData
11567 | NoData
11568 | NoData
11569 | NoData
11570 | NoData
11571 | NoData
11572 | NoData
11573 | NoData
11574 | NoData
11575 | NoData
11576 | NoData
11577 | NoData
11578 | NoData
11579 | NoData
11580 | NoData
11581 | NoData
11582 | NoData
11583 | NoData
11584 | NoData
11585 | NoData
11586 | NoData
11587 | NoData
11588 | NoData
11589 | NoData
11590 | NoData
11591 | NoData
11592 | NoData
11593 | NoData
11594 | NoData
11595 | NoData
11596 | NoData
11597 | NoData
11598 | NoData
11599 | NoData
11600 | NoData
11601 | NoData
11602 | MAKE SURE ALL PORTABLE FIRE EXTINGUISHERS HAVE A CURRENT INSPECTION TAG ON THEM
11603 | MAKE SURE BOTH THE LEFT AND RIGHT SIDE ENTRANCE/EXIT DOORS REMAIN UNLOCKED DURING BUSINESS HOURS
11604 | MAKE SURE YOU KEEP A 24 INCH CEILING CLEARANCE IN THE BACK STORAGE ROOM
11605 | LABEL THE DOOR WITH THE ELECTRICAL PANELS IN THE "ELECTRICA PANELS INSIDE"
11606 | INSTALL SPACERS INSIDE OF OPEN SPACES IN THE ELECTRICAL BOX WITH MISSING SWITCHES
11607 | MAKE SURE ALL PORTABLE FIRE EXTINGUISHERS ARE NOT OBSTRUCTED BY ANY OBSTICLES. ALL PORTABLE FIRE EXTINGUISHERS SHOULD BE EASY TO ACCESS
11608 | PUT A SIGN ON THE ENTRANCE EXIT DOOR THAT READS "THESE DOORS MUST REMAIN UNLOCKED DURING BUSINESS HOURS"
11609 | MAKE SURE ALL EMERGENCY EGRESS LIGHTS ARE WORKING PROPERLY IN CASE OF POWER OUTAGE OR POWER FAILURE
11610 | RENEW THE M3(FUEL DISPENSER) PERMIT AT 1002 WASHINGTON AVE. 832-394-8811
11611 | NoData
11612 | NoData
11613 | NoData
11614 | NoData
11615 | NoData
11616 | NoData
11617 | NoData
11618 | NoData
11619 | MAKE SURE ALL PORTABLE FIRE EXTINGUISHERS HAVE A CURRENT INSPECTION TAG ON THEM
11620 | REPLACE BOTH OF THE MISSING PORTABLE FIRE EXTINGUISHERS AT THE FUEL PUMPS
11621 | MOUNT THE TYPE "K" PORTABLE FIRE EXTINGUISHER IN THE KITCEN AREA AND DO NOT HAVE IT FREE STANDING ON THE KITCHEN FLOOR
11622 | DISCONTINUE USING A LOCK BAR DURING BUSINESS HOURS
11623 | REMOVE ALL OBSTRUCTIONS FROM IN FRONT OF THE MAIN ENTRANCE/EXIT DOOR
11624 | MAKE SURE BOTH THE LEFT AND RIGHT SIDE DOORS REMAIN UNLOCKED DURING BUSINESS HOURS
11625 | DO NOT USE THE KITCHEN UNTIL THE KITCHEN SUPPRESSION SYSTEM GET A CURRENT INSPECTIN TAG ON IT
11626 | LABEL THE ROOM WITH THE ELECTRICAL PANELS INSIDE OF IT "ELECTRICAL PANELS INSIDE" ALSO REMOVE THE OBSTRUCTIONS FROM IN FRONT OF THE DOOD LEADING INTO THE ELECTRICAL ROOM
11627 | APPLY FOR AND POST THE M3(FUEL DISPENSER) AND THE L1 (LPG STORAGE) PERMITS AT 1002 WASHINGTON AVE. 832-394-8811
11628 | PROVIDE AND POST THE ORIGINAL CERTIFICATE OF OCCUAPANCY, IF YOU DO NOT HAVE IT APPLY AT 1002 WASHINGTON AVE. 82=394-8811
11629 | DISCONTINUE USING A LOCK BAR DURING BUSINESS HOURS
11630 | DISCONTINUE USING CROSSBAR LOCK ON THE REAR EXIT DOOR DURING BUSINESS HOURS
11631 | NoData
11632 | NoData
11633 | NoData
11634 | NoData
11635 | K1 permit needs to be renewed. Pay past due amount in 10 business days.
11636 | NoData
11637 | NoData
11638 | NoData
11639 | provide and install missing light fixture cover where owner works in front main office
11640 | NoData
11641 | repair or replace all exit lights that are not working through out the hold building
11642 | All auto-matic sprinkler systems shall be inspected once a year and tag with an up dated state inspection tag by a certifide company.
11643 | test done by a certifide sprinkler company and show prove to fire marshal's office.
11644 | all fire extinguishers shall be inspected by a certified company once a year and tag.
11645 | remove all combustible materials such as old tires,bxes,cloth materials ,plastics paper and any other trash combustibles not been use for transport.
11646 | NoData
11647 | provide and install a falcon lock on the 911 emergency red box open only by fire marshal's key to put your front entrance gate lock key inside
11648 | NoData
11649 | remove all plastic containers not approved for gasoline storage and provide an approved metal container for storage of (5) of gas with out a permit
11650 | label all electrical breakers and switches located in all electrical panels.
11651 | remove all L,P bottles outside of warehouse right away and install in metal cage due to danger during a fire for fire fighters and workers
11652 | provide and install one 2a 10 bc fire extinguisher at the main front office and mount.
11653 | provide and install sprinkler connection caps if missing outside of warehouse at (Y) connector for fire department water hoses if needed
11654 | Apply for a certificate of occupancy at 1002 Washington on line occupancy.inspection@houstontx.gov
11655 | remove dumpster at lease (10) feet away from building to prevent warehouse from fire due to combustible materials in container.
11656 | provide and install 911 emergency red box and mount at front main entrance gate along with a falcon lock and extra key from your gate lock to be put inside red box.to open up gate incase of an emergency.
11657 | NoData
11658 | all doors shall be proper identified with the following words incase of an emergency ,storage ,office ,kitchen private room electrical room exc
11659 | remove all obstruction away from main sprinkler system such as l p g bottles and any other obstructions away from sprinkler riser
11660 | NoData
11661 | remove any combustible materials away from all electrical panels at lease (3) feet away
11662 | keep waste oil storage to (55) gallon drums or apply for a combustible liquid f7 permit if stored in container over 60 gallons
11663 | remove all open one gallon waste oil containers and remove all hazardous waste oil from the ground floor area .provide and install (55) gallon drums and install sign indicating waste oil with letters at lease (4) inches tall.
11664 | provide and install sign on the inside of all exit doors
11665 | keep all exit doors clear from any obstructions to keep exit pathway clear at all times
11666 | NoData
11667 | NoData
11668 | NoData
11669 | P2 (ASSEMBLY PERMIT) EXPIRED ON 1-6-20201.
11670 | Please repair sprinkler system in 72 hours, maintain a firewatch on building #6 until all repairs are completed.
11671 | NoData
11672 | NoData
11673 | Please provide information that the Fire Alarm System is working correctly according to L.S.B #4 of Houston Fire Department Standards.
11674 | Please repair all fire department access gates. Automatic gates and manual gates. Provide falcon or Knox locks to secure 911 boxes, to be used only for police or fire department personal.
11675 | Please repair all fire department access gates. Automatic gates and manual gates. Provide falcon or Knox locks to secure 911 boxes, to be used only for police or fire department personal.
11676 | NoData
11677 | All installation of security gates across a fire access road follow the Houston Fire Department LSB Standard No. 04, Access Control Gates and LSB Standard No. 05, Key Boxes instructions.
11678 | NoData
11679 | complaint received for red tagged FACP.red tag violation corrected
11680 | NoData
11681 | Fire Alarm need testing
11682 | Evac Routes must be posted
11683 | NoData
11684 | NoData
11685 | NoData
11686 | NoData
11687 | replace low battery smoke alarms
11688 | repair outside emergency light
11689 | Please have the fire extinguishers serviced in the Boiler Room, and any storage building which has supply's. equipment, or appliances.
11690 | Please sign the Owners Statement of Compliance document and return to the Fire Inspector.
11691 | Please check all Boiler Rooms, Maintenance Rooms, Equipment Rooms, Storage Rooms on the property for combustible material.(paper, cardboard, gasoline, propane cylinders, combustible paints, shop towels, cleaning rags)
11692 | Please provide documentation that the Boiler Room, or any other building with a gas meter, has had a five year gas test. If it has been over five years please provide a gas leak test. To be performed by a licensed plumbing contractor.
11693 | NoData
11694 | The fire alarm and sprinkler systems are due for an annual inspection. Have both systems inspected to achieve compliance.Sprinkler system in building 2 and 11 have no water pressure due to pipe rupture from inclement weather.A 24 hrs. 7 days a week inhouse firewatch is required until both systems are back in compliance.
11695 | Remove outdated fire extinguishers.
11696 | Ensure all fire extinguishers are removed from the ground and mounted accordingly.
11697 | Provide a fire extinguisher with a minimum rating of 2A:20BC within 75 feet of fueling station.
11698 | Replace the inoperable rusted padlock on the 911 key box with a Knox or Falcon Padlock. The padlock can be obtained at knoxbox.com.
11699 | Repair the inoperable emergency illumination on the exit signs.
11700 | Obtain a fuel dispense permit from the Houston Permitting Center at 1002 Washington Ave. Houston, TX.
11701 | provide and install conduit piping on all expose wires
11702 | have all fire extinguishers inspected and tag
11703 | repair or replace all emergency lights that are not working or simply replace batteries if needed
11704 | provide and install a plain exit sign on top of exit door
11705 | provide and install signs on all doors with the following wordage ,office ,restroom ,electrical room storage room exc. due to an emergency or fire.
11706 | provide and install sign towards middle of the front exit door
11707 | Repair ASAP.
11708 | Please have the fire extinguishers serviced in the Boiler Room, and any other storage building which has supply's, equipment, or appliances.
11709 | Please sign the Owners Statement of Compliance document and return back to the Fire Inspector.
11710 | Please check all Boiler Rooms, Maintenance Rooms, Equipment Rooms, Storage Rooms on the property for combustible material.(paper, cardboard, gasoline, propane cylinders, combustible paints, shop towels, cleaning rags)
11711 | Please provide documentation that the Boiler Room, or any other building with a gas meter, has had a five year gas test. If it has been over five years please provide a gas leak test. To be performed by a licensed plumbing contractor.
11712 | NoData
11713 | NEED TO BE SERVICE . HAS TROUBLE LIGHT ON. 9-16-20 LAST DATE
11714 | NEED TO BE SERVICE. 7-26-19 NEW INSTALATION DATE ONLY.
11715 | NEED TO BE SERVICE . 7-26-19 NEW INSTALATION DATE ONLY
11716 | NEED TO BE SERVICE . 8-20 LAST DATE
11717 | NEED TO PUT UP A FIRE ALARM ROOM SIGN
11718 | COVER THE EXSPOSED WIRES UNDER THE STAIRS BY ROOM 101A
11719 | NEED TO GET A GAS TEST DONE BECAUSE THERE IS A STRONG SMELL OF GAS IN THE BOILER ROOM
11720 | NEED TO GET A C7 COMPRESS GAS PERMIT FOR THE ARAGON BOTTLES IN THE BUILDING
11721 | NO VIOLATIONS FOUND.
11722 | NoData
11723 | NoData
11724 | 5-27-2020 IN COMPLIANCE
11725 | 7-2020 IN COMPLIANCE
11726 | 7-2020 IN COMPLIANCE
11727 | NoData
11728 | NoData
11729 | NoData
11730 | PER NFPA 55 7.1.8.4.2At cylinder-filling plants, authorized cylinder requalifier's facilities, and distributors' warehouses,the nesting of cylinders shall be permitted as a means to secure cylinders.There is no need for straps, chains or cables whiles cylinders are being stored in an appropriate manner per the code.IN COMPLIANCE AT THIS TIME
11731 | Where required by the code official, an application for a permit shall include an HMIS, such as Superfund Amendments and Reauthorization Act of 1986 (SARA) Title III, Tier II Report or other approved statement. The HMIS shall include thefollowing information: 1. Product Name. 2. Component. 3. Chemical Abstract Service (CAS) number. 4. Location where stored or used. 5. Container size. 6. Hazard classification. 7. Amount in storage. 8. Amount in use-closed systems. 9. Amount in use-open systems. Use the forms provided. Additional forms may be found at:http://houstontx.gov/fire/formsandpermits/index.htmlhttp://www.houstontx.gov/fire/business/hmisinstructions.pdfBased upon the amounts and classifications provided on the required HMIS, a supplemental Notice of Violation may be issued to require additional operational permits.THE FORM SUBMITTED SHALL SHOW THE PROPERTY ADDRESS, CONTROL AREA ID, PRINTED NAME OF THE PERSON SUBMITTING THE FORM AND THEIR SIGNATURE, AND DATE. IF THE BUILDING HAS MULTIPLE CONTROL AREAS THE FORMS SHALL SHOW THE AMOUNTS IN EACH CONTROL AREA. THE FORM, AS SUBMITTED, SHOWS AMOUNTS IN EXCESS OF THE MAQ FOR THE OCCUPANCY CLASSIFICATION AND COULD RESULT IN MOVING THIS OCCUPANCY TYPE TO AN H OCCUPANCY.COMPLIANCE WITHIN30 DAYS
11732 | Compliance: 30 calendar days.
11733 | NoData
11734 | Throughout facility.
11735 | Compliance: 30 calendar days.
11736 | All extinguishers are in compliance at this time. Per our conversation, make sure all are hanging in the required locations.
11737 | See above- the fire extinguisher on the fork lift needs to maintained annually, it's in compliance at this time (11-2020)
11738 | Jolene Fenley281-249-4725
11739 | The FAP is in compliance at this time (3-15-2021) maintain the system as stated above.
11740 | See above concerning body work -spray painting
11741 | See above concerning exits- per our conversation (unloading dock area) remove anything that can obstruct an exit.
11742 | NoData
11743 | NoData
11744 | NoData
11745 | Obtain a compressed gas permit for O2 in amounts greater than 504 cu. ft. (tier 1). Permits can be obtained from the Houston Permitting Center at 1002 Washington Ave. Houston, TX.
11746 | Overflow protection is required on dip tank.
11747 | An approved fire extinguishing system is required for the dip tank.
11748 | Ensure adequate ventilation is provided for dip tank.
11749 | Fill out and return HMIS forms.
11750 | Obtain a LPG permit or reduce amount stored to less than 125 water gallons in aggregate. Permits can be obtained from the Houston Permitting Center at 1002 Washington Ave. Houston, TX.
11751 | Ensure exit signs are fully illuminated.
11752 | NoData
11753 | PANIC HARDWARE A REQUIREMENT IN HIGH PILE STORAGE WAREHOUSES. MAKE SURE ALL EXIT DOORS HAVE PANIC HARDWARE INSTALLED.
11754 | BROKEN EMERGENCY LIGHTING NOTED AT REAR EXIT NEAR DOOR 20 - CHECK ALL EMERGENCY LIGHTS FOR PROPER OPERATION
11755 | ENSURE ANNUAL TESTING IS BEING DONE ON EMERGENCY LIGHTING PER ABOVE FIRE CODE
11756 | KEYS IN KEYBOX DID NOT OPEN HFD ACCESS DOORS AROUND BUILDING - HAVE DOORS RE - KEYED AND NOTIFY FIRE INSPECTOR TO REPLACE KEYS IN 911 KEYBOX
11757 | PANIC HARDWARE A REQUIREMENT IN HIGH PILE STORAGE WAREHOUSES. MAKE SURE ALL EXIT DOORS HAVE PANIC HARDWARE INSTALLED.
11758 | MUST PROVIDE 30 INCH MINIMUM SPACING (FRONT, BACK, AND SIDES) FROM ELECTRICAL SERVICE PANELS AND BATTERY CHARGING MODULES TO ANY COMBUSTIBLE MATERIALS. AS WELL, ALWAYS PROVIDE MINIMUM 36 INCH AISLEWAY LEADING TO ELECTRICAL SERVICE PANELS.
11759 | NoData
11760 | Remount the fire extinguisher that is on the floor by the exit door near the stairs in suite 1000. See the mounting instruction for height requirements. Consult with fire extinguisher company if needed.
11761 | The yellow tags on the fire alarm panel shall be corrected as soon as possible. Make all other code violation corrections prior to the re-inspection date noted on page one of the inspection report.
11762 | The annual fire alarm system test expired on 1/15/21. Provide a current annual fire alarm test. Provide the report for the test and the panel shall have a current blue tag.
11763 | Provide current audibility test documentation within the last 3 years for the fire alarm system.Test documentation must have one of two things to be acceptable. A) Must show each audibility device’s ambient decibel level and the decibel level when the device is active. The difference in DB level must fall within NFPA 72’s acceptable range for the device to pass the test. OR B) A document from their company on company’s letter head that has the following information – 1) Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all audibility devices passed the audibility test as required by NFPA 72.
11764 | The fire alarm system has multiple yellow tags that must be corrected as soon as possible. All yellow tags shall be addressed with a white tag when repaired.
11765 | Remount the fire extinguisher that is on the floor by the exit door near the stairs in suite 1000. See the mounting instruction for height requirements. Consult with fire extinguisher company if needed.
11766 | Consult with a certified fire alarm inspection company. If the system is an addressable / Intelligent system - provide the digital diagnostic reading showing the detectors status. If the system is conventional - test each device with synthetic smoke and provide documentation. The documentation is required to show: 1)Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all smoke detector devices passed the sensitivity test as required by NFPA 72.
11767 | The fire alarm system must be monitored by a supervising station. Provide documentation that the system is monitored by the monitoring alarm company.
11768 | Provide the Certificate of Occupancy for each suite. 700, 800, 900, and 1000. The Building Department issued certificates of occupancy shall be posted near the main entrances of each suite / unit. If you do not have a copy of the Certificate of Occupancy, contact the City of Houston Permitting Center / Occupancy Team.
11769 | Provide the Certificate of Occupancy for each suite. 700, 800, 900, and 1000. The Building Department issued certificates of occupancy shall be posted near the main entrances of each suite / unit. If you do not have a copy of the Certificate of Occupancy, contact the City of Houston Permitting Center / Occupancy Team.
11770 | NO VIOLATIONS FOUND AT THIS TIME
11771 | NoData
11772 | NoData
11773 | NoData
11774 | NoData
11775 | NoData
11776 | No missing spacers allowed in electrical panels
11777 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs
11778 | Fire protection equipment must be identified, please add permanent labeling for "Riser Room"
11779 | NoData
11780 | NoData
11781 | NoData
11782 | NoData
11783 | NoData
11784 | NoData
11785 | Where required by the code official, an application for a permit shall include an HMIS, such as Superfund Amendments and Reauthorization Act of 1986 (SARA) Title III, Tier II Report or other approved statement. The HMIS shall include thefollowing information: 1. Product Name. 2. Component. 3. Chemical Abstract Service (CAS) number. 4. Location where stored or used. 5. Container size. 6. Hazard classification. 7. Amount in storage. 8. Amount in use-closed systems. 9. Amount in use-open systems. Use the forms provided. Additional forms may be found at:http://houstontx.gov/fire/formsandpermits/index.htmlhttp://www.houstontx.gov/fire/business/hmisinstructions.pdfBased upon the amounts and classifications provided on the required HMIS, a supplemental Notice of Violation may be issued to require additional operational permits.THE FORM SUBMITTED SHALL SHOW THE PROPERTY ADDRESS, CONTROL AREA ID, PRINTED NAME OF THE PERSON SUBMITTING THE FORM AND THEIR SIGNATURE, AND DATE. IF THE BUILDING HAS MULTIPLE CONTROL AREAS THE FORMS SHALL SHOW THE AMOUNTS IN EACH CONTROL AREA. THE FORM, AS SUBMITTED, SHOWS AMOUNTS IN EXCESS OF THE MAQ FOR THE OCCUPANCY CLASSIFICATION AND COULD RESULT IN MOVING THIS OCCUPANCY TYPE TO AN H OCCUPANCY.COMPLIANCE WITHIN30 DAYS
11786 | NoData
11787 | Door handle twist locks not allowed, replace with approved door locking mechanism
11788 | Unlatching of door requires one motion, hotel room type hardware is acceptable
11789 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs
11790 | HMIS required due to types and amounts of materials on site
11791 | Gas cylinders must be secured. Attach chain to non-movable object in order to keep cylinders upright
11792 | 36" Working clearance must be maintained in front of electrical panels
11793 | No missing spacers allowed in electrical panels; All junction boxes, light switches and plug outlets must have cover plates installed
11794 | LP containers must meet minimum separation from openings, lot lines and building: 5 ft
11795 | One fire extinguisher required in office, one additional in shop 1; can move one from shop 2
11796 | Extinguisher must be conspicuously marked, please mark location with RED tape, preferably DOT reflective or other approved RED marking
11797 | 3-way plugs, multiple outlet adapters and multi-outlet cords are not allowed unless they are "resettable" type (overcurrent protected)
11798 | Portable fire extinguisher(s) annual maintenance expired; requires current inspection. Last insp 11/19
11799 | Extinguisher can be mounted or placed on shelf
11800 | NoData
11801 | Portable space heater must be plugged into approved receptacle
11802 | Portable space heater CANNOT be plugged into extension cord
11803 | All electrical circuits must be labeled
11804 | Extension cords not allowed as a replacement for permanent wiring
11805 | NO LP or PROPANE storage allowed inside building; Group B, M type occupancy not allowed
11806 | REMOVE bolt lock from door
11807 | Obtain and post Certificate of Occupancy [104.1(9)]. Current yellow application receipt also acceptable
11808 | Directional arrows showing incorrect direction to exit
11809 | Approved locking device on door for buisness must meet requirements 2, 2.1 and 2.2 or use panic / hotel room type hardware
11810 | NoData
11811 | NoData
11812 | NoData
11813 | NEED SERVICE. 6-20-19 LAST DATE
11814 | NEED SERVICE
11815 | FAILURE TO SERVICE THE SPRINKLER SYSTEM
11816 | NoData
11817 | NEED SERVICE. 4-19 LAST DATE
11818 | NoData
11819 | FIRE PANEL NEED SERVICE . HAS A TROUBLE SIGNAL ON. 9-23-19 LAST SERVICE DATE
11820 | NEED SERVICE. 3-19 LAST DATE
11821 | NoData
11822 | 2-11-2020 LAST TEST DATE. NEED TO BE SERVICE BECAUSE THE SUPERVISORY SIGNAL IS ON AND SYSTEM ON SILENCE
11823 | NoData
11824 | NoData
11825 | FIRE PANEL NEED SERVICE ,HAS A TROUBLE SIGNAL. 4-24-20 LAST INSPECTION DATE
11826 | NoData
11827 | SYSTEM HAS NO ANNUAL INSPECTION TAG ON THE PANEL . SHOW PROOF OR GET IT SERVICE
11828 | NEED TO BE SERVICE
11829 | NoData
11830 | NoData
11831 | NoData
11832 | NoData
11833 | NoData
11834 | NoData
11835 | SECURE ALL LP CONTAINERS WITH CHAIN TO AVOID ACCIDENTAL FALLING OVER.
11836 | NoData
11837 | NoData
11838 | 9-11-2019 last test date. Need to fix the trouble signal on the panel
11839 | Exit sign near 164 waiting C and near 317 need repair.
11840 | The storage room near telephone room maintain 18 inches from ceiling.
11841 | Both the Key Box and Fire Alarm Permits are required to be posted on the premises and readily available for the fire official.
11842 | NoData
11843 | NoData
11844 | Sign owner letter of Compliance
11845 | Please provide a gas leak pressure test. To be performed by a licensed plumbing contractor. Last gas test 2010.
11846 | Mark the unit numbers on exterior of all electrical disconnects servicing the apartments.
11847 | Sign owner letter of Compliance
11848 | No Knox box/key box required.
11849 | Permit not required at this location property is open.
11850 | NoData
11851 | ANSUL NEED SERVICE 5-2020 LAST DATE
11852 | LAST EMERGENCY LIGHT TEST FOUND IN FIRE MARSHAL BINDER-- 10-01-19BRING UP TO CODE
11853 | MAKE SURE ANSUL SYSTEM IS UP TO DATE FOR SEMI-ANNUAL INSPECTION.LAST INSPECTION 9-20-20
11854 | Keys to allow HFD to access the gates and facility must be placed inside the 911 key box for life-safety emergencies.The locks to 911 key box must be serviced or replaced.Gates must be maintained and operable to allow HFD personnel access to the facility. Compliance within 30 days.
11855 | ENSURE A CURRENT EMERGENCY PLAN IS MAINTAINED ON THE PREMISES AT ALL TIMES.COMPLIANCE WITHIN 30 DAYS.
11856 | THE REQUIRED FIRE-RESISTANCE RATING OF FIRE-RESISTANCE-RATED CONSTRUCTION SHALL BE MAINTAINED. SUCH ELEMENTS SHALL BE PROPERLY REPAIRED, RESTORED OR REPLACED WHEN DAMAGED, ALTERED, BREACHED OR PENETRATED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
11857 | Exit sign must serviced and operableCompliance within 30 days.
11858 | Keys to allow HFD to access the gates and facility must be placed inside the 911 key box for life-safety emergencies.The locks to 911 key box must be serviced or replaced.Gates must be maintained and operable to allow HFD personnel access to the facility. Compliance within 30 days.
11859 | ENSURE A CURRENT EMERGENCY PLAN IS MAINTAINED ON THE PREMISES AT ALL TIMES.COMPLIANCE WITHIN 30 DAYS.
11860 | THE REQUIRED FIRE-RESISTANCE RATING OF FIRE-RESISTANCE-RATED CONSTRUCTION SHALL BE MAINTAINED. SUCH ELEMENTS SHALL BE PROPERLY REPAIRED, RESTORED OR REPLACED WHEN DAMAGED, ALTERED, BREACHED OR PENETRATED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
11861 | ONLY USING ONE UPSTAIRS CLASSROOM IN BLD 4 AND THE GYM .
11862 | NEED SERVICE TO FIX THE YELLOW TAG. 2-12-20 LAST DATE
11863 | ADD 2 MORE FIRE EXSTINGUISHERS INSIDE OF THE GYM
11864 | Location and placement of the fire extinguisher shall be placed in accordance with the manufactures guidelines or Section 1.3.8, near the kitchen entryway, accessible and no closer than 5 feet from the cooking appliance.The extinguisher shall be placed so that the top of the extinguisher is not more than five feet above floor and the clearance between the bottom of the extinguisher and the floor is not less than 4 inches
11865 | Ann Marie Pedraza 832 607 6461Properties with 3 or more units are required to register with the City of Houston as required by Ordinance No. 2006-1124 (Apartment Security Ordinance).Please contact the City of Houston “Multi-Family Rental Property Registration” at 832-394-8841 or log on to http://www.houstonmultifamily.org/Provide copy of lease agreement with smoke detector, fire extinguisher and openFlame cooking policy or addendum.
11866 | Label Water heater room.
11867 | minimum of 2A:10BC fire extinguisher is needed in water heater room.
11868 | Required every 5 years and must be completed with an approved permit from theBuilding Department.
11869 | NoData
11870 | NoData
11871 | provide all expose wiring under conduit piping to keep from been expose for fire hazard
11872 | provide and install emergency 911red box
11873 | provide and install a falcon lock with an extra key front your gate lock on the 911 red box
11874 | provide and install street address numbers at lease (4) inches tall
11875 | NoData
11876 | apply for a flammable and combustible liquid storage permit at 1002 Washington for storing more than (25) of waste oil in a plastic container with a storage capacity of (200) gallons or more
11877 | Please renew the K1, key box permit. Expired 2/13/21.Please renew the A4, access gate permit. Expired 2/13/21.
11878 | NoData
11879 | Provide correction Tag (within 48 Hours of this Report) for Trouble Alarms on Main Fire Alarm Panel.
11880 | Provide correction Tag (within 48 Hours of this Report) for Trouble Alarms on Main Fire Alarm Panel.
11881 | NoData
11882 | Repair ASAP.
11883 | DO NOT BLOCK EXITS AT ANY TIME - THIS IS A TICKETABLE OFFENSE
11884 | NoData
11885 | NoData
11886 | provide permit for electrical work, repair all expose wires
11887 | Camilo Cabrera 3468126759, Afonso Gonzales 8326039527
11888 | 2A:10BC minimum is required, exception apartment unit minimum 1A:10BC. required for laundry room, office and water heater.
11889 | provide cooking policy
11890 | fail safe required
11891 | key box required
11892 | Label office, Laundry and water heater.
11893 | repair all wall and ceiling penetration
11894 | On the ceiling or wall outside of each separate sleeping area in theimmediate vicinity of bedrooms, In each room used for sleeping purposes
11895 | Required every 5 years and must be completed with an approved permit from theBuilding Department.
11896 | Obtain keybox permit
11897 | fail safe required on gate, recommend toggle switch for gate.
11898 | After January 1, 2017, as a battery-operated singlestationalarm is replaced, that smoke alarm shall be replaced with a tamperresistantbattery-operated single-station smoke alarm. Provided, however,nothing in this section shall require an owner to replace an operationalbattery-operated single-station smoke alarm
11899 | NoData
11900 | NoData
11901 | NoData
11902 | NoData
11903 | NoData
11904 | f7 permit expired 11/14/2020
11905 | NoData
11906 | NoData
11907 | NoData
11908 | NoData
11909 | NoData
11910 | SEEK TECHNICAL ASSISTANCE PER ABOVE CODE TO CONFIRM WHATEVER FIRE PROTECTION NEEDS MAY BE NECESSARY TO MAKE THIS AREA OF BUILDING COMPLIANCE WITH ITS USE
11911 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
11912 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
11913 | Provide Documentation/Report and tag for the 5th Year FDC Hydrostatic test.
11914 | Provide documentation/report for fire damper testing and any necessary repairs.
11915 | Correct 3/19/2021 Advantage Interests Yellow Tag on Sprinkler System. (2 YT)
11916 | Please renew the A4, access gate permit.Expired 2/26/21.
11917 | NoData
11918 | KnoxBox.com 3200 series
11919 | Correct all red & yellow tags on property.
11920 | Repair all yellow tags
11921 | Annual flow test is required for all private F/H on property.
11922 | Informed all residents on the proper use of all open flame cooking devices.
11923 | Check for proper "Fail Safe" operations
11924 | Micro Switch located inside 911 box is defective. Also, a 911 Falcon lock is required.
11925 | Verify all draft stops integrity on property
11926 | HFD 9" Fire Hydrant sign is faded and needs replacing on main access gate
11927 | Blue reflector is required in middle of Apparatus Access road to identify F/H locations.
11928 | Verify all units have working smoke alarms
11929 | Check when your last Gas test was done on property. My records show 02/08/2019.
11930 | Please update your Access gate (a4) permit with HPC. A4 permit expired on 04/06/2020
11931 | Please update your Key box (k1) permit with HPC.K1 permit expired on 04/06/2020
11932 | Please have a gate contractor repair all deficient equipment with your access gates.
11933 | COMPLIANCE DATE: 15 CALENDAR DAYS
11934 | K1 Permit is expired at this time, And must be updated immediately.
11935 | Please renew the K1, key box permit.Expired 3/7/21.Please renew the A4, access gate permit.Expired 8/16/2020.
11936 | HAVE FIRE ALARM PANEL INSPECTED AND TAGGED BY A LICENSED FIRE PROTECTION EQUIPMENT COMPANY. THIS INSPECTION SHALL BE PERFORMED ANNUALLY.
11937 | HAVE EMERGENCY ILLUMINATION IN WAREHOUSE REPAIRED OR REPLACED.
11938 | FIRE ALARM PANEL REQUIRED. APPLY WITH THE CITY OF HOUSTON PERMITTING OFFICE.
11939 | ADD DECAL TO FRONT ENTRY DOOR THAT READS, "THESE DOORS TO REMAIN UNLOCKED DURING BUSINESS HOURS".
11940 | HAVE ALL EMERGENCY EXIT ILLUMINATION REPAIRED OR REPLACED. CHECK THE BATTERY BACKUP BATTERIES LOCATED WITHIN SIGN BY DEPRESSING TEST BUTTON THE SIDE OR BOTTOM.
11941 | NoData
11942 | Ensure all fire extinguishers have a annual acceptable service tag from a licensed fire protection company.
11943 | Systems or devices that are permanently out of service or any non-required life safety system or fire protection system that no longer functions as originally installed shall be removed or the appearance changed so as not to be mistaken for functioning life safety or fire protection equipment.
11944 | Ensure all exit signs are properly illuminated under battery back up power.
11945 | NoData
11946 | NoData
11947 | NoData
11948 | NoData
11949 | No violations found at this time.
11950 | INSPECTION TAG EXPIRED. ENSURE FIRE EXTINGUISHERS ARE INSPECTED ANNUALLY IN COMPLIANCE WITH CODE.
11951 | SUBMIT PROOF OF RECENT AUDIBILITY TEST WITHIN THE LAST 3 YEARS
11952 | SUBMIT PROOF OF RECENT DETECTOR SENSITIVITY TEST WITHIN THE LAST 2 YEARS
11953 | SUBMIT PROOF OF GAS LEAK TEST PERFORMED WITHIN THE LAST 5 YEARS.
11954 | NoData
11955 | Fire extinguisher must be inspected annually.
11956 | Mount fire extinguisher
11957 | Replace missing electrical cover plate.
11958 | NoData
11959 | NoData
11960 | NoData
11961 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
11962 | NoData
11963 | PLEASE RE-NEW "OPEN FLAMES / CANDLES" PERMIT WITHIN 10 BUSINESS DAY ... BY 01/17/20 COH - PERMIT OFFICE 1002 WASHINGTON AVE. HOUSTON, TX 77002
11964 | PLEASE RE-NEW "PUBLIC ASSEMBLY" PERMIT WITHIN 10 BUSINESS DAY ... BY 01/17/20 COH - PERMIT OFFICE 1002 WASHINGTON AVE. HOUSTON, TX 77002
11965 | NoData
11966 | NoData
11967 | NoData
11968 | NoData
11969 | NoData
11970 | all fire extinguishers shall be inspected and tag by a certified company
11971 | ALL FIRE EXTINGUISHERS SHALL BE SERVICED AND TESTED BY A QUALIFIED FIRE PROTECTION COMPANY ANNUAL. EXTINGUISHER SHALL HAVE A ANNUAL INSPECTION TAG ATTACHED.
11972 | MOUNT THE FIRE EXTINGUISHER FOLLOWING THE ABOVE CODE. FIRE EXTINGUISHERS ARE REQUIRED TO BE MOUNTED IN AN AREA WHERE IT IS READILY VISIBLE, EASILY ACCESSIBLE, NEAR A COMMON PATH OF TRAVEL, AND NOT SUBJECT TO DAMAGE
11973 | A 2A 10B:C RATED EXTINGUISHER NEEDS TO BE MOUNTED IN BUSINESS.
11974 | COMPLY WITH ABOVE CODE.
11975 | COMPLY WITH ABOVE CODE.
11976 | Forklifts must have current fire extinguisher.
11977 | NoData
11978 | Address must be visible from the street.
11979 | Breaker box must be labeled.
11980 | Apply for hotworks permit.
11981 | Apply for oil storage permit.
11982 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
11983 | NoData
11984 | No violation found.
11985 | M3 (MOBILE FUEL DISPENSING) PERMIT EXPIRED 2-2-2021.
11986 | COMPLIANCE DATE: 15 CALENDAR DAYS
11987 | (P2) fire prevention permit is expired and must be renewed immediately.
11988 | NoData
11989 | Mount the fire extinguishers located on the ground accordingly.
11990 | Provide a warning sign for the fuel dispenser.
11991 | Ensure the spare propane cylinders are stored outside in a protected enclosure.
11992 | Provide externally illuminated exit signs for the shop and warehouse exits. Internally illuminated exit signs located in the office area are required to be listed and labeled in accordance with UL924.
11993 | Obtain a fuel dispense permit from the Houston Permitting Center located at 1002 Washington Ave. Houston, TX.
11994 | Ensure the exits are unlocked from the egress side while the building is occupied.
11995 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
11996 | ONCE WORK IS COMPLETE ON RISER, PERFORM 1 YEAR AND 5 YEAR REQUIRED INSPECTION PER NFPA 13 ON SPRINKLER SYSTEM (LAST INSPECTION NOTED ON TAG IS 2016).
11997 | AQUIRE AN M3 (FUEL DISPENSING) PERMIT WHEN YOUR FUEL TANK IS OPERATIONAL
11998 | Sign letter provided.
11999 | Label exterior electrical boxes with unit number they operate.
12000 | Sign letter provided.
12001 | FYI: Last gas test performed on 2/22/2018. #17138120.
12002 | Need access gate permit.
12003 | Sign letter provided.
12004 | Need key box permit.
12005 | Main gate- Switch not working. Need keys for failsafe to place in 911 box. Back gate (entrance side) paint 911 box red. Need new pad locks for failsafe and keys to be placed in 911 box. Back gate (exit side) switch not working. Need new pad lock and key for 911 box.
12006 | Amount Due: $503.95
12007 | NoData
12008 | NoData
12009 | Have the annual fire extinguisher service/inspection performed on all extinguishers in the facility(3) by a certified company, ensuring new tags are placed.
12010 | Have the annual Fire Alarm Inspection performed and tagged by a certified fire protection company. (The last inspection was noted as 2/13/2020)
12011 | NoData
12012 | NoData
12013 | NoData
12014 | NoData
12015 | NoData
12016 | NoData
12017 | NoData
12018 | NoData
12019 | NoData
12020 | All fire extinguishers must be serviced and have a current service tag placed on them. The fire extinguisher in the stagemechanical room D136.4 was last checked in 2016.
12021 | The fire alarm system must have an emergency lighting test performed on it.
12022 | The sprinkler system must have an annual inspection performed on it.
12023 | A gas test must be performed on the gas piping system.
12024 | All draperies and curtains must be treated with fire retardant materials. The certificate showing this treatment must be placed inside of the FMB.
12025 | The intercom system must have an annual inspection performed on it.
12026 | All violations listed in this report must be corrected within 30 DAYS in order to avoid citations and re-inspection fees.
12027 | On 6/12/2020 the fire alarm was yellow tagged for deficiencies. Have a certified fire alarm company correct all deficiencies to bring the system back into full operation with no impairments within 30 DAYS, ensuring that a correction tag is placed once repairs are complete.
12028 | Make all code violation corrections prior to the re-inspection date.
12029 | Provide current audibility test documentation within the last 3 years for the fire alarm system.Test documentation must have one of two things to be acceptable. A) Must show each audibility device’s ambient decibel level and the decibel level when the device is active. The difference in DB level must fall within NFPA 72’s acceptable range for the device to pass the test. OR B) A document from their company on company’s letter head that has the following information – 1) Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all audibility devices passed the audibility test as required by NFPA 72.
12030 | Provide documentation for an annual load test meeting the code requirements above.
12031 | Provide fire rated caulk in all gaps / opening of piping and / or conduit going into and through the ceiling or walls. Expanding foam is not acceptable. Must be fire rated caulk. Fire stop tested up to 4 hours in accordance with ASTM E 814 (UL 1479) and CAN/ULC S115Noted areas were the Fire Alarm room and the Sprinkler riser room. Mechanical rooms as needed.
12032 | NoData
12033 | Please renew the A4, access gate permit. Expired 3/11/21.Please renew the K1, key box permit. Expired 3/11/21.
12034 | NoData
12035 | NoData
12036 | NEED SERVICE. FIX YELLOW TAG. 6-2-20 LAST DATE
12037 | NEED SERVICE. 8-19 LAST DATE
12038 | NoData
12039 | NoData
12040 | please renew your access gate (a4) permit that expired on 02/26/21. FYI, Your Key Box (k1) permit expires on 03/29/21. If you need an invoice or have questions to the amount owed, please call the HPC office at 832-394-8811 then dial "0" and a representative should be available to answers your questions.
12041 | NoData
12042 | NEED SERVICE TO FIX RED TAG. 12-11-20 LAST DATE
12043 | NoData
12044 | Please renew the A4, access gate permit. Expired 2/7/2020.Please renew the K1, key box permit. Expired 7/15/2020.
12045 | NoData
12046 | NoData
12047 | NoData
12048 | • Reentry-FC00 1005.3.2.4.3International Building Code 403.12 Stairway door operation. Doors opening into interior stair enclosures shall not be locked from either side. However, a door locked from the stair side may be permitted provided that such door is equipped with an automatic fail safe system for opening in the event of the activation of any automatic fire detection system, or when any elevator recall is activated, or when any signal is received from the fire command center. Such door shall be deemed as openable from the stair side. Stair reentry signs shall be posted throughout the stairway indicating that reentry is provided only during fire emergencies. Such signs shall be in accordance with Section 1026.4.2. PROVIDE A MANUAL DOOR LOCK OVERRIDE SWITCH ON THE ALARM PANEL FOR STAIRWAY DOOR OPERATION.COMPLIANCE WITHIN 60 CALENDAR DAYS.
12049 | Garage Exit sign by Stair 2 D is not illuminated.COMPLIANCE WITHIN 60 CALENDAR DAYS.
12050 | • Reentry-FC00 1005.3.2.4.3International Building Code 403.12 Stairway door operation. Doors opening into interior stair enclosures shall not be locked from either side. However, a door locked from the stair side may be permitted provided that such door is equipped with an automatic fail safe system for opening in the event of the activation of any automatic fire detection system, or when any elevator recall is activated, or when any signal is received from the fire command center. Such door shall be deemed as openable from the stair side. Stair reentry signs shall be posted throughout the stairway indicating that reentry is provided only during fire emergencies. Such signs shall be in accordance with Section 1026.4.2. PROVIDE A MANUAL DOOR LOCK OVERRIDE SWITCH ON THE ALARM PANEL OR IN THE FIRE COMMAND ROOM FOR RELEASING STAIRWAY DOOR LOCKS FOR EMERGENCY USE.Security console and stairway reentry phone system on floors 8 and 5 needs to be evaluated to determine if system was permitted and approved. COMPLIANCE WITHIN 60 CALENDAR DAYS.
12051 | Building stair doors 8 B did not close completely and needs to be adjusted.COMPLIANCE WITHIN 60 CALENDAR DAYS.
12052 | Garage Standpipe Pressure gauge located by Stair 6 D is not showing the pressure of system and needs to be replaced.COMPLIANCE WITHIN 60 CALENDAR DAYS.
12053 | Fire Fighter communication phone that was tested was inoperable and needs to be replaced.COMPLIANCE WITHIN 60 CALENDAR DAYS.
12054 | Elevator car Numbers need to be posted on the recall floors of the Building and Garage. COMPLIANCE WITHIN 60 CALENDAR DAYS.
12055 | Add a lock out tag out kit to the Garage Elevator machine room.COMPLIANCE WITHIN 60 CALENDAR DAYS.
12056 | Stairway signs located on 4 A, 4 B, 2 A, 2 B read No-Reentry. Doors were unlocked at time of inspection. Stairway signs need to accurately reflect the Intent of the door they identify.COMPLIANCE WITHIN 60 CALENDAR DAYS.
12057 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice.COMPLIANCE WITHIN 60 CALENDAR DAYS.
12058 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualFire Extinguishers- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
12059 | NoData
12060 | LAST EMERGENCY LIGHT TEST FOUND IN FIRE MARSHAL BINDER WAS 11-20-2019BRING UP TO CODE
12061 | LAST FIRE EXTINGUISHER INSPECTION 8-2019BRING UP TO CODE
12062 | LAST ANSUL INSPECTION MAY 2020BRING UP TO CODE
12063 | UPDATE ELEVATOR PERMITPERMIT EXPIRED 4TH QUARTER 2020
12064 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
12065 | NoData
12066 | ELEMENTARY AND MIDDLE SCHOOL PANELS NEED TO BE SERVICE ,TO FIX THE YELLOW TAGS.8-7-2020 LAST DATE
12067 | THE HIGH SCHOOL NEED TO HAVE THE FIRE EXSTINGUISHERS SERVICE. NO TAGS ON THEM. NEED TO ADD ONE RED ONE IN THE KITCHEN
12068 | THE HIGH SCHOOL NEED TO ADD 1 IN THE KITCHEN. THE SILVER ONE
12069 | NoData
12070 | NEED SERVICE 8-19 LAST DATE
12071 | Fire Alarm need testing
12072 | Evac Routes must be posted
12073 | Please repair window/windows in apartment unit #74. Windows which are designed to be opened shall be operational at all times for emergency egress.
12074 | Correct the Yellow tagged Fire Alarm Panel3/24/20 FACP corrected
12075 | NoData
12076 | last annual Fire Sprinkler System Test 1/8/2018
12077 | 3/24/2021 re-inspection fee for fire sprinkler system expired annual inspection of 2018
12078 | NoData
12079 | NEED TO GET ONE PUT IN THE KITCHEN. THE SILVER ONE.
12080 | INFORMATION ONLY
12081 | NEED TO PUT ONE IN THE KITCHEN
12082 | NEED TO LABEL THE RISER ROOM DOOR
12083 | Please have all fire extinguishers inspected annually.
12084 | Exits must be clear of obstructions.
12085 | Adjust the door near bait station 35 and any others so that it does not require special effort to open.Compliance by 4-27-2021
12086 | Place electrical room signs on both rear doors leading into the electrical room.Compliance by 4-27-2021
12087 | Place an approved electrical plate over the open electrical plug.Compliance by 4-27-2021
12088 | Have fire door company perform annual drop test on all fire doors.Compliance by 4-27-2021
12089 | Have qualified sprinkler company address the yellow tag riser issues in the hand prep, pump room, stuffing and building B areas.Also have company place a sprinkler wrench in the sprinkler head box in the stuffing area per NFPA.Compliance by 4-27-2021
12090 | Have qualified sprinkler/ alarm company perform annual inspections on the risers and alarm panel.Also provide documentation of the five year testing for your water tank and private fire hydrants. Compliance by 4-27-2021
12091 | Submit an updated HMIS form using the guidelines that will be provided.Compliance by 4-27-2012
12092 | Repair or replace emergency lighting in the nurses station, route sales office and throughout your facility. Provide documentation that they have been tested and the dates of the test.Compliance by 4-27-2021
12093 | Remove the letters HFD off of all doors that were not designated as firefighter access doors.Compliance by 4-27-2021
12094 | Secure the 2nd floor of building B so that no one can enter or maintain a safe working space.Compliance by 4-27-2021
12095 | NoData
12096 | NoData
12097 | Add electronic lock override switch to FCC per code.
12098 | Trim bushes that are obstructing the FDC.
12099 | Add cover to junction box on level 5 near stair A per code.
12100 | Return the fire rating to its designed fire resistance rating per code.Go through mechanical, electrical and IT rooms and make additional corrections as needed.
12101 | Ensure all stairwell doors close and latch from the open position per code.
12102 | Remove chevron so exit sign points to the exit per code.
12103 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. • Present Permits that apply to facility Address listed • on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS.
12104 | Have a licensed fire protection company inspect and tag the two out of date extinguishers.
12105 | Move the fire extinguisher marking sign over the fire extinguisher that was moved.
12106 | Have a licensed fire protection company perform an annual fire alarm inspection and correct the trouble/supervisory alarm.
12107 | Ensure audibility test is up to date.
12108 | Ensure smoke detector sensitivity is up to date.
12109 | Apply for and obtain a Certificate of Occupancy that reflects the current work being performed in the structure. www.houstonpermittingcenter.org/hpwcode1106
12110 | Fill out and return the HMIS form.
12111 | Repair or replace the inoperable emergency lighting located in the halls of floors 2, 3, and 4.
12112 | Exit doors to the stairway are required to be closed.
12113 | Repair inoperable lighting on exits signs.
12114 | Remove combustible material stored in 16th floor mechanical room per code.
12115 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriateinspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualFire Extinguishers- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
12116 | NoData
12117 | NoData
12118 | NoData
12119 | YOU CURRENTLY HAVE NO CONSTRUCTION DOCUMENTS (PLANS) SHOWING YOUR HIGHPILE STORAGE ARRANGEMENTS. THIS WAS PART OF THE FIRE MARSHALLS OFFICE APPROVING YOUR BEING ABLE TO APPLY A PRE-1973 FIRE CODE FOR THIS OCCUPANCY. PROVIDE PROOF THAT THESE ARE BEING DRAWN UP BY AN APPROVED AGENCY AND A TIMELINE FOR THEM BEING SUBMITTED FOR APPROVAL.
12120 | THE SPRINKLER EVALUATION FOR YOUR FACILITY ONLY ALLOWS FOR STORAGE OF CLASS III COMMODITIES TO 20FT TO TOP OF THE COMMODITY. YOU ARE CURRENTLY EXCEEDING THAT HEIGHT THROUGHOUT YOUR FACILITY. EITHER LOWER YOUR STORAGE TO WHAT IS ALLOWED PER THE SPRINKLER EVALUATION OR PROVIDE A TIMELINE FOR IMPROVING YOUR SPRINKLER SYSTEM TO ACCOMODATE THE EXTRA HEIGHT STORAGE. IF LOWERING IS THE DECISION HAVE COMMODITIES LOWERED WITHIN 60 DAYS.
12121 | CofO#:95073400 HI-PILE,PRE-1973 FIRE CODE EAST/WEST RISERS YELLOW TAGGED (5/30) EAST FIRE ALARM CONTROL PANEL OK (6/1) WEST FIRE ALARM CONTROL PANEL RED TAG (6/1) FIRE EXTINGUISHERS OK (10/2017) DRY CHEM EXTINGUISHER BY DIESEL STORAGE TANK OK (10/2017)
12122 | ALL SPRINKLER RISERS YELLOW TAGGED ON ANNUAL INSPECTION (5/30) - CORRECT NOTED IMPAIRMENTS WITHIN 30 DAYS WEST SIDE FIRE ALARM CONTROL PANEL RED TAGGED ON ANNUAL INSPECTION (6/1) - CORRECT NOTED IMPAIRMENTS WITHIN 30 DAYS
12123 | Please renew your access gate (a4) permit that expired on 03/06/21. If you require an invoice number or the total amount owed, please contact the HPC office at 832-394-8811 "dial 0" and a representative will assist you.
12124 | NoData
12125 | Post the occupant load.
12126 | Must have a current inspection tag on all portable fire extinguishers. Since the business opened in October of 2020, I will allow the fire extinguishers to be untagged until September 30, 2021. Meaning, all portable fire extinguishers must have a current inspection tag for the month of October 2021.
12127 | Follow the LSB standard for Mounting all portable fire extinguishers.
12128 | Move the existing portable fire extinguisher to the middle of the chemical storage warehouse. Must add two additional 2-A, 10B:C portable fire extinguishers for the electrical room and office area.
12129 | It is the owner/occupants responsibility to obtain all permits and correct all fire code violations prior to follow up inspection.
12130 | Provide a NFPA 704 Diamond for Corrosives and place on the outside of any door leading into the chemical warehouse.
12131 | Must place fuel used for blower in approved safety can defined below. SAFETY CAN. An approved container of not more than 5-gallon (19 L) capacity having a spring-closing lid and spout cover so designed that it will relieve internal pressure when subjected to fire exposure.
12132 | Please make sure the signs adhere to the above fire code.
12133 | Must purchase the Tier 1 Hazardous Materials permit for the corrosives stored in the business. City of Houston Permitting Center address is 1002 Washington Avenue, Houston Texas 77002. Phone number for the Fire Permit Office is 832 394 8811.
12134 | Must purchase a Tier 1 Hazardous materials permit for the corrosive liquids stored at the business.
12135 | NoData
12136 | Please renew your access gate (a4) and Key box (k1) permits that expired back on 09/24/20. If you require an invoice number or the total amount owed, please contact the HPC office at 832-394-8811 "dial 0" and a representative will assist you. Thank you!
12137 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
12138 | Provide documentation/report for annual 'Load Test' and any necessary repairs.
12139 | Provide Semi-annual Inspection and Service Tag of all Vent Hood Fire Suppression Systems. (Not a Visual Inspection as per the Tags)
12140 | Provide an electrical switch (toggle or micro switch with button) to automatically activate once the 911 Knox box is opened.
12141 | Provide front door key for 911 Knox Box.
12142 | Correct all 5/4/2020 Advantage Interests Yellow Tags on Sprinkler System. A Service tag should be provided for each Yellow Tag.
12143 | NoData
12144 | NoData
12145 | NoData
12146 | NoData
12147 | NoData
12148 | NoData
12149 | It is the owner/occupants responsibility to correct the following violations:-Permits to be obtained: A4 (Access Gate), H3 (Cutting/Welding)-Permits to be canceled: F7 (Flammable/Combustible Liquid Storage)-Permits pending approval: H1 (Hazardous Materials Tier 1) HMIS requested -Install a Knox Box on a post near the gated entrance 48"-60" off the ground and in such a way that it is readily accessible, easily visible, and not subject to damage. The Knox Box should have a electronic means of opening the gate, and a key to the exterior lock on the fail safe box.-Install a NFPA 704 Placard on the front gate and on each man door entrance to the warehouse. This placard should represent the highest threat level present of anystored commodityfor each category.-Pallets stored inside are not to be stored at a height of 6 feet or greater.-Cover all open spaces inside the breaker boxes using the proper breaker box filler plate and properly secure all breaker labels to the inside of the breaker box door.-Create and maintain a clear path of travel to and a working space in front of the breaker boxes.-Remove propane tanks found in the warehouse.
12150 | High-Piled Combustible Storage: Storage of combustible materials in closely packed piles or combustible materials on pallets, in racks or on shelves where the top of the storage is greater than 12 feet in height. When required by the fire code official, high-piled combustible storage also includes certain high-hazard commodities, such as rubber tires, Group A plastics, flammable liquids, idle pallets and similar commodities, where the top of the storage is greater than 6 feet in height.
12151 | The MAQ (Maximum Allowable Quantity) of nonflammable hazardous material solids stored in an indoor control area shall not exceed 9,750 pounds. The MAQ (Maximum Allowable Quantity) of nonflammable/noncombustible hazardous material liquids stored in an indoor control area shall not exceed 975 gallons. In wholesale occupancies the quantities of industrial products containing not more than 50% by volume of water miscible liquids and with the remainder of the solutions not being flammable, shall not be limited, provided that such materials are packaged in individual containers not exceeding 1.3 gallons. Reduce all quantities of hazardous materials being stored indoors to below the MAQ.
12152 | The MAQ (Maximum Allowable Quantity) of nonflammable hazardous material solids stored in an indoor control area shall not exceed 9,750 pounds. The MAQ (Maximum Allowable Quantity) of nonflammable/noncombustible hazardous material liquids stored in an indoor control area shall not exceed 975 gallons. In wholesale occupancies the quantities of industrial products containing not more than 50% by volume of water miscible liquids and with the remainder of the solutions not being flammable, shall not be limited, provided that such materials are packaged in individual containers not exceeding 1.3 gallons. Reduce all quantities of hazardous materials being stored indoors to below the MAQ.
12153 | NoData
12154 | NoData
12155 | NoData
12156 | NoData
12157 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
12158 | The ATV must be removed from the inside of the shop within bldg. 69. Any gas powered equipment cannot stored be inside a building with fuel inside the gas tank. Also, gas cans cannot be stored inside bldg, permit will be needed if storage is continued.
12159 | Flammable liquids permit will be needed, if gas can, paint thinner, or any flammable liquids are going stored inside shop.
12160 | The correct size fire extinguisher must be tagged by a certified company and hung in each space above. If the area has 2 levels there should be a fire extinguisher on each level.
12161 | Ensure fire extinguisher are placed in areas as specified in the LSB above.
12162 | Fire extinguishers in common areas must be inspected annually by a certified company.
12163 | Ensure the electrical boxes are label with the number of the unit to which it serves. All doors must indicate or identify the proper usage of the space.
12164 | Ensure all electrical covers are replaced throughout property on all outlets, light switches and in each electrical panel boxes.
12165 | Ensure the walls and ceilings are repaired and replaced with sheetrock..The safety rings around the exhaust vents must in place.
12166 | Ensure the firestops in the attics are intact to stop or slow fire spread through the attic.
12167 | All gates on property must have a hydrant sign that indicates the hydrants behind that gate. The hydrant sign on the gates are incorrect. Removed the signs and replace with correct signage.
12168 | Gast test is needed for this property. Proof of gas test needed for a gas test was performed within 5 years by a certified plumber.
12169 | Buildings with offices and/or shops within that are rated R2 must be returned to their original R2 status. If the owner wants to keep any apartment unit as a shop/storage/office, the owner must apply for a change of use through the building department in order to make the appropriate designation.
12170 | Hot works is needed if storage of cutting and welding are going to be stored on property.
12171 | You will have automatic gates and existing manual gates Key box permit is needed for property.
12172 | Directory maps at all entrances onto property.
12173 | Ensure gates are built to proper specifications that was sent through via email to office manager. annual permit will be needed for access gates.Missing falcon locks and keys are needed for new and existing gates on property. Please review the info on manual gates also that is provided within the access gate LSB which was sent via email.
12174 | Fire extinguishers must have current inspection tags.
12175 | Fire extinguishers must have current inspection tags.
12176 | Maintain shop clear of combustibles.
12177 | NoData
12178 | NoData
12179 | NoData
12180 | NoData
12181 | Compliance: 30 calendar days.
12182 | Compliance: 30 calendar days.
12183 | Repair ASAP.
12184 | Permit Expired 1/15/2021; Unpaid $266.80
12185 | No violations found
12186 | Install knox-box on gates.
12187 | Place knox box on access gates.
12188 | Install fail-safe on access gate.
12189 | Replace cover on junction box.
12190 | Cover opening in electrical room with fire resistant caulking.
12191 | Have the 6 mo. inspection/service performed on the kitchen hood ANSUL system, ensuring that new tags are placed at the pull station. (Last inspection tag noted as 2/2020)
12192 | NoData
12193 | Have the annual inspection/service performed on all extinguishers, ensuring that new tags are placed. This is to include: (2) regular extinguishers: kitchen and bar and (1) K-type extinguisher: in kitchen
12194 | LASTS KNOWN ANNUAL INSPECTION 6/10/2018 (PER STICKER ON FIRE ALARM CONTROL PANEL). PROVIDE PROOF OF MORE RECENT ANNUAL INSPECTION, PUT CURRENT STICKER ON PANEL.
12195 | NoData
12196 | PER APPROVED PLANS, NO RACK STORAGE WAS APPROVED FOR THIS FACILITY. PLEASE LOWER ALL STORAGE IN RACKS TO 12FT (TO TOP OF COMMODITY) UNTIL THE NEW SPECIFICATIONS HAVE BEEN SUBMITTED FOR REVIEW AND APPROVAL.
12197 | CofO#: 16065803 TYPE 'F2' PERMITS CURRENT (K1,H2,A4) SPRINKLER RISER CURRENT (6/2019) FIRE EXTINGUISHERS CURRENT (2019)
12198 | NoData
12199 | NoData
12200 | NoData
12201 | NoData
12202 | NoData
12203 | Have a licensed fire protection company correct the deficiencies on the yellow tagged sprinkler system.
12204 | Jamel ArnsworthNO VIOLATIONS FOUND AT THIS TIME.
12205 | provide chains or other approved metal restrains to keep all compress bottles from falling down
12206 | provide and install a metal can with a metal lid
12207 | secure l. p. gas bottle on forklift .
12208 | provide and install a metal can with a metal lid and label oily rags for oily rags or paper towels
12209 | label main electrical panel breakers as required by fire code
12210 | all fire extinguishers shall be inspected by a certified company and tag
12211 | provide and install sign at use waste oil storage tank indicating waste oil and another sign at wash vet indicating varsol to identified combustible liquid been use
12212 | remove all plastic containers for storing gasoline to the outside of the building
12213 | OBTAIN AND POST THE FOLLOWING PERMITS: -GATE PERMIT (A4) -911 KEYBOX PERMIT (K1)
12214 | NoData
12215 | NoData
12216 | NoData
12217 | NoData
12218 | NoData
12219 | Do not story any combustibles with in 3 feet of the battery charging station.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12220 | The owner/occupant shall be held responsible for the correction and abatement of all violations listed in this notice of violations report. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12221 | The approved construction documents indicate that a 911 Key Box be installed near the main entrance, but no 911 Key Box visible during this inspection. Provide an approved 911 Key Box or KnoxBox hinged-door 3200 series with the Houston key as indicated on the plans. Failure to comply could result in the revocation of your high-piled permit.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12222 | Provide proper covers for all electrical junction boxes.COMPLIANCE DATE: WITHIN 30 CALENDAR DAYS.
12223 | Apply for and obtain the HFD key box permit (K1) from the city of Houston Permit Center located at 1002 Washington Ave. (832)394-9000. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12224 | Provide a sign for the fire pump room.COMPLIANCE DATE: WITIN 30 CALENDAR DAYS.
12225 | Firefighter access doors shall be labeled with "HFD" on the exterior in the top left-hand corner. The letters shall be not less than 4 inches (100 mm) in height on a contrasting background. Lettering shall be legible, durable and reflective in nature.Provide the approved "HFD" lettering on all HFD Access Doors from the approved construction documents.COMPLIANCE DATE: WITHIN 30 CALENDAR DAYS.
12226 | NoData
12227 | NoData
12228 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
12229 | NoData
12230 | NoData
12231 | Have fire extinguishers inspected and tested. Last inspected and tested April 2020. Must be performed annually.
12232 | Have the sprinkler system inspected or tested, or provide a report regarding its inspection and testing (tags pertaining to the aforementioned were not found). If an acceptable inspection and testing was performed, but it is expired or will expire within 30 days from March 24, 2021, then have the sprinkler system inspected and tested. The fire code requires that this is done annually.
12233 | NoData
12234 | NoData
12235 | NoData
12236 | NoData
12237 | NoData
12238 | NoData
12239 | NoData
12240 | NoData
12241 | Portable fire extinguisher(s) annual maintenance expired; requires current inspection. 2 extinguishers dated 8/20 still within inspection.
12242 | Mounted portable fire extinguishers are required to meet code
12243 | Commerical Kitchen Hood 6-month (ANSUL) extinguisher maintenance expired (dt: 8/20); requires current inspection
12244 | Portable K class extinguisher required and tagged
12245 | Commercial cooking with solid fuel or oil fryers requires Class K rated extinguisher within 30 ft
12246 | Based on size of fryer equipment, a minimum of 1 extinguisher with at least 1.5 Gal capacity Class K rated extinguisher is required
12247 | Keep all exit door(s) and pathways clear. This is the 2nd exit as required by the building department from the Occupancy report proj# 06046184
12248 | NoData
12249 | 3-way plugs, multiple outlet adapters and multi-outlet cords are not allowed unless they are "resettable" type (overcurrent protected)
12250 | Extension cords not allowed as a replacement for permanent wiring
12251 | No missing spacers allowed in electrical panels; All junction boxes, light switches and plug outlets must have cover plates installed
12252 | Commercial Kitchen hood requires minimum 6-MONTH inspection for business operations. Sticker needs to be affixed to hood
12253 | REMOVE all non-functioning life safety and/or fire protection equipment. Specifically remove used fire extinguishers
12254 | Extinguisher(s) missing required labeling
12255 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs
12256 | Required exit signage for egress must be maintained and visible at all times
12257 | Sign/stickers posted on or next to doorway of main entrance - THIS DOOR TO REMAIN UNLOCKED WHILE BUILDING IS OCCUPIED or THIS DOOR TO REMAIN UNLOCKED DURING BUSINESS HOURS. Lettering must be at least 1" tall and contrasting color
12258 | Unlatching of door requires one motion, panic / hotel room type hardware is acceptable - as per Occupancy report 06046184
12259 | Required exit signage for egress must be maintained and visible at all times
12260 | Continuous access to required exit must be maintained. This is the 2nd exit as required by the building department from the Occupancy report proj# 06046184
12261 | NoData
12262 | NoData
12263 | NoData
12264 | NoData
12265 | Repair ASAP.
12266 | Repair ASAP.
12267 | NoData
12268 | NoData
12269 | NoData
12270 | Ensure 3' clearance of all combustibles around electrical equipment/panels.
12271 | On both office exit doors place signage: This door to remain unlock while building is occupied.
12272 | NoData
12273 | NoData
12274 | NoData
12275 | Doors to electrical room(s) must be identified. Add sign to entrance door to riser room and electrical room with "RISER ROOM / ELECTRICAL ROOM UPSTAIRS"
12276 | NoData
12277 | 3-year audibility test needs to be performed, correct any deficiencies and report provided to fire marshal
12278 | Please renew the K1, key box permit. Expired 3/10/21.Please renew the A4, access gate permit. Expired 11/28/19.
12279 | 109.2 Owner/occupant responsibility. Correction and abatement of violations of this code shall be the responsibility of the owner. If an occupant creates, or allows to be created, hazardous conditions in violation of this code, the occupant shall be held responsible for the abatement of such hazardous conditions.
12280 | 3201.3 Construction documents. At the time of building permit application for new structures designed to accommodate high-piled storage or for requesting a change of occupancy/use, and at the time of application for a storage permit, plans and specifications shall be submitted for review and approval. In addition to the information required by the International Building Code, the storage permit submittal shall include the information specified in this section. Following approval of the plans, a copy of the approved plans shall be maintained on the premises in an approved location.Compliance: 30 calendar days.
12281 | 506.1 Where required. Where access to or within a structure or an area is restricted because of secured openings or where immediate access is necessary for life-saving or fire-fighting purposes, the fire code official is authorized to require a key box or a fire depository box to be installed in an approved location. The key box shall be of an approved type listed in accordance with UL 1037, and shall contain keys to gain necessary access as required by the fire code official. Key boxes shall be provided in accordance with Houston Fire Department LSB Standard No. 05, “Key Boxes.”
12282 | 901.6 Inspection, testing and maintenance. Fire detection, alarm, and extinguishing systems, mechanical smoke exhaust systems, and smoke and heat vents shall be maintained in an operative condition at all times, and shall be replaced or repaired where defective. Nonrequired fire protection systems and equipment shall be inspected, tested and maintained or removed.Compliance: 30 calendar days.
12283 | 1006.3 Emergency power for illumination. The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1. Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2. Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3. Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4. Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. Compliance: 30 calendar days.
12284 | NoData
12285 | The fire alarm control unit was found to have a yellow tag attached. Contact a licensed fire protection to correct the violations and ensure a current service tag reflecting the corrections made is attached.
12286 | Because your facility is protected in accordance with NFPA 13 -12.12.1.2 (4), they may be stored indoors as described below "pallets arestored no higher than 6 ft (1.8 m) and each pile of no more than four stacksshall be separated from other pallet piles by at least 8 ft (1.4 m) of clearspace or 25 ft (7.6 m) of commodity". Ensure pallets are arrangedaccordingly.Storage of idle pallets shall comply with NFPA 13NFPA 13 – 2010 Storage of idle wood pallets12.12 Protection of Idle Pallets.12.12.1 Wood Pallets.12.12.1.1Wood pallets shall bepermitted to be stored in the following arrangements:(1) Stored outside(2) Stored in adetached structure(3) Stored indoorswhere arranged and protected in accordance with 12.12.1.212.12.1.2Wood pallets, wherestored indoors, shall be protected in accordance with one of the following:(1) Control modedensity/area sprinkler protection as specified in Table 12.12.1.2(a).(2) CMSA sprinklerprotection in accordance with Table 12.12.1.2(b).(3) ESFR sprinklerprotection in accordance with Table 12.12.1.2(c).(4) Control modedensity/area sprinkler protection in accordance with the OH2 curve of Figure13.2.1 existing with a hose stream demand of at least 250 gpm (946 L/min) for aduration of at least 60 minutes when pallets are stored no higher than 6 ft(1.8 m) and each pile of no more than four stacks shall be separated from otherpallet piles by at least 8 ft (1.4 m) of clear space or 25 ft (7.6 m) ofcommodity. The maximum clearance of 20 ft (6.1 m) specified in 12.1.3.4 shallnot apply to arrangement 12.12.1.2(4).12.12.1.3Idle wood palletsshall not be stored in racks unless they are protected in accordance with theappropriate requirements of Table 12.12.1.2(a) or Table 12.12.1.2(c).(SeeSection C.7.)
12287 | Several rack structures are found to be damaged at the footing where protections were not installed. These racks must be repaired or replaced and maintained to manufacturer standards as specified by approved plans. Should repairs be made, a letter must be signed and stamped by an engineer ensuring all standards have been met.The following locations were noted on inspection: B16-A1, B17-A4, D06-A1, D08-A1, E02-A1, F07-A1, J07-A1, K20-A1, K14-A1, K02-A1, K02-A2Please ensure all damaged footings not listed above are included
12288 | Ensure the proper clearance is maintained by the electrical charging stations as required by code.
12289 | The last drop test completed on the rolling fire door was 4/28/2017. Have the annual drop test performed and tagged. Maintain annual tests
12290 | An alarm company technician shall be on-site during alarm test to ensure the monitoring station is receiving a HAZMAT signal and the Houston Fire Department is the responding agency.
12291 | Must have a licensed fire equipment inspection company inspect and tag all portable fire extinguishers.
12292 | Must have a current tagged portable fire extinguisher mounted on all fork lifts in use with a 10 B:C rating.
12293 | It is the owner's/occupant responsibility to correct all fire code violations prior to permit approval.
12294 | Must secure and cap all cylinders not currently secured or capped.
12295 | Reinspection fee added for failure to complete HMIS, HMMP and maintain adequate aisle space in the storage area for Hazmat materials.Compliance within 30 days
12296 | For Reference
12297 | The Hazardous Materials Management Plan included with this report must be filled out and stored in the Fire Department depository box in a weather proof packet.
12298 | Clearance in aisles must be maintained when not restocking. Ensure adequate aisle space is maintained.
12299 | Complete the HMIS included with this report to account for all Hazardous Materials on site.
12300 | ASSEMBLY PERMIT HAS EXPIRED AND REQUIRES RENEWING.
12301 | NoData
12302 | All extinguishers are in compliance at this time(5-2020)
12303 | See above concerning the fork lift.
12304 | See above- per our conversation remove all obstructions from the exit door by the roll-up door
12305 | Zach- owner of Tell Projects832-591-7991
12306 | See above concerning the storage of material on the lot line.
12307 | See above- per our conversation continue to pursue your Certificate of Occupancy by the city.
12308 | No Violations Found
12309 | Have a licensed fire protection company perform an annual inspection on the sprinkler system and correct any deficiencies.
12310 | Have a licensed fire protection company perform a 5 year FDC test and correct any deficiencies.
12311 | Vent hoods are due for cleaning.
12312 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
12313 | Repair the front exit doors to ensure they swing in the direction of egress.
12314 | Repair or replace inoperable emergency illumination.
12315 | Remove bolt locks from the front exit doors.
12316 | NoData
12317 | NoData
12318 | NoData
12319 | NoData
12320 | HAVE SPRINKLER COVERAGE IN Ainslie Fukuda OFFICE. ANY AREA THAT ISNT COVERED SHOULD BE PLACED UP TO CODE. AS NOTED ONTHE REPORT WHICH WAS IN PLACE DURING INSPECTION.COMPLIANCE WITHIN 30 DAYS.
12321 | APPROVED PLANS ARE TO BE KEPT ON SITE AT ALL TIMES. IF APPROVED PLANS CANNOT BE LOCATED, AREQUEST TO THE BUILDING DEPARTMENT MAY BE ABLE TO DUPLICATE THE ORIGINAL 1002WASHINGTON AVE HOUSTON TEXAS 77002.APPROVED PLANS MUST BE SUBMITTED TO FIRE MARSHAL OR THE PROCESSFOR HIGH-PILED STORAGE PLAN SUBMITTAL PROCESS SHALL BE RESTARTED.COMPLIANCE WITHIN 30 CALENDAR DAYS.
12322 | THE 911 KEY BOX, OR KNOX BOX 3200 SERIESHINGED LID, SHALL BE OF AN APPROVED TYPE LISTED IN ACCORDANCE WITH UL 1037 ANDSHALL CONTAIN KEYS FOR IMMEDIATE ACCESS FOR LIFE-SAVING OR FIRE-FIGHTINGPURPOSES.911 KEY BOX, OR KNOX BOX, SHALL BE LOCATED WITHIN 48 TO 60 INCHESABOVE THE GROUND LEVEL.COMPLIANCE WITHIN 30 DAYS.
12323 | ALL ACCESSDOORS SHALL BE IDENTIFIED WITH LETTERING “HFD”, WHICH MEETS THE ABOVE CODEREQUIREMENTS, BEING MARKED ON THE UPPER LEFT-HAND CORNER OF EACH DOOR. ALL ACCESSAND EXIT DOORS SHALL BE KEYED ALIKETOENSURE ALL FIREFIGHTER ACCESS DOORS HAVEAPPROVED HARDWARE THAT IS READILY OPERABLE FROM THE EGRESS SIDE. (PANICHARDWARE OR LEVER ACTION WHICH OPEN WITH ONE MOVEMENT AND REQUIRE NO SPECIALTOOLS OR KNOWLEDGE)COMPLIANCE WITHIN 30 DAYS
12324 | AQUIRE AN M3 (FUEL DISPENSING) PERMIT WHEN YOUR FUEL TANK IS OPERATIONAL
12325 | BROKEN EMERGENCY LIGHTING NOTED AT REAR EXIT NEAR DOOR 20 - CHECK ALL EMERGENCY LIGHTS FOR PROPER OPERATION
12326 | ENSURE ANNUAL TESTING IS BEING DONE ON EMERGENCY LIGHTING PER ABOVE FIRE CODE
12327 | KEYS IN KEYBOX DID NOT OPEN HFD ACCESS DOORS AROUND BUILDING - HAVE DOORS RE - KEYED AND NOTIFY FIRE INSPECTOR TO REPLACE KEYS IN 911 KEYBOX
12328 | PANIC HARDWARE A REQUIREMENT IN HIGH PILE STORAGE WAREHOUSES. MAKE SURE ALL EXIT DOORS HAVE PANIC HARDWARE INSTALLED.
12329 | MUST PROVIDE 30 INCH MINIMUM SPACING (FRONT, BACK, AND SIDES) FROM ELECTRICAL SERVICE PANELS AND BATTERY CHARGING MODULES TO ANY COMBUSTIBLE MATERIALS. AS WELL, ALWAYS PROVIDE MINIMUM 36 INCH AISLEWAY LEADING TO ELECTRICAL SERVICE PANELS.
12330 | NoData
12331 | NoData
12332 | NoData
12333 | NoData
12334 | NoData
12335 | NoData
12336 | NoData
12337 | APPLY FOR AND OBTAIN A HFD KEY BOX PERMIT (K1) FROM THE CITY OFHOUSTON PERMIT CENTER LOCATED AT 1002 WASHINGTON AVE. (832)394-9000. COMPLIANCE WITHIN 30 DAYS
12338 | For the failure to abate the following violations: Obtaining a 911 key box permit, removal of drop bars and installing approved locks/latches.
12339 | FOLLOW CODE REFERRED TO ABOVE CONCERNINGLOCKS OR LOCKING MAIN ENTRANCE.COMPLIANCE WITHIN 30 DAYS
12340 | The vent hood suppression system is due for service before the end of 03/2021.
12341 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
12342 | Repair the broken emergency illumination in the dining area.
12343 | Remove bolt latch from the rear exit door. Repair panic hardware if necessary.
12344 | Have the kitchen hood suppression system inspected/tested by a certified fire protection company and ensure new tags are placed at the ansul pull station. (Last ansul system tag was noted as 4/2020). This is required every 6 months.
12345 | Have the 5 yr gas test completed by a licensed plumber, ensuring that a permit is pulled through city permitting by the plumber performing the test -OR- provide documentation of a completed test within the last 5 years.
12346 | Renew your P2: Public Assembly permit that expired 1/15/2021 per the instructions on the permit renewal notice.
12347 | Information only.
12348 | Replace failsafe feature on automatic gates.
12349 | Information only.
12350 | FYI: This is a condo community.
12351 | NoData
12352 | NoData
12353 | Portable Fire Extinguisher(s) annual maintenance Dt: 1/21
12354 | NoData
12355 | NoData
12356 | NoData
12357 | NoData
12358 | NoData
12359 | NoData
12360 | Please repair the fire alarm system. Repair any system deficiencies.
12361 | NoData
12362 | NoData
12363 | NoData
12364 | P2 permit is expired. Expired on 2/27/2021. Amount owed 386.44 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Permit Prevention Office.
12365 | NoData
12366 | Last inspection 6/2019Have all fire extinguishers inspected.Inspected 11/2020 - OK
12367 | Correct violations within 60 calendar days.
12368 | Have egress lighting tested and provide documentation that any deficiencies were corrected.
12369 | Document obstructed fire drills.​3/25/2021 - Obstructed drills OK
12370 | By order of the Fire Marshal assignment was to perform a site inspection after the ice storm to inspect the Sprinkler System, Alarm and Water. This location do have busted pipes from the freeze that cause the Sprinkler to be inoperable. I call the Alarm Company [Alarmtechs (281-391-5505)] to verify an operation System and Alarmtechs verified that the System is been Monitoring. Set with the Facility Manager to initiate and sign a inhouse Fire Watch.
12371 | By order of the Fire Marshal assignment was to perform a site inspection after the ice storm to inspect the Sprinkler System, Alarm and Water. This location do have busted pipes from the freeze that cause the Sprinkler to be inoperable. I call the Alarm Company [Alarmtechs (281-391-5505)] to verify an operationSystem and Alarmtechs verified that the System is been Monitoring. Set with the Facility Manager to initiate and sign a inhouse Fire Watch.
12372 | NoData
12373 | NoData
12374 | THIS FACILITY IS NO LONGER IN BUSINESS. BUILDING WAS DEMOLISHED.
12375 | NoData
12376 | NoData
12377 | All extinguishers are in compliance at this time (5-2020)
12378 | See above- per our conversation provide an extinguisher for the fork lift
12379 | Zach- owner832-977-5529
12380 | See above- per our conversation remove all obstructions next to the roll up door
12381 | Repaint Fire Lanes
12382 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
12383 | Provide documentation/report for fire damper testing and any necessary repairs.
12384 | NO VIOLATIONS FOUND
12385 | replace low battery smoke alarms
12386 | repair outside emergency light
12387 | Conduct and document required annual fire safety training.Conducted 1/11/2021 - OK
12388 | Conduct and document obstructed fire drills.
12389 | Conduct and document monthly fire drills.
12390 | Correct all violations within 60 calendar days.
12391 | Obtain smoke detector sensitivity report from alarm company, or obtain signed letter stating that alarm panel internally monitors sensitivity and reports when detectors are out of range.Smart panel. Automatic, internal sensitivity testing.
12392 | Have 90 minute test performed on all required exit signs and emergency lights, and provide documentation that any deficiencies were corrected.
12393 | NoData
12394 | ALL VERTICAL ROLLING FIRE DOORS SHALL BE INSPECTED ANNUALLY BY A LICENSED COMPANY.COMPLIANCE: 30 CALENDAR DAYS.
12395 | ALL LPG CAGES SHALL BE STORED OUTSIDE10 FT AWAY FROM BUILDING.COMPLIANCE: 30 CALENDAR DAYS.
12396 | AN ANNUAL INSPECTION SHALL BE DONE ON FIRE ALARM PANEL BY A LICENSED COMPANY.AN SEMI ANNUAL INSPECTION ISSHALL BEMAINTAINED ON FIRE SUPPRESSION SYSTEM FOR BUILDING A.AN ANNUAL INSPECTION SHALL BE DONE ON THE IN RACK SPRINKLER SYSTEM INSIDE OF MAIN WAREHOUSE.
12397 | ALL PERMITS REQUIRED FOR FACILITY TO OPERATE SHALL BE POSTED OR READY FOR REVIEW.MISSING H2(HIGH PILED ), H1( HAZARDOUS MATERIAL )COMPLIANCE: 30 CALENDAR DAYS.
12398 | ALL PERMITS REQUIRED FOR FACILITY TO OPERATE SHALL BE POSTED OR READY FOR REVIEW.MISSING H2(HIGH PILED ), H1( HAZARDOUS MATERIAL )COMPLIANCE: 30 CALENDAR DAYS.
12399 | NoData
12400 | No violations found.
12401 | Must repair all exit signs/emergency lighting in the business that are not working correctly.
12402 | Ensure the rear exit is free from obstructions.
12403 | Ensure compressed gas cylinders are secured to prevent falling.
12404 | Ensure the locking bar is removed from the rear exit while the building is occupied.
12405 | NoData
12406 | It is the owner/occupants responsibility to correct all violations. Reinspection fees or citations can be issued if the violations are not corrected prior to the follow up date.
12407 | NoData
12408 | The exit sign above the front door did not properly illuminate under battery back up power when tested. Repair or replace the exit sign so that it is properly illuminated under battery back up power in case of a loss of power to the building.
12409 | It is the owner/occupants responsibility to correct all fire code violations in this report.
12410 | Must place "THIS DOOR TO REMAIN UNLOCKED WHEN BUSINESS IS OCCUPIED" on all exit doors.
12411 | Fire extinguisher needs to be properly mounted.
12412 | Owner has the responsibility for all requirement when operating a business.
12413 | Updated service tags and testing needed.
12414 | All required service tags need to be updated and provide documentation on test results.
12415 | Needs service tag.
12416 | NoData
12417 | All need to be tested and documentation showing pass or fail.
12418 | HVAC need to have dampers tested or if smokes are in the system documentation must be provided.
12419 | Updated services tags required. RED TAG
12420 | Required service tags needed
12421 | Building dept. approval must be met before early learning occupancy.
12422 | A technical report must be submitted by a certified license suppression company within 72 hours of this notice identifying the minimum requirement set by code and inspected to correct operations. All sets of plans must be summited for all new installations of fire systems and a copy of the plan must be keep on location at all times for review.
12423 | Need certificate of occupancy for the church and early learning. That was approved by the building dept.
12424 | No records on approved plans for installation of fire alarm system.
12425 | Provide updated P2 permit
12426 | House keeping In storage room removed. Exit door to the public way needs to be corrected and open without problem. All storage under stairway needs to be removed.
12427 | - RENEW F7 PERMIT (FLAMMABLE/COMBUSTIBLE STORAGE AND USE) - EXP. 2/20
12428 | Please repair sprinkler system in 72 hours, maintain a fire watch on building #6 until all repairs are completed.
12429 | Yellow/Red Tagged Fire Alarm Panel.
12430 | Annual generator load test is due.
12431 | While putting locks on 911 boxes, one lock was faulty and would not release my falcon key. Please return faulty lock for a new one.
12432 | 5 year gas test is due
12433 | F7 (Fuel Storage) permit is needed for the generator fuel storage tank
12434 | Please renew your access gate (a4) permit that expired on 03/10/21. If you require an invoice or amount owed, please contact the HPC office @ 832-394-8811 (dial "0"). Thank you!
12435 | NoData
12436 | NoData
12437 | NoData
12438 | NoData
12439 | Spray booth shall be inspected by a licensed HVAC company.Compliance: 30 calendar days.
12440 | NoData
12441 | NoData
12442 | NoData
12443 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
12444 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
12445 | Provide documentation/report for fire damper testing and any necessary repairs.
12446 | Provide certificate of flame resistance, it shall indicate the color for all decorative materials. 1. new curtains, new certificate or 2. new certificate showing retesting of flame resistance.
12447 | Correct 5/29/2019 IMPACT FIRE Yellow tag on Sprinkler System (FDC); Correct Trouble Alert on Fire Alarm System--TROUBLE ALERT CORRECTED
12448 | Owner's responsibility. Comply with the above fire code.
12449 | Have pedestrian gates/doors repaired to open readily from the egress side without the use of a key or special knowledge or effort.
12450 | Have elevators repaired to satisfy IFC requirements. Elevators are required by IFC to be operational for firefighters operation.
12451 | NoData
12452 | Michelle Pirtle 713 910 7774
12453 | service yellow tag sprinkler system
12454 | service private hydrant
12455 | service no tag fire extinguisher in shop and elevator room.
12456 | 3 ft clearance from circuit breaker and water heater
12457 | Label shop, Label Fire alarm room
12458 | repair stairway door.
12459 | repair emergency lighting in hallway.
12460 | post current certificate of occupancy, k1 permit, a4 permit, elevator permit, fire alarm permit.
12461 | replace low batteries smoke detector.
12462 | NoData
12463 | NoData
12464 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL PERFORM A TEST OF ALL THEFIRE ALARM SYSTEM ANNUNCIATION DEVICES NOT LESS THAN EVERY 3 YEARSCOMPLIANCEWITHIN 30 DAYS
12465 | THE 911 KEY BOX, OR KNOX BOX 3200 SERIESHINGED LID, SHALL BE OF AN APPROVED TYPE LISTED IN ACCORDANCE WITH UL 1037 ANDSHALL CONTAIN KEYS FOR IMMEDIATE ACCESS FOR LIFE-SAVING OR FIRE-FIGHTINGPURPOSES.911 KEY BOX, OR KNOX BOX, SHALL BE LOCATED WITHIN 48 TO 60 INCHESABOVE THE GROUND LEVEL.COMPLIANCE WITHIN 30 DAYS.
12466 | HAVE A FALCON LOCK PLACED ON THE 911 BOX OUTSIDE THE DOOR AS PER THE FIRE CODE.COMPLIANCE WITHIN 30 DAYS
12467 | ALLACCESS DOORS SHALL BE IDENTIFIED WITH LETTERING “HFD”, WHICH MEETS THE ABOVECODE REQUIREMENTS, BEING MARKED ON THE UPPER LEFT-HAND CORNER OF EACH DOOR NOTINGOR SHOWING HARDWARE TYPE FOR HFD ACCESS DOORS. THESE DOORS MUST ALLOW ENTRANCEFROM EXTERIOR AS WELL AS EXIT FORM INTERIOR. ALL HFD ACCESS DOORS, NOTED ONPLANS, NEED TO BE KEYED THE SAME.COMPLIANCEWITHIN 30 DAYS.
12468 | NFPA 13: 12.12.1.1 - WOOD PALLETS SHALL BE PERMITTED TO BE STORED IN THEFOLLOWING ARRANGEMENTS:(1) STORED OUTSIDE.(2) STORED IN A DETACHED STRUCTURE.(3) STORED INDOORS WHERE ARRANGED IN ACCORDANCE WITH 12.12.1.2. NFPA 13: 12.12.1.2 – WOOD PALLETS, WHERE STORED INDOORS, SHALL MEET THE FOLLOWING:(1) PALLETS SHALL BE STORED NO HIGHER THAN 6 FEET.(2) EACH PALLET PILE OF NO MORE THAN 4 STACKS SHALL BE SEPARATED FROM OTHER PALLET PILES BY AT LEAST 8 FEET OF CLEAR SPACE OR 25 FEET OF COMMODITY.COMPLIANCE WITHIN 7 DAYS
12469 | NoData
12470 | NoData
12471 | NoData
12472 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
12473 | NoData
12474 | NoData
12475 | NoData
12476 | NoData
12477 | NoData
12478 | NoData
12479 | NoData
12480 | NoData
12481 | NoData
12482 | Do not storyany combustibles within 3 feet of the battery charging station.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
12483 | All fireextinguishers shall have a current annual inspection tag by an approvedlicensed fire protection equipment company.All servicing, testing, maintenance and tagging of listed portable fireextinguishers shall be conducted annually by qualified personnel in accordancewith LSB standard 01, "installation and maintenance of portable fireextinguishers"COMPLIANCE:WITHIN 30 CALENDAR DAYS.
12484 | Exits and exit pathways are to remain clear of obstructions at all times. Do not allow anything to be placed in front of the emergency exits at any time.IMMEDIATE COMPLIANCE REQUIRED
12485 | The owner/occupant shall be heldresponsible for the correction and abatement of all violations listed in thisnotice of violations report. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12486 | Aisles in the rack storage must be kept according tothe code paying special attention to keeping aisles clear of storage. Aislescannot be used for storage. Half of the aisle is always to remain clear.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
12487 | A 4-A/20-B:C fire extinguisher must be properly mounted within 20 feet of the battery charging station.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12488 | Mark the posts of your rack storage at 12 feet from the ground and ensure that your storage stays below the 12 foot mark.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12489 | A workingspace (cleared of all combustible material) of not less than 30 inches inwidth, 36 inches in depth and 78 inches in height shall be provided in front ofelectrical service equipment.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
12490 | HIGH-PILEDCOMBUSTIBLE STORAGE. Storage of combustible materials in closelypacked piles or combustible materials on pallets, in racks or on shelves wherethe top of storage is greater than 12 feet (3658 mm) in height. When requiredby the fire code official, high-piled combustible storage alsoincludes certain high-hazard commodities, such as rubber tires. Group Aplastics, flammable liquids, idle pallets and similar commodities, where thetop of storage is greater than 6 feet (1829 mm) in height.This facility was never approved forhigh-piled storage. Plans were neversubmitted to the building department or the fire marshal’s office for approvalof rack storage of high-piled operation.Lower all class I-IV commodities to a maximumof 12 feet and high-hazard commodities to 6 feet, as required by table 3206.2,for non-sprinklered buildings and maintain commodities at this height. AN OWNER'S STATEMENT MUST BE SIGNED If you choose to become high-piled submit plans to the building department andthe hazmat/high-piled storage team for review and approval for high-piledcombustible storage. Acquiring the expertise of a certified fireprotection engineer for this process is highly advisable.SEE ATTACHED COPY OF HIGH-PILED STORAGE PLANSUBMITTAL GUIDELINE.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
12491 | NoData
12492 | NoData
12493 | NoData
12494 | NoData
12495 | NoData
12496 | Extension cord used for permanent wiring not allowed. Remove extension cord powering water cooler.
12497 | Riser room needs to be identified on room plaque. Wording either "Riser Room" or "Sprinkler Riser" are acceptable
12498 | Please service all internally illuminated exit signs. Found one not working and several that were very dim on battery.
12499 | NoData
12500 | NoData
12501 | Please weld open and/or remove section of gate that can block access point. Gate motor shall be removed as well. Please provide me with a letter explaining the properties decision to remove access gate and motor so future access gate and key box permits will not be required.
12502 | If pedestrian gate is to be locked from the outside, a 911 KNOX BOX (3200 series) is required with a key box (k1) permit.
12503 | Please identify all electrical panels with proper unit number.
12504 | please complete the "Fire Marshal's Office Owners Statement Of Compliance" concerning draft stops. Just have Mr. Jose take a look inside attics space to identify draft stops and conditions. If draft stops are found, please repair all damages.
12505 | Please have a "HFD 0" Sign made and placed on fence. 18"x18" sign shall be RED/WHITE in color.
12506 | please complete the "Fire Marshal's Office Owners Statement Of Compliance" concerning portable fire extinguishers.
12507 | please complete the "Fire Marshal's Office Owners Statement Of Compliance" concerning working smoke alarms locations.
12508 | Please trim tree branches to 14ft.
12509 | NoData
12510 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
12511 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
12512 | Provide documentation/report for annual Load testing and any necessary repairs.
12513 | Provide documentation/report for 5 year FDC testing and any necessary repairs.
12514 | Provide documentation/report for fire damper testing and any necessary repairs.
12515 | Repaint Fire Lane
12516 | The owner / occupant shall be held responsible for the correction and abatement of all violations listed in this notice of violations report. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12517 | Fire detection, alarm, and extinguishing systems shall be maintained in an operative condition at all times and shall be replaced or repaired where defective.The fire protection sprinkler system shall be tested annually by a licensed company and all trouble (yellow and/or red) tag(s) shall be removed and acceptable (white) service tag(s) shall be affixed to ensure system is maintained in operative condition.Fire detection, alarm, and extinguishing systems shall be maintained in an operative condition at all times and shall be replaced or repaired where defective.The fire protection sprinkler system shall be tested annually by a licensed company and all trouble (yellow) tag(s) shall be removed and acceptable (white) service tag(s) shall be affixed to ensure system is maintained in operative condition.IMMEDIATE COMPLIANCE IS REQUIRED
12518 | Fire detection, alarm, and extinguishing systems shall be maintained in an operative condition at all times and shall be replaced or repaired where defective.The fire protection sprinkler system shall be tested annually by a licensed company and all trouble (yellow and/or red) tag(s) shall be removed and acceptable (white) service tag(s) shall be affixed to ensure system is maintained in operative condition. Fire detection, alarm, and extinguishing systems shall be maintained in an operative condition at all times and shall be replaced or repaired where defective.The fire protection sprinkler system shall be tested annually by a licensed company and all trouble (yellow) tag(s) shall be removed and acceptable (white) service tag(s) shall be affixed to ensure system is maintained in operative condition.IMMEDIATE COMPLIANCE IS REQUIRED
12519 | Fire detection, alarm, and extinguishing systems shall be maintained in an operative condition at all times and shall be replaced or repaired where defective.The fire protection sprinkler system shall be tested annually by a licensed company and all trouble (yellow and/or red) tag(s) shall be removed and acceptable (white) service tag(s) shall be affixed to ensure system is maintained in operative condition. Fire detection, alarm, and extinguishing systems shall be maintained in an operative condition at all times and shall be replaced or repaired where defective.The fire protection sprinkler system shall be tested annually by a licensed company and all trouble (yellow) tag(s) shall be removed and acceptable (white) service tag(s) shall be affixed to ensure system is maintained in operative condition.IMMEDIATE COMPLIANCE IS REQUIRED
12520 | Records of all fire protection system inspections, tests and maintenance required by the referenced standards, and all major repairs to the life safety and fire protection equipment systems, shall be maintained on the premises for a minimum of 3 years and shall be copied to the fire code official upon request.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12521 | Perform the proper notifications as required by the Houston LSB standard.
12522 | The fire alarm systems shall be tested annually and audibility test every 3 years by a licensed company and an acceptable tag shall be affixed to ensure system is maintained in operative condition. Records of the test should be maintained for a minimum of 3 years and provided upon request of the fire code official.COMPLIANCE: WITHIN 30 CALENDAR DAYS
12523 | The fire alarm systems shall be tested annually and audibility test every 3 years by a licensed company and an acceptable tag shall be affixed to ensure system is maintained in operative condition. Records of the test should be maintained for a minimum of 3 years and provided upon request of the fire code official.COMPLIANCE: WITHIN 30 CALENDAR DAYS
12524 | All “FIRE DEPARTMENT CONNECTION’S” and “STANDPIPE CONNECTIONS” shall be inspected quarterly by building personnel. Inspections should check for: missing protective caps or covers, damaged hose couplings, couplings not operating freely, missing or deteriorated coupling thread gaskets, and the presence of foreign material. An approved fire department connection "FDC" sign shall be located on or adjacent to the "FDC", on the street front of the building, and shall be constructed of durable material. “FDC” sign shall have the letters "FDC" at least six (6) inches in height. Sign shall be reflective with a red background and white lettering.“FDC” sign shall be labeled with the building address and area of coverage in reflective white letters/numbers no less than two (2) inches in height."FDC" sign shall be placed approximately eight (8) feet above ground level.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12525 | All “FIRE DEPARTMENT CONNECTION’S” and “STANDPIPE CONNECTIONS” shall be inspected quarterly by building personnel. Inspections should check for: missing protective caps or covers, damaged hose couplings, couplings not operating freely, missing or deteriorated coupling thread gaskets, and the presence of foreign material. An approved fire department connection "FDC" sign shall be located on or adjacent to the "FDC", on the street front of the building, and shall be constructed of durable material. “FDC” sign shall have the letters "FDC" at least six (6) inches in height. Sign shall be reflective with a red background and white lettering.“FDC” sign shall be labeled with the building address and area of coverage in reflective white letters/numbers no less than two (2) inches in height."FDC" sign shall be placed approximately eight (8) feet above ground level.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12526 | All “FIRE DEPARTMENT CONNECTION’S” and “STANDPIPE CONNECTIONS” shall be inspected quarterly by building personnel. Inspections should check for: missing protective caps or covers, damaged hose couplings, couplings not operating freely, missing or deteriorated coupling thread gaskets, and the presence of foreign material. An approved fire department connection "FDC" sign shall be located on or adjacent to the "FDC", on the street front of the building, and shall be constructed of durable material. “FDC” sign shall have the letters "FDC" at least six (6) inches in height. Sign shall be reflective with a red background and white lettering.“FDC” sign shall be labeled with the building address and area of coverage in reflective white letters/numbers no less than two (2) inches in height."FDC" sign shall be placed approximately eight (8) feet above ground level.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12527 | The storage of gas fueled equipment is only allowed when the total fuel contained in that equipment is not more than 10 gallons and the whole building is equipped with a working sprinkler system. All liquid gas operated equipment, including any and all motor vehicles, must be removed until the sprinkler system is properly working.IMMEDIATE COMPLIANCE REQUIRED
12528 | No storage is allowed in electrical rooms.IMMEDIATE COMPLIANCE REQUIRED
12529 | A working space (cleared of all combustible material) of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12530 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES. ABIDE BY THE CERTIFICATE OF OCCUPANCY AT ALL TIMES.
12531 | GET ALARM PANEL INSPECTED ANNUALLY.
12532 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES AND KEEP UPDATED PER CODE. TRAIN QUARTERLY.
12533 | Have the fire extinguisher serviced by a licensed fire protection company and ensure a current service tag is attached.
12534 | Properly secure the compressed gas cylinder near the fountain drink machine with a chain.
12535 | Repair or replace the exit sign above the front door. The exit sign should be lit at all times, and should be lit under battery back up power. Remove the exit signs above both doors leading to the rear exit.
12536 | Apply for a Certificate of Occupancy at the Houston Permitting Center and complete the process as outlined by the Building Department.
12537 | Remove the illegal magnetic lock above the front door.
12538 | NoData
12539 | NoData
12540 | NoData
12541 | NoData
12542 | NoData
12543 | NoData
12544 | USING THE FORMAT PROVIDED, A CURRENT HMIS STATEMENT SHALL BE SUBMITTED TO THE HAZMAT / HIGH-PILED 180 TEAM FOR REVIEW. THE HMIS FORM AND INSTRUCTIONS ON HOW TO FILL OUT THE FORM CAN BE FOUND AT THE CITY OF HOUSTON WEBSITE: HTTP://WWW.HOUSTONTX.GOV/FIRE/FORMS/HMISCORRECTLY FILL OUT A NEW HMIS FOR ALL HAZARDOUS MATERIALS STORED INSIDE THE BUILDING. THE WAREHOUSE AREA AND THE HAZARDOUS MATERIALS STORAGE ROOM REQUIRE SEPARATE HMIS’S. THE CLASSIFICATION OF THE HAZARDOUS MATERIALS SHALL COMPLY WITH THE 2012 INTERNATIONAL FIRE CODE CLASSIFICATIONS SYSTEM.IT IS HIGHLY ADVISABLE TO SEEK TECHNICAL ASSISTANCE IN CORRECTLY COMPLETING THE HMIS FOR THE HAZARDOUS MATERIAL BEING STORED ON THE FACILITY.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12545 | APPLY FOR AND OBTAIN A FIRE ALARM PERMIT FROM THE CITY OF HOUSTON PERMIT CENTER LOCATED AT 1002 WASHINGTON AVE. (832-394-9000). COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12546 | AT THE TIME OF INSPECTION, APPROVED H-ROOM PLANS COULD NOT BE PRESENTED FORINSPECTION BY THE FIRE MARSHAL. APPROVED PLANS ARE TO BE KEPT ON SITE AT ALL TIMES. IF APPROVED PLANS CANNOT BE LOCATED, A REQUEST TO THE BUILDING DEPARTMENT MAY BE ABLE TO DUPLICATE THE ORIGINAL.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12547 | THE EXIT PATHWAYS AND EXIT STAIRWAYS LEADING AWAY FROM THE WAREHOUSE SHALL HAVE A CLEAR PATH TO AN AREA OF SAFE REFUGE.COMPLIANCE: WITHIN 7 CALENDAR DAYS.
12548 | NoData
12549 | NoData
12550 | NoData
12551 | NoData
12552 | 2/2020One extinguisher in upstairs electrical room hasn't been inspected since 2017. Have extinguisher updated during next inspection (Due next month)
12553 | Remove all items stored in stairwells.
12554 | Remove all combustible items stored in electrical and mechanical rooms.
12555 | Cover all missing breaker slots.
12556 | Replace all missing ceiling tiles.
12557 | Conduct and document obstructed fire drills.
12558 | Conduct monthly fire drills and provide log for inspector to review.
12559 | Remove all curtains, drapes, and fabrics that are not of fire-retardant materials.
12560 | Provide sign clearly marking location of the FDC.
12561 | Rotate exit signs and/or change chevrons as necessary to ensure that all signs clearly indicate direction of exit(s).
12562 | Label stairwell doors that lead to roof access ladder.
12563 | Correct all violations within 60 calendar days
12564 | Conduct and document required annual fire safety training.
12565 | Have egress lighting tested and provide documentation that any deficiencies were corrected.
12566 | Permit Expired 1/29/2021; Unpaid $177.87
12567 | 2/2020 - OK
12568 | Replace all missing ceiling tiles.
12569 | Conduct and document obstructed fire drills.
12570 | Conduct and document monthly fire drills.
12571 | Label door that leads to roof access ladder.
12572 | Correct all violations within 60 calendar days.
12573 | Panel locked and unable to access. Provide report from last fire alarm inspection.Two missing horn/strobes in office and duct detector in gym does not appear to be working. Have alarm company repair and/or replace.
12574 | Conduct and document required annual fire safety training.
12575 | NoData
12576 | Yearly flow test is required on both F/H's.
12577 | Visually inspect the attic space for solid draft stop construction.
12578 | Three "HFD 2" all weather signs are required on the outside of all emergency gates.
12579 | See Fire Marshal's Statement of Compliance form
12580 | Please Purchase a Access Gate (a4) permit at 1002 Washington Avenue, Houston Tx. 77002 or call 832-394-8811.
12581 | Please Purchase a Key Box (k1) permit at 1002 Washington Avenue, Houston Tx. 77002 or call 832-394-8811.
12582 | Please add a 911 Falcon lock on back gate for HFD access
12583 | NoData
12584 | Sign needed on for n umber of hydrants on the property. HFD 0.
12585 | Ensure there are small fire extinguishers in each unit and charged. Proper sized fire extinguisher need in the boiler /storage room.
12586 | Proof of gas test needed. If the gas test is not performed within 5 years, one should be performed.
12587 | 3 gas cans were left underneath stairway near the pedestrian entrance to the right.
12588 | Directory map needed for property.
12589 | Ensure there are smoke detectors in each bedroom and hallway leading into room. The smoke detectors should be the tamper resistant type, 10 year battery life
12590 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES. ABIDE BY CERTIFICATE OF OCCUPANCY AT ALL TIMES.
12591 | GET ALARM SYSTEM INSPECTED ANNUALLY.
12592 | KEEP EMERGENCY EVACUATION PLANS ON PROPERT AT ALL TIMES. KEEP UPDATED PER CODE AND TRAIN QUARTERLY.
12593 | NoData
12594 | Permit Expired 1/29/2021; Unpaid $385.38
12595 | NoData
12596 | Multiple fire extinguishers that are mounted and assigned to the occupancy for fire safety were found to be red tagged. Have all assigned red tagged fire extinguishers serviced by a licensed fire protection company and ensure a current service tag is attached.
12597 | Properly secure the compressed gas cylinders in the warehouse with a chain or strap to the wall or other stable/immovable object.
12598 | Mount a fire extinguisher with a minimum rating of 2:A 10:BC and a current service tag on the second floor storage area of the warehouse.
12599 | Have all exit signs serviced to ensure they will illuminate under battery back up power in case of a power outage.
12600 | Have all exit signs serviced to ensure they are properly illuminated under regular service power.
12601 | Exits must be clear of obstructions.
12602 | Reposition or remove desk in front of warehouse exit.
12603 | Have all fire extinguishers inspected annually.
12604 | Store propane outside of building.
12605 | NoData
12606 | NoData
12607 | NoData
12608 | NoData
12609 | Need access gate permit. Permit office located at 1002 Washington Ave.
12610 | Need key box permit. Permit office located at 1002 Washingtom Ave.
12611 | Gate right of office needs failsafe box repaired and new pad lock installed. Gate left of office needs pad lock installed on failsafe. I will place new keys to pad locks in main 911 boxes.
12612 | NoData
12613 | NoData
12614 | No violations found at this time. - Fire alarm annual inspection - done 12/3/2020 - Fire extinguisher annual inspection - done 8/2020
12615 | NoData
12616 | NoData
12617 | NoData
12618 | NoData
12619 | NoData
12620 | NoData
12621 | A LICENSED FIRE PROTECTION SERVICE COMPANY SHALL CONDUCT HYDROSTATIC AND FLOW TESTS OF ALL FIREDEPARTMENT CONNECTIONS, PIPING AND CHECK VALVE ASSEMBLIES, NOT LESS THAN EVERY FIVE (5) YEARS.PROVIDE WRITTEN REPORT OF INSPECTION FINDINGS IF COMPLETED WITHIN THE LAST FIVE (5) YEARS.COMPLIANCE:WITHIN 30 CALENDAR DAYS.
12622 | EXIT SIGNS SHALL BE ILLUMINATED AT ALL TIMES. TO ENSURE CONTINUED ILLUMINATION FOR ADURATION OF NOT LESS THAN 90 MINUTES IN CASE OF PRIMARY POWER LOSS, THE SIGNILLUMINATION MEANS SHALL BE CONNECTED TO AN EMERGENCY POWER SYSTEM PROVIDEDFROM STORAGE BATTERIES, UNIT EQUIPMENT OR AN ON-SITE GENERATOR.COMPLIANCE: WITHIN 30CALENDAR DAYS.
12623 | NoData
12624 | NoData
12625 | NoData
12626 | NoData
12627 | NoData
12628 | NoData
12629 | NoData
12630 | NoData
12631 | MAKE SURE ALL PORTABLE FIRE EXTINGUISHERS HAVE A CURRENT INSPECTION TAG ON THEM AND HUNG ON A BRACKET
12632 | MAKE SURE ALL PORTABLE FIRE EXTINGUISHERS HAVE A CURRENT INSPECTION TAG ON THEM AND HUNG ON A BRACKET
12633 | MAKE SURE BOTH THE LEFT AND RIGHT SIDE EXIT DOORS REMAIN UNLOCKED DURING BUSINESS HOURS
12634 | INSTATLL SPACERS IN THE OPEN GAPS OF THE ELECTRICAL PANEL
12635 | APPLY FOR AND POST THE M3(FUEL DISPENSER) AND THE L1(PROPANE STORAGE) PERMIT AT 1002 WASHINGTON AVE. 832-394-8811
12636 | NoData
12637 | NoData
12638 | NoData
12639 | NoData
12640 | NoData
12641 | NoData
12642 | NoData
12643 | NoData
12644 | NoData
12645 | NoData
12646 | NoData
12647 | NoData
12648 | NoData
12649 | NoData
12650 | NoData
12651 | NoData
12652 | NoData
12653 | NoData
12654 | NoData
12655 | NoData
12656 | NoData
12657 | NoData
12658 | NoData
12659 | NoData
12660 | NoData
12661 | NoData
12662 | NoData
12663 | NoData
12664 | NoData
12665 | See above for the Fire extinguishers (all of the current extinguishers are out of date) 2-2016
12666 | Apply for the (F7) permit with the permitting office.
12667 | Please renew the A4, access gate permit. Expired 3/11/21.
12668 | THE REQUIRED 5 YEAR GAS TEST IS DUE FOR YOUR PLACE OF BUSINESS. THE LAST TEST WAS PERFORMED 4-29-2014.
12669 | THE REQUIRED 5 YEAR GAS TEST IS DUE FOR YOUR PLACE OF BUSINESS. THE LAST TEST WAS PERFORMED 4-29-2014.
12670 | BEFORE GAS TEST IS PERFORMED A PERMIT MUST BE OBTAINED FROM THE HOUSTON PERMITTING OFFICE.
12671 | EXIT LIGHT LOCATED AT FRONT ENTRANCE AND SIDE DOOR NEED TO BE REPAIRED OR REPLACED. LIGHT SHOULD BE ILLUMINATED AT ALL TIMES.
12672 | HAVE ALL EMERGENCY ILLUMINATION LIGHTS REPAIRED OR REPLACED. CHECK LIGHTS BY PRESSING THE TEST BUTTON LOCATED ON THE SIDE OR BOTTOME OF LIGHT. CHECK THE BATTERIES INSIDE OF LIGHTS SHOULD THEY NEED REPLACING.
12673 | POST CERTIFICATE OF OCCUPANY AND ASSEMBLY PERMIT IN A LOCATION THAT IS READILY AVAILABLE FOR INSPECTION.
12674 | ADD SIGN/DECAL TO FRONT DOORS THAT READS, "THESE DOORS SHALL REMAIN UNLOCKED DURING BUSINESS HOURS".
12675 | Please renew the K1, key box permit. Expired 2/28/21.Please renew the A4, access gate permit. Expired 2/28/21.
12676 | Owner's responsibility. Comply with the above fire code.
12677 | The fire alarm panel is red tagged dated 3/9/2021. Have the fire alarm system serviced to achieve compliance status within 72 hours. The sprinkler system to the parking garage is red tagged. Have the sprinkler system serviced to achieve compliance status.Initiate a in house fire watch until both fire protection systems are returned to compliant status.In house fire watch assignment agreement form signed.I performed a reinspection on Monday 3/22/2021. The F/A panel has been replaced with a new panel and is yellowed tagged as of 3/22/2021. Supporting documentation is attached.
12678 | NoData
12679 | NoData
12680 | NoData
12681 | NoData
12682 | NoData
12683 | Please service the red tagged fire alarm system within 72 hours. Life safety equipment shall be operational at all times. Contact the Fire Inspector if more time is needed for repairs.
12684 | Make all code violation corrections prior to the re-inspection date on page one.
12685 | Provide current audibility test documentation within the last 3 years for the fire alarm system.Test documentation must have one of two things to be acceptable. A) Must show each audibility device’s ambient decibel level and the decibel level when the device is active. The difference in DB level must fall within NFPA 72’s acceptable range for the device to pass the test. OR B) A document from their company on company’s letter head that has the following information – 1) Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all audibility devices passed the audibility test as required by NFPA 72.
12686 | By order of the Fire Marshal assignment was to perform a site inspection after the ice storm to inspect the Sprinkler System, Alarm and Water. This location do have busted pipes from the freeze that cause the Sprinkler to be inoperable. I call the Alarm Company to verify an operation System and Alarmtechs verified that the System is been Monitoring. Set with the Facility Manager to initiate and sign a inhouse Fire Watch.
12687 | NoData
12688 | NoData
12689 | NoData
12690 | NoData
12691 | Please renew Key Box permit, expired 11-4-19.
12692 | NoData
12693 | NoData
12694 | Please sign Fire Marshal's Office Owners Statement of Compliance document provided to you.
12695 | NoData
12696 | Please sign Fire Marshal's Office Owners Statement of Compliance document provided to you.
12697 | Owner's responsibility. Comply with the above fire code.
12698 | The fire alarm panel is red tagged dated 3/9/2021. Have the fire alarm system serviced to achieve compliance status within 72 hours. The sprinkler system to the parking garage is red tagged. Have the sprinkler system serviced to achieve compliance status.Initiate a in house fire watch until both fire protection systems are returned to compliant status.In house fire watch assignment agreement form signed.I performed a reinspection on Monday 3/22/2021. The F/A panel has been replaced with a new panel and is yellowed tagged as of 3/22/2021. Supporting documentation is attached.
12699 | Have a licensed fire protection company perform an annual fire alarm inspection and correct any deficiencies.
12700 | Have a licensed fire protection company perform an annual fire sprinkler inspection and correct any deficiencies.
12701 | Have a licensed fire protection company perform a 5 year FDC inspection and correct any deficiencies.
12702 | The fire sprinkler system requires monitoring.
12703 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
12704 | Label water heater room.
12705 | Repair wall penetration in water heater room.
12706 | Fire Extiguisher is out of date required annual service.
12707 | Elizabeth Pugh 8326999773
12708 | NoData
12709 | Please renew the K1, key box permit. Expired 3/15/20.Please renew the A4, access gate permit. Expired 3/19/20.
12710 | NoData
12711 | NoData
12712 | NEED SERVICE LAST DATE 8-20
12713 | NEED SERVICE , 5-2020 LAST DATE
12714 | FAILURE TO SERVICE FIRE EXTINGUISHERS. 9-18 LAST DATE
12715 | NoData
12716 | NEED SERVICE, 9-2018 LAST DATE
12717 | FAILURE TO SERVICE FIRE EXTINGUISHERS. 6-18 LAST DATE
12718 | NoData
12719 | NEED SERVICE 6-18 LAST DATE
12720 | NoData
12721 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
12722 | NO LONGER BEING USED AS A SCHOOL. VACANT CAMPUS.
12723 | The Fire Alarms in each building Annual Inspection tag is out of date by more than a year. Perform the Fire Alarm Annual Inspection as required by code.
12724 | Make Repairs to the Fire Alarm SystemMaintain Self-Fire Watch until the repairs are made and the fire alarm system is back in service.
12725 | Owner's responsibility. Comply with the above fire code.
12726 | The fire alarm panel has an yellow tag attached for 4300 and 4310 Dunlavy. Have fire alarm system serviced to achieve compliant status. Sprinkler system shows to be compliant at this time. Performed reinspection on 3/29. The F/A system at 4300 Dunlavy has been repaired. Supporting photos is attached. The F/A system at 4310 Dunlavy is red tagged as of 3/22. Spoke with Savanna of monitoring and she state F/A system was still receiving and sending notifications. Spoke with Jeff of Wilson fire and he stated that they would repaired the panel on 4/5/2021.
12727 | Owner's responsibility. Comply with the above fire code.
12728 | The fire alarm system has been red tagged dated 3./8/2021.The sprinkler system has also been red tagged and have no water pressure.Have the fire alarm and sprinkler systems repaired to compliant status.A continuous in house fire watch shall be implemented 24 hours 7 days a week until both systems have been repaired.Sign Fire Watch Assignment Agreement form.
12729 | NoData
12730 | NoData
12731 | NoData
12732 | NoData
12733 | The fire extinguisher located under the bar is past due for service.
12734 | Repair the inoperable emergency illumination on the exit sign located at the side exit.
12735 | The assembly permit is due for renewal before the end of 03/2021.
12736 | remove all trash and rubbish plastic bags from inside warehouse that are creating a fire hazard in bldg. 400 and all boxes and papers on bldg. 400B
12737 | replace electrical metal cover missing in the main panel on bldg. 400B and on bldg. 400 replace outlet electrica plastic cover that is missing in the office area
12738 | NoData
12739 | remove all trash and rubbish plastic trash bags
12740 | remove boxes down for proper clearance from metal storage rack for fire fighting in case of fire
12741 | provide and install #400 on scorpion's metal shop and #400 B on LA BODEGA DEL PACO
12742 | label all electrical breakers to identified locationsfor example office ,restroons .bay area exc.
12743 | remove all extension cords not use on permanet appliances
12744 | all wiring under conduit piping
12745 | remove all L.P.gas bottles right away to the out of the bldg. and provide and install in a metal cage on the ones that are going to be kept .L.P.GAS BOTTLES THAT ARE FULL OR EMPTY are very dangerous to employees or fire fighters during a fire that's why they are require by the fire code to be outside of the building.
12746 | all fire extinguishers shall be inspected and tag by a certified company and tag plus mounted on a metal rack and not put on the ground.
12747 | provide and install a plain exit sign on westside exit door leading directly to the out side of the bldg. located in the office area
12748 | provide and install a metal cage for all L.P GAS bottles to be stored outside of the bldg. plus applied for a permit if storing more than the required amount along with a no smoking sign
12749 | provide and install a 21/2 fire extinguisher on the l.p.gas fork lift been use on your property on bldg. 400 and on bldg. 400B provide and install a 20 pound abc fire extinguisher plus mounted
12750 | provide and install metal chains and all compress gas bottles use for open flames on metal work or cutting and welding plus replace missing caps on bldg. 400 and on bldg. 400b chain metal restrain and cap missing on air compress bottle only
12751 | make application for a certificate of occupancy from the bldg. dept 1002 Washington bldg. dept.
12752 | provide and install sign on middle part of the office door leading towards the outside of the bldg
12753 | Gates must approved by fire dept. in accordance with LSB 4 that was sent to you via email.
12754 | Gates must approved by fire dept. in accordance with LSB 4 that was sent to you via email.
12755 | Ensure all electrical panels are marked with appropriate unit number.
12756 | Ensure draft stops in the attics are in in place and in tact, no holes.
12757 | Ensure draft stops are in place and in tact.
12758 | Hydrant signs on gates must indicate the number of hydrants on the property. HFD "0".
12759 | Ensure all apt units has a working fire extinguisher
12760 | Gas test needed for this property.
12761 | Access gate and Key box permits need to be on property.
12762 | Gates must approved by fire dept. in accordance with LSB 4 that was sent to you via email.
12763 | NoData
12764 | NoData
12765 | NoData
12766 | NoData
12767 | NoData
12768 | Mount the fire extinguisher that's been placed on the ground.
12769 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
12770 | Clear and maintain space in front of the breaker panels.
12771 | Post the occupant load.
12772 | NoData
12773 | NoData
12774 | NoData
12775 | NoData
12776 | NoData
12777 | NoData
12778 | NoData
12779 | NoData
12780 | NoData
12781 | NoData
12782 | Fire extinguishers last inspected and tested November 2019. Have all fire extinguishers inspected and tested.
12783 | NoData
12784 | Renew p2 (Places of Assembly) permit at 1002 Washington (832.394.8811).
12785 | NoData
12786 | NoData
12787 | NoData
12788 | HAVE SIGNAGE ON DOOR STATING "DOOR SHALL REMAIN OPEN DURING BUSINESS HOURS"COMPLIANCE WITHIN 30 DAYS
12789 | NoData
12790 | NoData
12791 | NoData
12792 | THE SPRINKLER SYSTEM NEED TO BE SERVICE OR SHOW PROOF OF APPROVED INSPECTION TAGS
12793 | NoData
12794 | Last inspection date 10-11-19. Need service in October. Need to put a fire panel inside sign by the door. Room 164 -BCR/BDP
12795 | Need service. Last inspection 11-2017
12796 | NoData
12797 | NoData
12798 | NoData
12799 | NoData
12800 | NoData
12801 | NoData
12802 | 24" clearance must be maintained between ceiling and combustible materials (Non-sprinkled building)
12803 | NoData
12804 | NoData
12805 | NoData
12806 | NoData
12807 | NoData
12808 | NoData
12809 | NoData
12810 | NoData
12811 | NoData
12812 | NoData
12813 | NoData
12814 | NoData
12815 | STANDPIPE SYSTEMS SHALL BE TESTED ANNUALLY BY A LICENSED COMPANY AND AN ACCEPTABLE TAGE SHALL BE AFFIXED TO ENSURE SYSTEM IS MAINTAINED IN OPERATIVE CONDITION. (YELLOW TAG IMPAIRMENT) COMPLIANCE: 7 DAYS.
12816 | THE HIGH-PILED STORAGE PROCESS IS INCOMPLETED FOR THE FINAL ONSITE. PLEASE HAVE YOUR FIRE PROTECTION ENGINEER TO CALL 832-394-9350 FOR THE FINAL ONSITE OR YOU WILL HAVE TO LOWER THE COMMIDITIES ON THE RACK TO UNDER 12 FEET.COMPLIANCE: 1 DAY
12817 | NoData
12818 | NoData
12819 | NoData
12820 | Provide updated Permit.
12821 | RENEW F7 (FLAMMABLE/COMBUSTIBLE) PERMIT THAT EXPIRED ON 2-2-21.
12822 | F-7 PERMIT FLAMMABLE AND COMBUSTIBLE LIQUID PERMIT EXPIRED
12823 | Provide 1st Floor Electrical Cover Plate in Electrical Room and 2nd floor Mechanical Room Stair "B."
12824 | Provide continuous mounting of Fire Extinguishers when not in use. Several Fire Extinguisher discovered off the mount in rooms.
12825 | NoData
12826 | NoData
12827 | Replace or Repair Stair "B" 3rd floor Exit Sign and Stair "A" 2nd floor Exit Sign.
12828 | Provide Current Annual Inspection Tags for the Fire Hose and Fire Extinguishers.
12829 | Provide Current Annual Inspection Tags for the Fire Hose and Fire Extinguishers.
12830 | Provide bright Red paint for front entrance Key Box.
12831 | Provide Emergency Contact List and Mobility Impaired List for Fire Depository Box.
12832 | Replace Ceiling Tile inside 1st floor Electrical Room and 2nd floor Mechanical Room (Stair "B").
12833 | Throughout Equipment Rooms.
12834 | NoData
12835 | Provide Current Annual Key Box Permit.
12836 | NoData
12837 | K1-permit expired
12838 | Permits Expired 1/31/2021; Unpaid $652.18
12839 | replace missing circuit breaker cover and spacer.
12840 | Provide copy of lease agreement with Flame cooking policy or addendum.
12841 | Label boiler room
12842 | check all fire extinguishers, Provide copy of lease agreement with fire extinguisher policy or addendum.
12843 | Required every 5 years and must be completed with an approved permit from theBuilding Department.
12844 | check all smoke alarm, Provide copy of lease agreement with smoke detector or addendum.
12845 | NoData
12846 | Please remove all chains from manual gates. All manual gates shall be secured with a master lock and appropriate key places inside the 911 box.
12847 | NoData
12848 | Electrical Boxes: Electrical panel/box and rooms shall be visibly, legibly and durably marked as required in this section to indicate the unit it services. 2012 I.F.C. 605.3.1
12849 | Draft stops shall be spot checked in accordance with your normal inspection procedures. When draft stops have been altered, damaged, breached or penetrated the notice of violation should include instructions to have a responsible contractor inspect all draft stops in the complex and itemize repairs made for each building and include a statement on their letterhead that all draft stops have been inspected and have been repaired or replaced to the required fire-resistance-rated construction required in accordance with the Houston Fire and Building Codes. (Note: At the very least they are required to obtain a repair permit thru one stop at Building Department)
12850 | Please provide a blue marker (reflector) next to all fire hydrants located on property.
12851 | Please paint all 911 boxes RED on property.
12852 | Draft Stops: 1. Draft stops shall be provided and maintained as required. Draft stops shall be spot checked in accordance with your normal inspection pr When draft stops have been altered, damaged, breached or penetrated the notice of violation should include instructions to have a responsible contractor insp all draft stops in the complex and itemize repairs made for each building and include a statement on their letterhead that all draft stops have been inspected and have been repaired or replaced to the required fire-resistance-rated construction required in accordance with the Houston Fire and Building Codes. (Note: At the very least they are required to obtain a repair permit thru one stop at Building Department) Occupancies in Group R-2 that do not exceed four stories in height, the attic space shall be subdivided by draft stops into areas not exceeding 3,000 square feet or above every two dwelling units, whichever is smaller. Provide site map or blue prints indicating the location of the attic access and the draft stops. Attic access shall be provided for the follow up inspection. Draft stops have been provided and shall be maintained as required. Doors have been provided in the draft stops for access, these doors are required to be closed at all times, if doors do not stay in the closed positio repairs or replacement shall be made.
12853 | Gas Test: Every 5 years, a pneumatic test of your natural gas system must be conducted blicensed plumber. Proof that you've had this test is a "verification affidavit" by the city plumbing inspector.
12854 | HFC 308.1 - OPEN FLAME COOKING DEVICES: ALL TENANTS HAVE ACKNOWLEDGED AND SIGN OUTDOOR COOKING POLICY WITHIN THE LEASE AGREEMENT OR OUTDOOR COOKING ADDENDUM
12855 | Hydrant Signs: 1. 18" X 18" H.F.D. signs shall be provided as per this section. 2. For complexes without any fire hydrants, the number "0" shall be placed the letters HFD PLEASE ATTACH HFD SIGNS ON ALL ACCESS GATES ON PROPERTY,
12856 | FIRE ALARM SYSTEM: ANNUAL ALARM SYSTEM INSPECTION WAS DONE BY FIRE PROFESSIONAL SERVICES INC. 02/19/2019 AND WAS ISSUED AN ACCEPTABLE RATING.
12857 | NoData
12858 | Trash: 1. Trash and rubbish shall not be stored or placed on the ground, street, sidewalks or around buildings or dumpster. 2. Remove all improperly stored materials from the property or place the materials into the dumpster. Over flowing dumpster shall be immediately discarded.
12859 | ALL FIRE HYDRANTS LOCATED ON PROPERTY SHALL HAVE A BLUE REFLECTOR LOCATED IN D MARKING THE LOCATION OF FIRE HYDRANT.
12860 | NoData
12861 | NoData
12862 | Access Gates - Fire Department Approval If property has controlled access gates, a set of drawings approved by the Fire Marshal's office must be available on site. 503.6 Security gates. The installation of security gates across a fire apparat access road shall be approved by the fire code official in accordance with Houston Fire Department LSB Standard No. 04, "Access Control Gates." Where security gates are installed, they shall have an approved means of emergency operation. The security gates and the emergency operation shall be maintained operational at all times, or secured in the open position. Repairs shall be in accordance with original specifications and approvals. Douglas.mendizabal@houstontx.gov 281-785-8310 Note: Access gate plans and a letter of explanation shall be submitted for approved by the Fire Marshal's office as required. Fire Marshal approved plans shall remain on site for any future referenc by the Code Official. Emergency access shall be provided and maintained at all times as\ required in this section. Damaged or inoperable gates shall remain in the open position until repairs or replacement is made. Repair or replace the Failsafe operation/box as needed.
12863 | FIRE SPRINKLER SYSTEM: ANNUAL SPRINKLER SYSTEM INSPECTION WAS DONE BY FIRE PROFESSIONAL SERVICES INC. 02/19/2019 AND WAS ISSUED A YELLOW TAGS IN ALL RISER ROOMS NOTING PAINTED HEADS. PLEASE HAVE ALL YELLOW TAGS ADDRESSED AND CORRECTED ON ALL BUILDINGS.
12864 | NoData
12865 | COMPLIANCE DATE 15 CALENDAR DAYS.
12866 | At this time the (K1 & A4) permit is expired and need to be updated immediately.
12867 | Mount extinguisher on wall.
12868 | Remove extension cords used as permanent source of power.
12869 | Replace missing spacers.
12870 | NoData
12871 | fire extinguishers expired last inspected Feb 2019;corrected annual mar 2021
12872 | violations corrected
12873 | NEED TO DO THE ANNUAL FIRE PUMP TESTING
12874 | NEED TO ADD KEY BOX TO PARKING GARAGE
12875 | Continue maintain all permits required as per the city of Houston fire and building codes
12876 | THERE SHALL BE NO COMBUSTIBLE MATERIAL STORAGED WITHIN 3 FT IN ALL DIRCETIONS OF BATTERY CHARGERS STATION.COMPLIANCE WITHIN 30 DAYS
12877 | A LICENSED FIRE PROTECTION SERVICE COMPANY SHALL CONDUCT HYDROSTATIC AND FLOW TESTS OF ALL FIRE DEPARTMENT CONNECTIONS, PIPING AND CHECK VALVE ASSEMBLIES, NOT LESS THAN EVERY FIVE (5) YEARS.PROVIDE WRITTEN REPORT OF INSPECTION FINDINGS IF COMPLETED WITHIN THE LAST FIVE (5) YEARS.COMPLIANCE: WITHIN 30 CALENDAR DAYS
12878 | REPAIR AND OR REPLACE ALL EXIT DOOR THAT ARE NOT FULLY FUNCTIONAL THROUGHOUT THE FACILITY.COMPLIANCE WITH 7 DAYS
12879 | ROMOVE ALL COMBUSTIBLE MATERIALS FROM ELECTRICAL ROOM AND OR RISER ROOM COMPLIANCE WITHIN 30 DAYS
12880 | EXTENSION CORDS SHALL NOT BE USED FOR A PERMIT SOURCE OF POWER IN FACILITY. COMPLIANCE WITHIN 30 DAYS
12881 | THE REQUIRED FIRE-RESISTANCE RATING OF FIRE-RESISTANCE-RATED CONSTRUCTION SHALL BE MAINTAINED.SUCH ELEMENTS SHALL BE PROPERLY REPAIRED, RESTORED OR REPLACED WHEN DAMAGED, ALTERED, BREACHED OR PENETRATED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
12882 | THE ROLLING FIRE DOORS SHALL BE ANNUALLY INSPECTED BY A LICENSED FIRE PROTECTION COMPANY TO ENSURE PROPER OPERATION IN THE EVENT OF EMERGENCY.COMPLIANCE WITHIN 30 DAYS.
12883 | HAND-HELD PORTABLE FIRE EXTINGUISHERS SHALL BE INSTALLED ON THE HANGERS OR BRACKETS SUPPLIEDCOMPLIANCE WITHIN 30 DAYS.
12884 | A PERMIT SHALL BE OBTAINED PRIOR TO ENGAGING IN ANY ACTIVITIES, OPERATIONS, PRACTICES, OR FUNCTIONS REGULATED BY THIS CODE AND REQUIRING A PERMIT AS LISTED IN SECTION 105.6.IT SHALL BE UNLAWFUL FOR ANY PERSON TO ENGAGE IN ANY ACTIVITIES, OPERATIONS, PRACTICES OR FUNCTIONS WITHOUT HOLDING A CURRENT AND VALID PERMIT. ISSUED PERMITS SHALL BE KEPT AT FACILITY AT ALL TIMES AND SHALL BE READILY AVAILABLE FOR INSPECTION BY THE FIRE CODE OFFICIAL.APPLY FOR AND OBTAIN A (H3) (HOTWORK) OPERATIONAL PERMIT FROM THE CITY OF HOUSTON PERMITTING CENTER LOCATED AT 1002 WASHINGTON AVE. (832-394-9000).COMPLIANCE WITHIN 30 DAYS
12885 | NFPA 13: 12.12.1.1 - WOOD PALLETS SHALL BE PERMITTED TO BE STORED IN THE FOLLOWING ARRANGEMENTS:(1) STORED OUTSIDE. (2) STORED IN A DETACHED STRUCTURE. (3) STORED INDOORS WHERE ARRANGED IN ACCORDANCE WITH 12.12.1.2. NFPA 13: 12.12.1.2 – WOOD PALLETS, WHERE STORED INDOORS, SHALL MEET THE FOLLOWING:(1) PALLETS SHALL BE STORED NO HIGHER THAN 6 FEET. (2) EACH PALLET PILE OF NO MORE THAN 4 STACKS SHALL BE SEPARATED FROM OTHER PALLET PILES BY AT LEAST 8 FEET OF CLEAR SPACE OR 25 FEET OF COMMODITY.COPLIANCE WITHIN 7 DAYS
12886 | Replace missing light covers.
12887 | Replace missing cover plate.
12888 | Fire extinguishers must be inspected and tagged annually.
12889 | Place fire extinguisher on bracket.
12890 | NoData
12891 | NoData
12892 | Remove pad lock from door to ensure someone can exit from the inside of the paint room per code.
12893 | Remove combustible storage from main electrical room on level 14 per code.
12894 | Ensure quantities of hazardous materials do not exceed maximum allowable quantities per code.
12895 | Relocatable power taps shall be directly connected to permanently installed receptacles per code.
12896 | Extension cords shall not be a substitute for permanent wiring. Remove extension cord and add permanent wiring per code.
12897 | No 20lb LP containers allowed. Remove 20lb tank immediately per code.
12898 | Code relating to HFC 6103.2. For reference regarding LP gas tanks.
12899 | Return the above listed locations to their designed fire rated construction per code.
12900 | Remove the door holder so the door closes and latches from the open position.
12901 | Have fire protection company evaluate the 14th floor upper tool room storage area for sprinkler coverage. Add additional sprinkler heads were required.
12902 | Correct occupant side re-entry signage per code. Send proof to inspector for approval prior to printing.
12903 | Correct stairway Re-entry sign for level 17 stair D. Send proofs to inspector for approval prior to printing.
12904 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriateinspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualEmergency radio coverage- AnnualFire Extinguishers- AnnualDry pipe partial- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualDry pipe full- 3 YearFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearClean agent – Semi-annualKitchen Hood System- Semi-annualBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
12905 | Do not store incompatible materials in flammable liquid cabinet per code.
12906 | Maintain clearance space around breaker boxes per code.
12907 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. • Present Permits that apply to facility Address listed • on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS.
12908 | All fire extinguishers must be inspected annually
12909 | Propane tanks must be stored outside.
12910 | Replace missing cover plate
12911 | Renew oil storage permit
12912 | Expired Access Gate Permit. (A4)
12913 | Expired (K1) Key/Fire Depository Box
12914 | NoData
12915 | Expired Key/Fire Depository Box (K1)
12916 | Red Tag 6/20
12917 | need oily rag can in high-rise elevator penthouse.
12918 | update mobility impairment listconfirm information on emergency contact list
12919 | Missing
12920 | fill penetration.
12921 | Echo in phone lines
12922 | Permit Expired 2/5/2021; Unpaid $267.53
12923 | Provide report for annual test and service tag for fire alarm system.
12924 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
12925 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
12926 | Provide Documentation/Report and tag for the 5th Year FDC Hydrostatic test.
12927 | Provide documentation/report for fire damper testing and any necessary repairs.
12928 | Repaint Fire Lane
12929 | Correct 3/16/2021 Advantage Interests Yellow Tag on Sprinkler System
12930 | COMPLIANCE DATE: 15 CALENDAR DAYS
12931 | C7,P2,L1 permits are expired and must be updated immediately.
12932 | P2 (ASSEMBLY PERMIT) EXPIRED ON 2-19-21. RENEW PERMIT ONLINE OR IN PERSON AT THE HOUSTON PERMITTING CENTER.
12933 | NoData
12934 | NoData
12935 | NoData
12936 | NoData
12937 | NoData
12938 | Correct all violations within 60 calendar days.
12939 | Have audibility test performed and provide documentation that deficiencies were corrected.1/26/2021 - OK
12940 | Conduct and document required annual fire safety training.1/15/2021 - OK
12941 | Cover all open junction boxes and empty breaker slots.
12942 | Conduct and document obstructed fire drills (50%).
12943 | Conduct and document monthly fire drills.
12944 | Fire alarm panel is showing trouble. Have a licensed fire alarm company correct trouble condition(s).Corrected 2/24/2021
12945 | Have detector sensitivity test performed and provided documentation that deficiencies were corrected.1/18/2021 - OK
12946 | Have 90 minute egress lighting test performed by a licensed electrician and provide documentation that deficiencies were corrected.1/26/2021 - Passed, OK
12947 | NoData
12948 | NoData
12949 | NoData
12950 | NoData
12951 | NoData
12952 | NoData
12953 | NoData
12954 | NoData
12955 | NoData
12956 | NoData
12957 | NoData
12958 | Make all code violation corrections prior to the re-inspection date noted on page 1. All code violations have been corrected
12959 | The annual fire alarm system inspection is expired. Provide for an annual inspection of the FAS by a state certified company. Provide a current fire alarm annual inspection report for review by the inspecting fire code official. The most current annual fire alarm inspection report shall be kept in the Fire Marshal’s Binder. The fire alarm panel shall also have an annual blue inspection tag that is current placed on the panel. All code violations have been corrected
12960 | The audibility test shows to have been done on 3/15/19. Provide test documentation for the noted audibility test date.Must have one of two things to be acceptable and the Documentation should contain Company’s ACR#, Tester’s FAL#, and date. A) Must show each audibility device’s ambient decibel level and the decibel level when the device is active. The difference in DB level must fall within NFPA 72’s acceptable range for the device to pass the test. OR B) A document from their company on company’s letter head that has the following information – 1) Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all audibility devices passed the audibility test as required by NFPA 72. All code violations have been corrected
12961 | The invoice shows an egress light test performed around 10/15/20. Provide the test documentation for a current emergency egress light annual test.An approved licensed master electrician or licensed electrical service company shall test all emergency lighting systems annually. The battery units, whether of the acid or alkali type, shall be tested continuously for a minimum of 90 minutes.Failed devices shall be corrected prior to the re-inspection.Provide dated documentation stating the master electrician and/or company's certification number, and that all devices passed the 90-minute test. All code violations have been corrected
12962 | Provide for annual fire extinguisher inspection. All extinguishers should have a current annual inspection tag. All code violations have been corrected
12963 | Provide documentation for the last sensitivity test. Consult with your fire alarm system inspection company to determine the type of system. If the system is an addressable / Intelligent system - provide the digital diagnostic reading showing the detectors status. If the system is conventional - test each device with synthetic smoke and provide documentation. The documentation is required to show: 1)Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all smoke detector devices passed the sensitivity test as required by NFPA 72. All code violations have been corrected
12964 | NoData
12965 | NoData
12966 | NoData
12967 | NoData
12968 | NoData
12969 | NoData
12970 | NoData
12971 | NoData
12972 | NoData
12973 | NoData
12974 | NoData
12975 | NoData
12976 | NoData
12977 | NoData
12978 | NoData
12979 | NoData
12980 | Provide a 5 lb. (2A:10B/C ) fire extinguisher mounted in the kitchen area. Mount the fire extinguisher in a conspicuous location per the mounting instructions noted in the Life Safety Bureau code. Keep the receipt handy to provide the date of purchase. The extinguisher will need to be inspected annually, and the initial purchase date will be needed. All code violations were corrected. All code violations were corrected
12981 | Make all code violation corrections and contact the inspecting code official when completed for reinspection. All code violations were corrected. All code violations were corrected
12982 | Provide a 5 lb. (2A:10B/C ) fire extinguisher mounted in the kitchen area. Mount the fire extinguisher in a conspicuous location per the mounting instructions noted in the Life Safety Bureau code. Keep the receipt handy to provide the date of purchase. The extinguisher will need to be inspected annually, and the initial purchase date will be needed. All code violations were corrected. All code violations were corrected
12983 | Provide a 5 lb. (2A:10B/C ) fire extinguisher mounted in the kitchen area. Mount the fire extinguisher in a conspicuous location per the mounting instructions noted in the Life Safety Bureau code. Keep the receipt handy to provide the date of purchase. The extinguisher will need to be inspected annually, and the initial purchase date will be needed. All code violations were corrected. All code violations were corrected
12984 | Provide a 5 lb. (2A:10B/C ) fire extinguisher mounted in the kitchen area. Mount the fire extinguisher in a conspicuous location per the mounting instructions noted in the Life Safety Bureau code. Keep the receipt handy to provide the date of purchase. The extinguisher will need to be inspected annually, and the initial purchase date will be needed. All code violations were corrected. All code violations were corrected
12985 | Provide a 5 lb. (2A:10B/C ) fire extinguisher mounted in the kitchen area. Mount the fire extinguisher in a conspicuous location per the mounting instructions noted in the Life Safety Bureau code. Keep the receipt handy to provide the date of purchase. The extinguisher will need to be inspected annually, and the initial purchase date will be needed. All code violations were corrected. All code violations were corrected
12986 | A gas leak test is required by the state for foster homes. This is an annual test that must be performed by a licensed plumber. Provide documentation on their company letter head stating that the gas leak test was performed and passed. The letterhead report should be dated and contain the plumbers name and licensing number. All code violations were corrected. All code violations were corrected
12987 | Correct all violations within 60 calendar days.
12988 | Have egress lighting tested and provide documentation of all corrected deficiencies.1/8/2021 - OK
12989 | Some classrooms do not have evacuation maps.Ensure that maps are placed near exits in all rooms.
12990 | Ensure that at least 50% of fire drills are obstructed.
12991 | Conduct and log monthly fire drills and provide log for inspector to review.
12992 | NoData
12993 | Compliance: 30 calendar days.
12994 | NoData
12995 | Lower wooden pallet stacks to a max of 6 ft.Compliance: 30 calendar days.
12996 | All extension cords shall be unplugged at the end of the work day to prevent electrical hazard.
12997 | Yellow tag on fire panel needs to be addressed.Compliance: 30 calendar days.
12998 | Provide a laminated card with the door code inside 911 box to gain access at front entry of facility.Compliance: 30 calendar days.
12999 | Key box permit shall be obtained from permitting office and posted along with all other permits.Compliance: 30 calendar days.
13000 | NoData
13001 | NoData
13002 | NoData
13003 | NoData
13004 | COMPLIANCE DATE: 15 CALENDAR DAYS
13005 | K1 fire prevention permit is expired at this time.
13006 | Please renew your expired Key box (k1) permit that expired on 3/13/21
13007 | Please renew your expired Access Gate (a4) permitthat expired on 03/13/21.
13008 | Have the annual inspection/service performed on all extinguishers, ensuring that new tags are placed. This is to include: (2) regular extinguishers: kitchen and bar and (1) K-type extinguisher: in kitchen
13009 | NoData
13010 | NoData
13011 | Have the 6 mo. inspection/service performed on the kitchen hood ANSUL system, ensuring that new tags are placed at the pull station. (Last inspection tag noted as 2/2020)
13012 | NoData
13013 | NoData
13014 | NoData
13015 | No violations found.
13016 | Sprinkler System repaired on Building #5.
13017 | Please have fire extinguishers serviced with current annual inspection tag.
13018 | Please have fire alarm system yellow tag addressed, with additional phone line.
13019 | Please trim the tree limbs over the entrance access gate. 13"6" clearance is required for HFD apparatus.
13020 | Please trim the tree limbs over the entrance access gate. 13'6" clearance is required for HFD apparatus.
13021 | %Please repair access gates. Both gates are required to open simultaneously when the 911 box is activated.
13022 | Please provide a KNOX box at the main entrance to the leasing office. Provide key/keys for immediate access for emergency's. (When ordering a KNOX box make sure that the box is keyed for HOUSTON)
13023 | Please provide a key FOB for the 911 box on the left side of building pedestrian gate. For building access.
13024 | NoData
13025 | NoData
13026 | Please have fire extinguishers inspected annually.
13027 | Remove extension cord used as permanent wiring.
13028 | Have all portable fire extinguishers inspected.11/2020 - OK
13029 | Add two fire extinguishers to gym.
13030 | Have audibility test performed and provide documentation that any deficiencies were corrected.1/16/2021 - OK
13031 | Remove all combustible items stored in electrical or mechanical rooms.
13032 | Provide documentation of required annual fire extinguisher and fire safety training.
13033 | Replace missing outlet cover in break room/cafeteria.
13034 | Provide emergency operations plan for inspector to review.
13035 | NoData
13036 | Most violations listed herein were also documented on the inspection report dated 9/17/2019. Correct all violations within 30 calendar days.
13037 | At least 50% of fire drills must be obstructed and make use of secondary exits.
13038 | Fire drills must be conducted and logged monthly.
13039 | Provide certificate of flame resistance for curtains in gym. Certificate of flame resistance must come from an accredited testing laboratory.Remove curtains immediately if a certificate of flame resistance is not available.
13040 | Have detector sensitivity test conducted and provide documentation that any deficiencies were corrected.
13041 | Have 90 minute egress test conducted and provide documentation that deficiencies were corrected.Repair or replace non-working exit signs.
13042 | Remove keyed deadbolts from gates in perimeter fence and replace with panic hardware (crash bars).If locks cannot be removed and replaced by the compliance date listed on Page 1 of this report, submit a plan of action with timeline for correction to inspector for approval.
13043 | Please provide City of Houston Fire Marshal's Office the Owners Statement of Compliance. (document will be provided to you to sign)
13044 | Note: Required permits shall be obtained. 1. The Houston Fire Department Permit Office is located at 1002 Washington Ave. Houston Texas and may be contacted at 832-394-9083. 2. Contact the Permit Office for any question regarding permits. 3. Required permits shall be renewed annually. Please provide a new K1, key box permit. Permit was canceled 11/14/2016 by Vicky Morris at the permit office because of new ownership at the property. This is a required permit.
13045 | NoData
13046 | Please provide and secure all air conditioning disconnect covers.
13047 | Please have the fire hydrants located inside the complex flow tested. All testing shall be performed by a licensed sprinkler company. Provide documentation on all maintenance/service repairs.
13048 | Please repair the micro switch or toggle switch in the "9-1-1" box located at the main entrance to the property. Be advised when fire department access gates are inoperable, gates shall remain open for "9-1-1 emergencies until it can be repaired.
13049 | Please mark the unit numbers on exterior of all electric disconnects servicing the apartments.
13050 | #NAME?
13051 | NoData
13052 | HIGH-PILED COMBUSTIBLE STORAGE.Storage of combustible materials in closely packed piles or combustible materials on pallets, in racks or on shelves where the top of storage is greater than 12 feet (3658 mm) in height. When required by the fire code official, high-piled combustible storage also includes certainhigh-hazard commodities, such as rubber tires,Group A plastics, flammable liquids, idle palletsand similar commodities, where the top of storage is greater than 6 feet (1829 mm) in height. NFPA 13: 12.12.1.1 - WOOD PALLETS SHALL BE PERMITTED TO BE STORED IN THE FOLLOWING ARRANGEMENTS:(1) Stored outside.(2) Stored in a detached structure.(3) Stored indoors where arranged in accordance with 12.12.1.2. NFPA 13: 12.12.1.2 – WOOD PALLETS, WHERE STORED INDOORS, SHALL MEET THE FOLLOWING:(1) pallets shall be stored no higher than 6 feet.(2) each pallet pile of no more than 4 stacks shall be separated from other pallet piles by at least 8 feet of clear space or 25 feet of commodity.You are not approved for high-piled storage and previously signed a owner's statement of intended use, which stated that you would not be a high-piled storage facility. Lower all commodities to below 12 feet and lower all high hazard commodities to below 6 feet.IMMEDIATE COMPLIANCE IS REQUIRED.
13053 | For informational purposes.
13054 | For informational purposes.
13055 | The owner/occupant shall be heldresponsible for the correction and abatement of all violations listed in thisnotice of violations report. COMPLIANCE:WITHIN 30 CALENDAR DAYS
13056 | The 911 key box, or Knox Box 3200 series hinged lid, shall be of an approved type listed in accordance with UL 1037 and shall contain keys for immediate access for lifesaving or firefighting purposes.(SEE ATTACHED LSB STANDARD 05 FOR MORE INFORMATION.)
13057 | You must provide a 911 key box with a key for the fire department to gain emergency access to the facility according to LSB Standard 05.COMMPLIANCE: WITHIN 30 CALENDAR DAYS.
13058 | The 911 key box, or Knox Box 3200 series hinged lid, shall be of anapproved type listed in accordance with UL 1037 and shall contain keys forimmediate access for lifesaving or firefighting purposes.(SEE ATTACHED LSB STANDARD 05 FOR MORE INFORMATION.)
13059 | The new 911 key box shall be attached according to the requirements described in LSB 5.3.3 above.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
13060 | Mark your building(s) with the address as stated above.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
13061 | The "FDC" sign shall be labeled with reflective white letters no less than 2 inches in height and follow the above code.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
13062 | A working space (cleared of all combustible material) of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
13063 | NoData
13064 | NoData
13065 | Renew the expired assembly permit.
13066 | NoData
13067 | NoData
13068 | have a licensed fire protection company repair the yellow tagged sprinkler system and perform a 5 year FDC test.
13069 | Have a licensed fire protection company correct the red tagged vent hood suppression system. Have the vent hoods professionally cleaned tagged.
13070 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a gas test permit.
13071 | Discontinue the use of the extension cord running through the ceiling.
13072 | Provide filler plates for the openings in the breaker panels. Provide a cover for the exposed wiring in the breaker panel room.
13073 | Repair the unmounted exit sign located in the rear of the business.
13074 | A permit is required for CO2 cryogenic liquids in excess of 60 gallons. If the cryogenic tank is greater than 60 gallons obtain a permit. Permits can be obtained at 1002 Washington Ave. Houston TX.
13075 | Post an occupant load sign near the main entrance to the business.
13076 | Ensure all fire extinguishers have a current service tag from a licensed fire protection company. Fire extinguishers are required to be serviced annually.
13077 | Ensure the fire extinguishers are properly hung using a wall mount, and are mounted with the bottom being a minimum of 4 inches off the floor, and the top being at a max height of 5 feet off the floor.
13078 | Discontinue all open burning.
13079 | Label the door to the closet where he breaker boxes are located."Electrical Room"
13080 | Replace the missing fire extinguisher in the office and provide one extinguisher in the second floor break room. Both extinguishers should have a minimum rating of 2:A 10:BC.
13081 | NoData
13082 | NoData
13083 | Claudia Guzman 7139213560
13084 | FYI: Last gas test performed on 1/28/2021. Good until 1/28/2025.
13085 | Need sight map posted near office.
13086 | Post main address near office.
13087 | NoData
13088 | NoData
13089 | Please Renew your expired Public Assembly Permit within 10 Business days
13090 | Please Renew your Expired Public Assembly Permit within 10 Business days
13091 | All fire extinguishers must be serviced and have a current service tag placed on them.
13092 | The fire alarm panel must have an annual inspection performed on it.
13093 | An emergency lighting test must be performed on the fire alarm system.
13094 | NO VIOLATIONS FOUND AT THIS TIME.
13095 | NoData
13096 | NoData
13097 | NoData
13098 | NoData
13099 | NoData
13100 | P2 assembly expired
13101 | NoData
13102 | NoData
13103 | night crew unable to preform an inspection without the building being occupied "to get a view of the operation when it's open" ??? CofO is posted, proj# 95109039, reciept for assembly perimt is posted, exits clear and open.
13104 | NoData
13105 | NoData
13106 | Ensure that all light switches and electrical outlets have the appropriate cover plates in place. Specifically noted as missing were outlet covers in the back room.
13107 | The fire alarm was yellow tagged for deficiencies on the annual inspection performed on 9/1/2020 for:1) Replace smoke taken down 2) Add smoke to room not coveredThe work appears to have been completed but the required correction tag corresponding to the date on the yellow tag was not placed. Have Omni Fire verify repairs are complete and place the appropriate correction tag-OR- have the necessary repairs completed and tagged if not complete.
13108 | As required by the state for all daycare occupancies:Have the bi-annual (2 yr) gas test performed by a certified plumber ensuring that the appropriate permit is obtained-OR-Provide proof of a completed test and permit within the last 2 years. (The last gas test found on record was 4/3/2018)
13109 | Ensure that ALL exit signs, including their integrated emergency lights, illuminate when the test button is pressed to simulate a loss of power. They are required to remain illuminated for 90 min. on battery back up in instances of power outage. (specifically noted was the exit sign in the school aged room)
13110 | SERVICE AND TAG ALL FIRE EXTINGUISHERS
13111 | BUSINESS IS TO FILL VOIDS WITH SPACERS IN ELECTRICAL BOX
13112 | THE FIRE ALARM SYSTEM MUST BE SERVICE IMMEDIATELY
13113 | NoData
13114 | BUSINESS MUST MOUNT UP PORTABLE CLASS K EXTINGUISHER
13115 | BUSINESS IS DISCONTINUE THE USE OF ALL EXTENSION CORDS FOR LIGHTING
13116 | BUSINESS ANSUL SYSTEM NEEDS TO BE SERVICE
13117 | MOUNT FIRE EXTINGUISHERS WHERE MARKING ARE LOCATED
13118 | BUSINESS IS TO HAVE ALL PORTABLE FIRE EXTINGUISHERS INSPECTED
13119 | NoData
13120 | SIGNS ARE REQUIRED ON SPRINKLER ROOM AND FIRE ALARM ROOM DOORS
13121 | REPAIR EMERGENCY ILLUMINATION LIGHTS NEAR ICE MACHINE AREA
13122 | NoData
13123 | BUSINESS IS TO OBTAIN CERTIFICATE OF OCCUPANCY IMMEDIATELY
13124 | NoData
13125 | NoData
13126 | BUSINESS IS TO DISCONTINUE USING ALL CANDLES UNTIL CANDLE PERMIT IS OBTAINED
13127 | BUSINESS IS TO POST ALL PERMITS
13128 | BUSINESS IS TO MAINTAIN RECORDS OF INSPECTIONS, TEST AND SERVICES
13129 | SPRINKLER SYSTEM MUST BE SERVICED AND TESTED IMMEDIATELY
13130 | CLEAR ALL BOXES FROM AROUND ELECTRICAL PANEL
13131 | CLEAR ALL DEBRIS IN ICE MACHINE AREA
13132 | NoData
13133 | NoData
13134 | NoData
13135 | NoData
13136 | NoData
13137 | NoData
13138 | NoData
13139 | NoData
13140 | NoData
13141 | ALL FIRE EXTINGUISHERS SHALL BE MOUNTED
13142 | NEED TO TEST THE FIRE ALARM (ANNUAL)
13143 | NEED TO REPLACE CAP ON THE FDC
13144 | NEED TO ADD AN ELEVATOR SIGN ON 2ND FLOOR
13145 | Correct all violations within 60 calendar days.
13146 | NoData
13147 | Provide documentation of required fire safety training.
13148 | Update EOP for 20-21 school year.
13149 | Provide fire drill log for inspector to review.
13150 | Have 90 minute egress test performed and provide documentation that any deficiencies were corrected.Deficiencies corrected 3/18/2021 - OK
13151 | NoData
13152 | NoData
13153 | NoData
13154 | night crew unable to preform an inspection without the building being occupied "to get a view of the operation when it's open" ??? CofO is posted, proj# 95109039, reciept for assembly perimt is posted, exits clear and open.
13155 | NoData
13156 | expired last annual 11/2018
13157 | NoData
13158 | NoData
13159 | NoData
13160 | NoData
13161 | NoData
13162 | NoData
13163 | NoData
13164 | For the expired Hot Works permit in the amount of $266.80
13165 | ALL FIRE EXTINGUISHERS SHALL BE SERVICED AND TESTED BY A QUALIFIED FIRE PROTECTION COMPANY ANNUAL. EXTINGUISHER SHALL HAVE A ANNUAL INSPECTION TAG ATTACHED.
13166 | MOUNT THE FIRE EXTINGUISHER FOLLOWING THE ABOVE CODE. FIRE EXTINGUISHERS ARE REQUIRED TO BE MOUNTED IN AN AREA WHERE IT IS READILY VISIBLE, EASILY ACCESSIBLE, NEAR A COMMON PATH OF TRAVEL, AND NOT SUBJECT TO DAMAGE
13167 | A 2A 10B:C RATED EXTINGUISHER NEEDS TO BE MOUNTED IN BUSINESS.
13168 | COMPLY WITH ABOVE CODE.
13169 | COMPLY WITH ABOVE CODE.
13170 | NoData
13171 | NoData
13172 | NoData
13173 | NoData
13174 | NoData
13175 | NoData
13176 | NO VIOLATIONS FOUND AT THIS TIME.
13177 | NoData
13178 | 109.2 Owner/occupant responsibility. Correction and abatement of violations of this code shall be the responsibility of the owner. If an occupant creates, or allows to be created, hazardous conditions in violation of this code, the occupant shall be held responsible for the abatement of such hazardous conditions.
13179 | 3201.3 Construction documents. At the time of building permit application for new structures designed to accommodate high-piled storage or for requesting a change of occupancy/use, and at the time of application for a storage permit, plans and specifications shall be submitted for review and approval. In addition to the information required by the International Building Code, the storage permit submittal shall include the information specified in this section. Following approval of the plans, a copy of the approved plans shall be maintained on the premises in an approved location. The plans shall include the following: 1. Floor plan of the building showing locations and dimensions of high-piled storage areas. 2. Usable storage height for each storage area. 3. Number of tiers within each rack, if applicable. 4. Commodity clearance between top of storage and the sprinkler deflector for each storage arrangement. 5. Aisle dimensions between each storage array. 6. Maximum pile volume for each storage array. 7. Location and classification of commodities in accordance with Section 3203. 8. Location of commodities which are banded or encapsulated. 9. Location of required fire department access doors. 10. Type of fire suppression and fire detection systems. 11. Location of valves controlling the water supply of ceiling and in-rack sprinklers. 12. Type, location and specifications of smoke removal and curtain board systems. 13. Dimension and location of transverse and longitudinal flue spaces. 14. Additional information regarding required design features, commodities, storage arrangement and fire protection features within the high-piled storage area shall be provided at the time of permit, when required by the fire code official.Compliance: 30 calendar days.
13180 | 901.6 Inspection, testing and maintenance. Fire detection, alarm, and extinguishing systems, mechanical smoke exhaust systems, and smoke and heat vents shall be maintained in an operative condition at all times, and shall be replaced or repaired where defective. Nonrequired fire protection systems and equipment shall be inspected, tested and maintained or removed.Compliance: 30 calendar days.
13181 | 901.6 Inspection, testing and maintenance. Fire detection, alarm, and extinguishing systems, mechanical smoke exhaust systems, and smoke and heat vents shall be maintained in an operative condition at all times, and shall be replaced or repaired where defective. Nonrequired fire protection systems and equipment shall be inspected, tested and maintained or removed.Compliance: 30 calendar days.
13182 | 901.6 Inspection, testing and maintenance. Fire detection, alarm, and extinguishing systems, mechanical smoke exhaust systems, and smoke and heat vents shall be maintained in an operative condition at all times, and shall be replaced or repaired where defective. Nonrequired fire protection systems and equipment shall be inspected, tested and maintained or removed. Compliance: 30 calender days.
13183 | NoData
13184 | NoData
13185 | NoData
13186 | Add KNOX BOX key box at rear walk way leading to Sprinkler Riser Room. 2 knox boxes are required, one on each side. for building 11220
13187 | Fire Prevention (A4) access gate permit is required.
13188 | NoData
13189 | The occupant (YMCA Children's Academy) representative Mrs. Garcia stated that the daycare is only occupying the first floor of suite 102 at this time. No violations found at this time in suite 102.
13190 | NoData
13191 | NoData
13192 | NoData
13193 | NoData
13194 | replace missing spacer on circuit breaker 49, and building 5. Check out Circuit breaker.
13195 | service out of date fire extinguisher
13196 | January 1, 2017 as battery operated single station alarm is replaced, that smoke alarm shall be replaced with tamper-resistant battery-operated single station smoke alarm.
13197 | Required every 5 years and must be completed with an approved permit from theBuilding Department.
13198 | renew K1 and H3 permit.Replace missing 911 falcon lock on main gate.
13199 | Pedro Rodriguez 713 923 1900
13200 | renew H3 permit
13201 | NoData
13202 | CERTIFICATE OF OCCUPANCY CORE ONLYACTIVE FIRE PERMITSFIRE DEPOSITORY KEY LETTERFIRE MARSHAL TRAINNING AND EVACUATION LETTERFIRE ALARM PERMITSPRINKLER PERCENTAGE LETTER AND FORMFire Drills-Every 6 months, LSB# 8.4.1Fire Wardens, LSB# 7.4.3.2FIRE PROTECTION SYSTEMElectronic Locks- Semi Annual, LSB# 2.4.1.1Fire Alarm System Test- Annual, LSB# 2.4.1.1Emergency radio coverage Annual, HFC 510.6.1Sprinkler System- Annual, LSB# 2.5.1.2Dry pipe partial Annual, LSB# 2.5.2.3Fire Extinguishers- Annual, LSB# 2.8.2Fire Hoses- Annual, LSB# 2.6.1Fire Pumps Flow Test- Annual, LSB# 2.5.5.3Emergency Power &amp; Lighting- Annual, LSB# 2.4.2.1Generator Test – Annual, LSB# 2.4.3.2Automatic Transfer Switch Test Annual, LSB# 2.4.3.3Fire Alarm Audibility Test- 3 Year, LSB# 2.4.1.3Dry Pipe Full Trip Test-3 Year, LSB# 2.5.2.3Fire Hose Pressure Test- 3 year, LSB# 2.6.2Fire Dampers-4 Year Test, LSB# 2.7.3Fire Alarm Sensitivity- 2 YearFDC Test - 5 Year, LSB# 2.5.4PRV / PRD Test- 5 Year, LSB# 2.5.3.6Stair pressurization Test- 5 Year, LSB# 2.4.4Standpipe System- 5 Year, LSB# 2.5.3Water Supply Tank Inspection- 5 Year, LSB# 2.5.6.2Kitchen Hood System Semi-Annual, LSB# 2.9.1Clean Agent System Semi-Annual, LSB# 2.9.6.3Boiler Permit-, LSB# 2 .2Elevator- Annual, LSB# 2.3Gas Test- 5 Years- LSB# 2.1.1Compliance in 60 days.
13203 | Occupancy approval sticker is missing from electronic locked door. Have lock approved by the building department occupancy team and sticker placed in door frame.
13204 | STANDPIPE SYSTEMS SHALL BE TESTED ANNUALLY BY A LICENSED COMPANY AND AN ACCEPTABLE TAGE SHALL BE AFFIXED TO ENSURE SYSTEM IS MAINTAINED IN OPERATIVE CONDITION. (YELLOW TAG IMPAIRMENT) COMPLIANCE: 7 DAYS.
13205 | THE HIGH-PILED STORAGE PROCESS IS INCOMPLETED FOR THE FINAL ONSITE. PLEASE HAVE YOUR FIRE PROTECTION ENGINEER TO CALL 832-394-9350 FOR THE FINAL ONSITE OR YOU WILL HAVE TO LOWER THE COMMIDITIES ON THE RACK TO UNDER 12 FEET.COMPLIANCE: 1 DAY
13206 | Still not in compliance
13207 | This facility was never approved for high-piled storage. Plans were never submitted to the building department or the fire marshal’s office for approval of rack storage of high-piled operation.Submit plans to the building department and the hazmat/high-piled storage team for review and approval for high-piled combustible storage. Acquiring the expertise of a certified fire protection engineer for this process is highly advisable. SEE ATTACHED COPY OF HIGH-PILED STORAGE PLAN SUBMITTAL GUIDELINE. COMPLIANCE: WITHIN 60 CALENDAR DAYS.IF YOU CHOOSE TO NOT BECOME APPROVED, LOWER ALL COMMODITIES TO A MAXIMUM OF 12 FEET (HIGH-HAZARD COMMODITIES TO 6 FEET) AND MAINTAIN COMMODITIES AT THIS HEIGHT. (WITH AN APPROVED SPRINKLER SYSTEM YOU ARE ALLOWED 2,500 SQ FT OF HIGH PILED COMBUSTIBLE STORAGE.) AN OWNER’S STATEMENT MUST BE SIGNED WITHIN 30 CALENDAR DAYS.
13208 | The owner / occupant shall be held responsible for the correction and abatement of all violations listed in this notice of violations report. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
13209 | This facility was never approved for high-piled storage. Plans were never submitted to the building department or the fire marshal’s office for approval of rack storage of high-piled operation.Submit plans to the building department and the hazmat/high-piled storage team for review and approval for high-piled combustible storage. Acquiring the expertise of a certified fire protection engineer for this process is highly advisable. SEE ATTACHED COPY OF HIGH-PILED STORAGE PLAN SUBMITTAL GUIDELINE. COMPLIANCE: WITHIN 60 CALENDAR DAYS.IF YOU CHOOSE TO NOT BECOME APPROVED, LOWER ALL COMMODITIES TO A MAXIMUM OF 12 FEET (HIGH-HAZARD COMMODITIES TO 6 FEET) AND MAINTAIN COMMODITIES AT THIS HEIGHT. (WITH AN APPROVED SPRINKLER SYSTEM YOU ARE ALLOWED 2,500 SQ FT OF HIGH PILED COMBUSTIBLE STORAGE.) AN OWNER’S STATEMENT MUST BE SIGNED WITHIN 30 CALENDAR DAYS.
13210 | Upon approval, a copy of the approved plans must be kept on the premises and available by request to the fire code official.
13211 | All access and exit doors shall be keyed alike.Ensure all firefighter access doors have approved hardware that is readily operable from the egress side. (panic hardware or lever action which open with one movement and require no special tools or knowledge) COMPLIANCE: WITHIN 30 CALENDAR DAYS.
13212 | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. COMPLIANCE: WITHIN 30 CALENDAR DAYS.
13213 | This facility was never approved for high-piled storage. Plans were never submitted to the building department or the fire marshal’s office for approval of rack storage of high-piled operation.Submit plans to the building department and the hazmat/high-piled storage team for review and approval for high-piled combustible storage. Acquiring the expertise of a certified fire protection engineer for this process is highly advisable. SEE ATTACHED COPY OF HIGH-PILED STORAGE PLAN SUBMITTAL GUIDELINE. COMPLIANCE: WITHIN 60 CALENDAR DAYS.IF YOU CHOOSE TO NOT BECOME APPROVED, LOWER ALL COMMODITIES TO A MAXIMUM OF 12 FEET (HIGH-HAZARD COMMODITIES TO 6 FEET) AND MAINTAIN COMMODITIES AT THIS HEIGHT. (WITH AN APPROVED SPRINKLER SYSTEM YOU ARE ALLOWED 2,500 SQ FT OF HIGH PILED COMBUSTIBLE STORAGE.) AN OWNER’S STATEMENT MUST BE SIGNED WITHIN 30 CALENDAR DAYS.
13214 | All emergency lights shall be repaired and tested to ensure proper operation in case of emergency. A written record of inspections shall be maintained.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
13215 | All access and exit doors shall be keyed alike.Ensure all firefighter access doors have approved hardware that is readily operable from the egress side. (panic hardware or lever action which open with one movement and require no special tools or knowledge) COMPLIANCE: WITHIN 30 CALENDAR DAYS.
13216 | This facility was never approved for high-piled storage. Plans were never submitted to the building department or the fire marshal’s office for approval of rack storage of high-piled operation.Submit plans to the building department and the hazmat/high-piled storage team for review and approval for high-piled combustible storage. Acquiring the expertise of a certified fire protection engineer for this process is highly advisable. SEE ATTACHED COPY OF HIGH-PILED STORAGE PLAN SUBMITTAL GUIDELINE. COMPLIANCE: WITHIN 60 CALENDAR DAYS.IF YOU CHOOSE TO NOT BECOME APPROVED, LOWER ALL COMMODITIES TO A MAXIMUM OF 12 FEET (HIGH-HAZARD COMMODITIES TO 6 FEET) AND MAINTAIN COMMODITIES AT THIS HEIGHT. (WITH AN APPROVED SPRINKLER SYSTEM YOU ARE ALLOWED 2,500 SQ FT OF HIGH PILED COMBUSTIBLE STORAGE.) AN OWNER’S STATEMENT MUST BE SIGNED WITHIN 30 CALENDAR DAYS.
13217 | Have a fire protection engineer evaluate all areas of the facility including all storage, usage, processes and drawings to assure compliance with all applicable codes. A copy of the stamped fire protection engineers report shall be submitted for review to the code official. COMPLIANCE: WITHIN 30 CALENDAR DAYS. (MORE TIME MAY BE GRANTED UPON WRITTEN REQUEST FROM THE FIRE ENGINEER ONLY.)
13218 | All access and exit doors shall be keyed alike.Ensure all firefighter access doors have approved hardware that is readily operable from the egress side. (panic hardware or lever action which open with one movement and require no special tools or knowledge) COMPLIANCE: WITHIN 30 CALENDAR DAYS.
13219 | All access and exit doors shall be keyed alike.Ensure all firefighter access doors have approved hardware that is readily operable from the egress side. (panic hardware or lever action which open with one movement and require no special tools or knowledge) COMPLIANCE: WITHIN 30 CALENDAR DAYS.
13220 | NoData
13221 | L1 (PROPANE PERMIT) EXPIRED ON 3-15-21. RENEW ONLINE OR IN PERSON AT HOUSTON PERMITTING CENTER.
13222 | NoData
13223 | NoData
13224 | NoData
13225 | Repair all the exits doors located in the rear of the business to ensure they open accordingly.
13226 | Ensure storage is maintained below 12 feet in height.
13227 | Provide LPG powered fork lifts with fire extinguishers with a minimum rating of 10BC.
13228 | Remove obstructions in front of exits.
13229 | Have a licensed fire protection company perform an annual inspection on the fire sprinkler system and correct any deficiencies.
13230 | Have a licensed fire protection company perform a 5 year FDC test and correct any deficiencies.
13231 | Fill out and return HMIS forms.
13232 | Provide an updated padlock key for the access gate.
13233 | Ensure MSDS are readily available upon request.
13234 | Have all Fire Doors inspected to NFPA 80 standard by a certified company. An approved service company shall perform any required repairs of fire doors or assemblies.
13235 | NoData
13236 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
13237 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
13238 | Correct Red Tags on Standpipe Hose
13239 | Provide documentation/report for pressure testing standpipe hose.
13240 | Provide documentation/report for Natural Gas Leak Test.
13241 | NoData
13242 | CURRENT INFORMATION -FPS FIRE ALARM SYSTEM ANNUAL INSPECTION DATE: 1/5/2019 ACCEPTABLE BLUE TAG SPRINKLER SYSTEM INSPECTION DATE: 5/16/2019 ACCEPTABLE BLUE TAG ANNUAL FIRE EXTINGUISHER INSPECTION DATE:7/2019
13243 | PROVIDE SIGNAGE "FIRE ALARM PANEL" ON/BY DOORS WHERE THE FIRE ALARM SYSTEM PANEL IS LOCATED. PROVIDE SIGNAGE FOR BOTH DOORS 204 ELECTRICAL AND 201 ELECTRICAL/IT
13244 | CORRECT 1/30/2019 YELLOW TAG (JOHNSON CONTROLS) ON FIRE PUMP ____________________________________________________ CORRECT TROUBLE ALERT ON FIRE ALARM PANEL
13245 | STANDPIPE HOSE SHALL BE INSPECTED AND SERVICE TAGGED ANNUALLY BY A LICENSED SERVICE COMPANY. PROVIDE ANNUAL INSPECTION AND SERVICE TAG OF STANDPIPE HOSES IN GARAGE
13246 | PROVIDE OCCUPANT LOAD FOR CAFETERIA
13247 | AN APPROVED LICENSED MASTER ELECTRICIAN OR LICENSED ELECTRICAL SERVICE COMPANY SHALL TEST ALL EMERGENCY LIGHTING SYSTEMS ANNUALLY. LAST TEST DATE: UNKNOWN PROVIDE WRITTEN DOCUMENTATION/REPORT OF TESTING RESULTS AND MAINTAIN ON FILE FOR FIRE CODE OFFICIAL. ANY FAILURES OF THE EMERGENCY LIGHTING SYSTEM SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
13248 | NoData
13249 | NEED SERVICE 4-8-20 LAST DATE
13250 | NEED SERVICE 8-19 LAST DATE
13251 | EXIT gate's micro switch does not open the gate as required.
13252 | Fail safe lock and manual gate lock keys are not in the 911 lock box.
13253 | HFD Hydrant Signs missing on Entrance and Exit Gate
13254 | Complete a natural gas testObtain a permit for a natural gas test from the Houston Permitting Center.
13255 | Fire Extinguishers are out of date.
13256 | NoData
13257 | Fire Alarm is Red Tagged ImpairedFire Sprinkler System is out of service.Maintain Self Fire-watch until systems are back in regular service.
13258 | Please renew the following permits that expired on 03/04/2021.Key Box (k1), Access gates (a4), & Assembly (p2) permits. If you need an invoice or the amount owed, please contact the HPC office at 832-394-8811 (dial 0) and someone will assist you.
13259 | P2 permit is expired. Expired on 1/09/2021. Amount owed 266.80 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
13260 | Please renew the K1, key box permit. Expired 3/16/2021.
13261 | NoData
13262 | NoData
13263 | NoData
13264 | NoData
13265 | NoData
13266 | NoData
13267 | NoData
13268 | NoData
13269 | NoData
13270 | NoData
13271 | Please contact the permit office to get your K1, key box and A4, access gate permits current.A4. access gate expired 2/21/2018.K1, key box permit expired 4/11/2018.
13272 | Please have a gas test done by a licensed Plumber if previous test was done before 05/01/16.
13273 | Please update/renew your Access Gate permit with HPC office located at 1002 Washington Ave. 832-394-8811 (dial 0) at the start of message.
13274 | Please update/renew your key box permit with HPC office located at 1002 Washington Ave. 832-394-8811 (dial 0) at the start of message.
13275 | Address must be legible.
13276 | Place sign indicating location of electrical room.
13277 | NoData
13278 | NoData
13279 | provide and install letters on oily stored metal can with the following words oily rags
13280 | remove all l.p ,gas bottles use for cooking outside
13281 | provide and install an extra 20abc fire extinguisher in the front part of garage
13282 | apply for a cutting and welding permit at 1002 Washington fire permit section and post at front office.
13283 | provide and install safety check values behind cutting and welding torch or in front of the regulators to prevent flames going back and causing a possible explosion at cutting and welding rig
13284 | apply for a permit if storing more than 25 gallons on waste oil inside shop or more than 55 gallons out side of shop Plus remove all plastic gas containers for storing gasoline to the outside of the bldg. and provide and install a metal approve container for storing only (5) gallons inside or (10) gallons outside of the garage.
13285 | NoData
13286 | NoData
13287 | NoData
13288 | NoData
13289 | NoData
13290 | Have a licensed fire protection company inspect and tag the fire extinguishers.
13291 | The fire extinguishers are required to be mounted.
13292 | Remove obstructions in the hallway that leads to the rear exit.
13293 | Have a licensed fire protection company inspect and tag the vent hood suppression system and correct any deficiencies.
13294 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a gas test permit.
13295 | Renew the expired assembly permit.
13296 | Post the occupant load near the main entrance of the business.
13297 | Repair the inoperable emergency illumination on the exit sign located in the kitchen.
13298 | Service all exit signs to ensure they are properly illuminated under regular building service power.
13299 | Ensure all breakers inside each breaker box are accurately labeled. Properly secure with a lock and label the exterior door housing the electrical equipment with a durable weather resistant sign that reads as follows: Electrical Room
13300 | One venthood had a current service tag attached showing the hood was serviced in Feb 2021. The second venthood did not have a service tag attached. Provide documentation showing service was performed on both venthoods.
13301 | The ANSUL Wet Chemical System on the North interior wall was found to have a pull station in disrepair and a canister in need of recharge. Have the system serviced by a licensed fire protection company and ensure a current service tag is attached.
13302 | NoData
13303 | Replace the missing fire extinguisher in the kitchen and mount a fire extinguisher in the dining room. Ensure both extinguishers have a minimum rating of 2:A 10:BC and have a current service tag attached.
13304 | Service all exit signs to ensure they are 100% operational under battery back up power.
13305 | Service the egress lighting on the exterior of the building to ensure it is 100% operational.
13306 | Awaiting 3 year audibility verification from authorized vendor.Compliance within 30 days
13307 | Remove or correct the direction of the HFD signs directing approaching fire department personnel to 911 key box.Compliance within 30 days.
13308 | All open voids must be covered, no open wiring should be exposed.Compliance within 30 days.
13309 | NoData
13310 | NoData
13311 | FIRE EXTINGUISHERS REQUIRE ANNUAL INSPECTION RENEWAL.
13312 | ASSEMBLY PERMIT EXPIRED. REQUIRE RENEWAL.
13313 | NoData
13314 | P2 permit expired
13315 | Ms. Guzman given 7 days to renew P2 permit
13316 | NoData
13317 | NoData
13318 | NoData
13319 | NoData
13320 | NoData
13321 | NoData
13322 | NoData
13323 | NoData
13324 | NoData
13325 | NoData
13326 | NoData
13327 | NoData
13328 | NoData
13329 | NoData
13330 | NoData
13331 | NoData
13332 | NoData
13333 | FIRE PANEL NEED SERVICE 1-8-20 LAST DATE
13334 | NEED SERVICE 8-19 LAST DATE
13335 | NEED TO BE INSPECTED
13336 | NoData
13337 | NEED SERVICE 3-19 LAST DATE IN ALL BUILDINGS
13338 | NEED SERVICE 3-19 LAST DATE
13339 | NoData
13340 | NEED SERVICE 8-19 LAST DATE
13341 | NoData
13342 | NoData
13343 | 8-18 Last date . NEED SERVICING
13344 | NoData
13345 | Portable Fire Extinguisher(s) annual maintenance Dt: 12/20
13346 | Keep all exit door(s) and pathways clear. Please remove trash in front of exit
13347 | Sprinkler system (wet) annual expired; requires current inspection Last date: 7/24/15
13348 | 5-year hydro/flow testing needs to be performed with any deficiencies corrected and report provided to fire marshal Last date: 10/12/15
13349 | Approved multi-outlet power taps must be plugged directly into an outlet. No daisy-chaining of power taps allowed
13350 | Main exit should not have arrows, N exit needs to point only in the direction of the exit
13351 | Portable Fire Extinguisher(s) annual maintenance Dt: 10/20
13352 | 36" Working clearance must be maintained in front of transformers
13353 | NoData
13354 | Gas cylinders must be secured. Attach chain to non-movable object in order to keep cylinders upright
13355 | Extension cords not allowed as a replacement for permanent wiring. Power for computer equipment
13356 | No missing spacers allowed in electrical panels; All junction boxes, light switches and plug outlets must have cover plates installed
13357 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs
13358 | Repair ASAP.
13359 | K1 permit is expired. Expired on 1/02/2021. Amount owed 177.87 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
13360 | NoData
13361 | NoData
13362 | Install an address sign with 7707 somewhere near the front entrance.Compliance by 5-4-2021
13363 | Secure your LP-Gas bottles from one of the ways listed in the section.Compliance by 5-4-2021
13364 | Fill out and submit a hazardous materials inventory statement showing the hazards that are stored and used in your plant from the guideline that will be provided.Compliance by 5-4-2021
13365 | Repair or replace all emergency lighting not working in these areas and provide documentation that they are working at that time.Compliance by 5-4-2021
13366 | Provide a spill pallet under the 55 gallon drums storing what appears to be hazardous material waste.Compliance by 5-4-2021
13367 | Apply for a Certificate of Occupancy at 1002 Washington Ave. or find out if you would just need to complete a name change for the existing Grinding & Sizing C of O.Compliance by 5-4-2021
13368 | Apply for a welding permit from the City of Houston website under fire department then permits or go to 1002 Washington Ave.Compliance by 5-4-2021
13369 | Apply for a LP-Gas permit from the City of Houston website under fire department then permits or go to 1002 Washington Ave.Compliance by 5-4-2021
13370 | Repair or replace all exits lights not illuminated in these areas and provide documentation that they are working at this time.Compliance by 5-4-2021
13371 | Install Portable Fire Extinguisher(Maintenance Install doing Inspection). No post violation.
13372 | Need to Install a up dated Key in the 911 Box for Emergence access (Maintenance Install doing Inspection). No post violation.
13373 | Install smoke Detector(Maintenance Install doing Inspection). No post violation.
13374 | Owner's responsibility. Comply with the above fire code.
13375 | The fire alarm system has been red tagged dated 3./8/2021.The sprinkler system has also been red tagged and have no water pressure.Have the fire alarm and sprinkler systems repaired to compliant status.A continuous in house fire watch shall be implemented 24 hours 7 days a week until both systems have been repaired.Sign Fire Watch Assignment Agreement form.
13376 | Have the kitchen hood suppression system inspected/tested by a certified fire protection company and ensure new tags are placed at the ansul pull station. (Last ansul system tag was noted as 4/2020). This is required every 6 months.
13377 | Renew your P2: Public Assembly permit that expired 1/15/2021 per the instructions on the permit renewal notice.
13378 | Have the 5 yr gas test completed by a licensed plumber, ensuring that a permit is pulled through city permitting by the plumber performing the test -OR- provide documentation of a completed test within the last 5 years.
13379 | NoData
13380 | Apply for fire alarm permit.
13381 | Apply for assembly permit at 1002 Washington ave.
13382 | Please renew 911 Key Box (K1) and Access Gate permits which expired on 4/19/20.
13383 | NoData
13384 | please connect ducting to the backside of dryer that allows for proper escape of lint and hot air through dryer vent.
13385 | NoData
13386 | identify the proper unit numbers on the outside of all electrical panels.
13387 | Please provide a fully charged 2-A, 10-B:C (RED) fire extinguisher inside the laundry room.
13388 | Also install a battery operated smoke detector inside laundry room
13389 | Please have a 5 year gas test done by a licensed plumber for gas dryers located inside laundry room.
13390 | NoData
13391 | NoData
13392 | The ANSUL Wet Chemical System on the North interior wall was found to have a pull station in disrepair and a canister in need of recharge. Have the system serviced by a licensed fire protection company and ensure a current service tag is attached.
13393 | NoData
13394 | Service all exit signs to ensure they are properly illuminated under regular building service power.
13395 | Ensure all breakers inside each breaker box are accurately labeled. Properly secure with a lock and label the exterior door housing the electrical equipment with a durable weather resistant sign that reads as follows: Electrical Room
13396 | One venthood had a current service tag attached showing the hood was serviced in Feb 2021. The second venthood did not have a service tag attached. Provide documentation showing service was performed on both venthoods.
13397 | Replace the missing fire extinguisher in the kitchen and mount a fire extinguisher in the dining room. Ensure both extinguishers have a minimum rating of 2:A 10:BC and have a current service tag attached.
13398 | Service all exit signs to ensure they are 100% operational under battery back up power.
13399 | Service the egress lighting on the exterior of the building to ensure it is 100% operational.
13400 | A LICENSED FIRE ALARMSERVICE COMPANY SHALL PERFORM A TEST OF ALL THE FIRE ALARM SENSITIVITY SYSTEM ANDANNUNCIATION DEVICES(AUDIBILITY) NOT LESS THAN EVERY 3 YEARSCOMPLIANCE WITHIN 30DAYS
13401 | APPROVEDPLANS ARE TO BE KEPT ON SITE AT ALL TIMES.IF APPROVED PLANS CANNOT BE LOCATED, A REQUEST TO THE BUILDING DEPARTMENTMAY BE ABLE TO DUPLICATE THE ORIGINAL.APPROVED PLANS MUST BE SUBMITTED TO FIRE MARSHAL OR THE PROCESS FORHIGH-PILED STORAGE PLAN SUBMITTAL PROCESS SHALL BE RESTARTED.COMPLIANCE WITHIN 30 DAYS.
13402 | ENSURE THAT ALL DUMPSTERS ARE MAINTAINED 10FEET MINIMUM FROM THE BUILDING AT ALL TIMES.COMPLIANCE: WITHIN30 CALENDAR DAYS.
13403 | ALL ACCESSAND EXIT DOORS SHALL BE KEYED ALIKE. ENSURE ALL FIREFIGHTER ACCESS DOORS HAVEAPPROVED HARDWARE THAT IS READILY OPERABLE FROM THE EGRESS SIDE.COMPLIANCE WITHIN 30 DAYS
13404 | NFPA 13: 12.12.1.1 -WOOD PALLETS SHALL BE PERMITTED TO BE STORED IN THE FOLLOWING ARRANGEMENTS:(1) STORED OUTSIDE.(2) STORED IN A DETACHED STRUCTURE.(3) STORED INDOORS WHERE ARRANGED IN ACCORDANCE WITH 12.12.1.2. NFPA 13: 12.12.1.2 – WOOD PALLETS, WHERE STORED INDOORS, SHALL MEET THE FOLLOWING:(1) PALLETS SHALL BE STORED NO HIGHER THAN 6 FEET.(2) EACH PALLET PILE OF NO MORE THAN 4 STACKS SHALL BE SEPARATED FROM OTHER PALLET PILES BY AT LEAST 8 FEET OF CLEAR SPACE OR 25 FEET OF COMMODITY.COPLIANCE WITHIN 7 DAYS
13405 | NoData
13406 | NoData
13407 | Have the annual fire extinguisher service/inspection performed on all extinguishers in the facility(3) by a certified company, ensuring new tags are placed.
13408 | Have the annual Fire Alarm Inspection performed and tagged by a certified fire protection company. (The last inspection was noted as 2/13/2020)
13409 | Owner's responsibility. Comply with the above fire code.
13410 | The fire alarm system has been red tagged dated 3./8/2021.The sprinkler system has also been red tagged and have no water pressure.Have the fire alarm and sprinkler systems repaired to compliant status.A continuous in house fire watch shall be implemented 24 hours 7 days a week until both systems have been repaired.Sign Fire Watch Assignment Agreement form.
13411 | I arrived on location to find 6 individual buildings in the apartment community. Three buildings have a red tagged fire alarm system and no water pressure in the sprinkler system. The remaining three buildings have no water pressure in the sprinkler system. I started an intervention form for an standby. I also initiated an in house fire watch agreement form.
13412 | Expired Access Gates Permit(A4)
13413 | NoData
13414 | NoData
13415 | Provide Boiler permits, 250355, 192429, 192430.
13416 | Provide New Installation tag and Blue ITM Tag on new Sprinkler System by New Gym from original Sprinkler company.
13417 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
13418 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
13419 | Provide documentation/report for annual 'Load Test' and any necessary repairs.
13420 | Provide documentation/report for fire damper testing and any necessary repairs.
13421 | Repaint Fire Lane
13422 | Provide elevator permits(2).
13423 | NoData
13424 | NoData
13425 | NoData
13426 | NoData
13427 | F-7 PERMIT FLAMMABLE AND COMBUSTIBLE LIQUID PERMIT EXPIRED
13428 | NoData
13429 | NoData
13430 | P2 permit is expired. Expired on 1/18/2021. Amount owed 385.38 Please pay for permit within 10 days of this notice. If more information is needed about permit, contact the Fire Prevention Permit Office.
13431 | NoData
13432 | Please apply for A4, access gate permit. Fire department access gates require a key box and access gate permit. Upon inspection of permits only key box permit was found. Which had expired 9/14/2018, please renew.
13433 | Please provide documentation for the Sprinkler System annual test.
13434 | Upon opening the 911 box, which controls the access gate, located on the North side of the building the gate did not open. Please have repaired.
13435 | Please perform the Fire Alarm System annual test by a licensed fire alarm company.
13436 | HAND-HELDPORTABLE FIRE EXTINGUISHERS SHALL BE INSTALLED ON THE HANGERS OR BRACKETS SUPPLIEDCOMPLIANCE WITHIN 30 DAYS.
13437 | REPALCEAND OR REPAIR LOCK THAT IN ON THE 911 BOX AT THE REAR HFD ACCESS DOOR WITH A NEWLOCK.COMPLIANCEWITHIN 30 DAYS
13438 | APPROVEDPLANS ARE TO BE KEPT ON SITE AT ALL TIMES.IF APPROVED PLANS CANNOT BE LOCATED, A REQUEST TO THE BUILDING DEPARTMENTMAY BE ABLE TO DUPLICATE THE ORIGINAL. APPROVED PLANS MUST BE SUBMITTED TO FIRE MARSHAL OR THE PROCESS FORHIGH-PILED STORAGE PLAN SUBMITTAL PROCESS SHALL BE RESTARTED.COMPLIANCE WITHIN 30 DAYS.
13439 | ENSURE THATALL DUMPSTERS ARE MAINTAINED 10 FEET MINIMUM FROM THE BUILDING AT ALL TIMES.COMPLIANCE:WITHIN30 CALENDAR DAYS.
13440 | AT LEAST ONEAPPROVED PORTABLE FIRE EXTINGUISHER, HAVING A MINIMUM CAPACITY OF 18 LB. DRYCHEMICAL WITH B:C RATING (AS PER NFPA 58 2011 EDITION SECTION 8.5.1 AND 8.5.2)SHALL BE LOCATED NO MORE THAN 50 FEET FROM THE LP GAS STORAGE LOCATION.SEPARATIONFROM EXPOSURES OF LP GAS CONTAINERS AWAITING USE OR EXCHANGE STORED OUTSIDE OF BUILDINGSSHALL BE A MINIMUM OF 10 FEET FROM EXIT DOORWAY.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
13441 | A WORKINGSPACE (CLEARED OF ALL COMBUSTIBLE MATERIAL) OF NOT LESS THAN 30 INCHES INWIDTH, 36 INCHES IN DEPTH AND 78 INCHES IN HEIGHT SHALL BE PROVIDED IN FRONT OFELECTRICAL SERVICE EQUIPMENT.COMPLIANCEWITHIN 30 DAYS
13442 | NoData
13443 | NoData
13444 | Approved submitted plans for the American Spectaclar event at the George R Brown and conducted a permit inspection(Assembly) in Hall B3.
13445 | NoData
13446 | NoData
13447 | NoData
13448 | NoData
13449 | Move the guy wire next to the fire hydrant to maintain 3 feet of clearance around the hydrant.
13450 | No combustible storage on transformer per code.
13451 | Ensure oily rag cans are emptied daily per code.
13452 | Lower storage height in kitchen area room near rear exit per code.
13453 | No combustible storage allowed per code.
13454 | Secure tank per code.
13455 | Update mobility impaired every 6 months per code. Update emergency contacts including Alley theater contacts. Organize binder.
13456 | Keys not working in Birraporettis B-1 level electrical and mechanical room. Access cards missing for B-1 level. Add correct keys and swipe cards per code.
13457 | Return the above listed locations to their designed fire resistance rating per code. Birraporettis B-1 electrical room repair sheetrock.
13458 | Correct the above fire doors so they close and latch from the open position per code.
13459 | Add two fire phones making a total of 4 per code.
13460 | Add test connection sign to the roof level test connection per code.
13461 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriateinspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualEmergency radio coverage- AnnualFire Extinguishers- AnnualDry pipe partial- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualDry pipe full- 3 YearFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearClean agent – Semi-annualKitchen Hood System- Semi-annualBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
13462 | Provide required clearance around electrical equipment per code.
13463 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. • Present Permits that apply to facility Address listed • on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS.
13464 | Please sign Fire Marshal's Office Owners Statement of Compliance document provided to you.
13465 | Please provide GAS test results of last test showing signature of City of Houston Plumbing Inspector. Please provide gas leak test. To be performed by a licensed plumbing company of your choice.
13466 | NoData
13467 | Please provide the Owner's Statement of Compliance document provided to the assistant MGR at our initial meeting. Please fill-out all sections that apply to your property. (In reference to smoke detectors, fire extinguishers, BBQ-pits, and draft stops.)
13468 | Please repair the 911 phones located by the swimming pools by building #32 and the leasing office. No dial tones. Please repair the swimming pool walk through gate by the leasing office. Located on the right side of pool area by building #7. Upon inspection the gate did not close automatically and latch. Please provide current FIRE EXTINGUISHERS, for ALL LAUNDRY ROOMS, BOILER, MAINTENANCE/SHOP, GYM/WORK-OUT ROOM building #28. Contact a professional fire extinguisher company.
13469 | Please clean lint from lint traps daily. Clean behind all commercial dryers in laundry rooms of lint and dirt.
13470 | Please repair sheet rock in building #12, boiler room and Building #33,LAUNDRY room.
13471 | Please repair/maintain drive through ACCESS GATES near the leasing office. Upon inspection the gate to the left of the office, closest to building #6, did not open when the 911 box was opened and switch activated. Please verify that the access gate to the right of office, closest to building #7, is working properly. Please repair exit access gate by building #1, gate did not open when the 911 box was opened and switch activated. Please repair access gate located on Hollister, near building #4, Upon inspection the gate did not open when the 911 box was opened and switch activated. Repair failsafe 911 box, (the 911 box on the gate with the pull cable inside). Please contact a professional gate company to repair the manual access gates, near building #26, On Hammerly Blvd., and manual gate on Hollister near building #20.
13472 | Please have FIRE HYDRANTS flow tested, by a licensed sprinkler company. Provide documentation upon completion of all testing.
13473 | Please repair smoke detector in GYM/WORK OUT ROOM building #28. Provide ADDITIONAL smoke detector in the room leading to the exit.
13474 | Information Only.
13475 | Please repair exit light in GYM/WORK OUT room, building #28. Provide one emergency light in GYM/WORK OUT room. The emergency light shall have an internal battery back-up, which shall stay on approximately 90 minutes after power failure.
13476 | Please provide a GAS pressure leak test. All testing shall be performed by a licensed plumbing company. Upon completion show signature of City of Houston plumbing inspector.
13477 | NoData
13478 | NoData
13479 | NoData
13480 | Apply for fire alarm permit at 1002 Washington ave.
13481 | Apply for assembly permit at 1002 Washington ave.
13482 | Please renew the A4, access gate permit. Expired 6/8/2019.This is the second notification. Please be advised if the permit is not paid within 10 days, a re-inspection fee will be applied.
13483 | NoData
13484 | Remount the fire extinguisher in the kitchen to ensure the top of the fire extinguisher isn't higher than 5 feet from the ground.
13485 | Move the class k extinguisher located in the side exit hallway and remount in the kitchen area.
13486 | Remove obstructions in front of the exit located on the side of the business.
13487 | Have a licensed fire protection company inspect and tag the vent hood extinguishing system. Have the vent hoods cleaned and tagged with the date of professional cleaning.
13488 | Post address numbers on the front of the business.
13489 | Repair the inoperable emergency illumination on the exit signs.
13490 | Post the occupant load.
13491 | No violations at the time of inspection
13492 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
13493 | NoData
13494 | NoData
13495 | Expired Key/Fire Depository Box(K1)
13496 | NoData
13497 | Please renew the K1, key box permit.Expired 5/9/19.
13498 | Expired Access Gate(a4)
13499 | NoData
13500 | Expired Access Gate(a4)
13501 | Expired Key/Fire Depository Box(k1)
13502 | NoData
13503 | Ensure extinguishers are unobstructed.
13504 | Clear and maintain clearance in front of the breaker panels.
13505 | Ensure all exit doors are unlocked while the building is occupied.
13506 | NoData
13507 | Provide Certificate of Flame Resistance for new blue curtains. (Date)
13508 | Provide Boiler Certificates- 163930, 202120, 239334
13509 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
13510 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
13511 | Provide Documentation/Report for the 5th Year FDC Hydrostatic test. (6/29/2017 BT/YT/ST IMPACT FIRE SERVICES)
13512 | Provide documentation/report for fire damper testing and any necessary repairs.
13513 | NoData
13514 | NoData
13515 | NoData
13516 | The fire suppression system for the vent hoods is due for service before the end of 03/2021.
13517 | Clear and maintain working space in front of the breaker panels.
13518 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
13519 | NoData
13520 | star epps 8326404444
13521 | check out fire extinguisher and sign manager letter.
13522 | replace missing batteries in all smoke detector.
13523 | replace unapproved lock
13524 | Have the exit sign over the exit door on the east side of the building serviced to ensure it is properly illuminated and 100% operational.
13525 | Ensure the microwave and all extension cords are plugged directly into a wall outlet.
13526 | NoData
13527 | NoData
13528 | NoData
13529 | NoData
13530 | NoData
13531 | NoData
13532 | NoData
13533 | NoData
13534 | INFORMATION ONLY
13535 | INFORMATION ONLY
13536 | INFORMATION ONLY
13537 | NoData
13538 | NoData
13539 | INFORMATION
13540 | INFORMATION
13541 | INFORMATION
13542 | NoData
13543 | INFORMATION
13544 | INFORMATION
13545 | INFORMATION
13546 | NEED TO UPDATE ELEVATOR PERMITEXPIRED 1-27-21
13547 | NoData
13548 | YOUR L1 LIQUID/GAS REN PERMIT IS EXPIRED AND MUST BE RENEWED.
13549 | To provide the required fire department access to the FDC which is located behind the newly installed fencing along the Irvington side of the building: Install a KNOX key box and provide a gate key at the pedestrian gate. As well, an all-weather FDC sign (red with white letters) must be installed on the gate to distinguish the gate as the access point for the FDC.
13550 | NoData
13551 | NoData
13552 | COMPLIANCE WITHIN 60 CALENDAR DAYS
13553 | COMPLIANCE WITHIN 60 CALENDAR DAYS.
13554 | COMPLIANCE WITHIN 60 CALENDAR DAYS
13555 | COMPLIANCE WITHIN 60 CALENDAR DAYS.
13556 | COMPLIANCE WITHIN 60 CALENDAR DAYS.
13557 | Fire Fighter phones need to be tested to ensure they are all functioning properly.COMPLIANCE WITHIN 60 CALENDAR DAYS
13558 | COMPLIANCE WITHIN 60 CALENDAR DAYS.
13559 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualFire Extinguishers- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS
13560 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice.COMPLIANCE WITHIN 60 CALENDAR DAYS.
13561 | Permit Expired 3/13/2021; Unpaid $267.53
13562 | NoData
13563 | 8/2020 - OK
13564 | 8/2020 - OK
13565 | 3/2021 - OK
13566 | 8/31/2020 - OK
13567 | 5/7/2020 - OK
13568 | Monthly drills conducted. Log OK.
13569 | 9/18/2018 - OK
13570 | 6/26/2020 - OK
13571 | Remove items blocking access to extinguisher in chemistry/science classroom.
13572 | Remove items obstructing rear exit in chemistry/science classroom.
13573 | Correct all violations within 60 calendar days. Provide action plan for violations that cannot be corrected by compliance date.
13574 | 8/19/2019 - Have fire alarm inspected and correct deficiencies.
13575 | Last audibility 2016 - Have audibility test performed and correct deficiencies.
13576 | Have load bank performed and provide report.
13577 | Last hydro of FDC (for hose cabinets) 2015 - Have hydro performed and correct deficiencies.
13578 | Clean all lint traps daily.
13579 | Remove all combustible items currently stored under stairs.
13580 | Remove all combustible materials from equipment and electrical rooms.
13581 | Place all acids/corrosives in an approved cabinet.Current acid cabinet has failed and must be replaced.
13582 | Replace all missing/damaged ceiling tiles.
13583 | Update EOP to include school level contacts and locations of mobility impaired students.
13584 | Conduct more obstructed fire drills.
13585 | Remove all curtains, drapes, fabrics, and 3D decorations that do not have certificates of flame resistance.
13586 | Update expired boiler certificate (124247).
13587 | Provide HMIS for all hazardous materials stored on campus.Flammable liquids - Class determined by flash point (IA, IB, IC)Combustible liquids - Class determined by flash point (II, IIIA, IIIB)Corrosives - Causes irreparable damage to skin after 4 hours of contactToxic - LD50 (rat, oral) 50mg/kg - 500mg/kgLD50 (rabit, dermal) 200mg/kg - 1000mg/kg, 24 hours or lessLC50 (rat, inhalation) 200ppm - 2000ppm or 2mg/L - 20mg/L, 1 hourHighly Toxic - anything below lowest toxic concentrations, same timelinesCombustible metalsOrganic PeroxidesOxidizing materialsDo not include aerosols on HMIS
13588 | Place "Sprinkler Valve" sign on record storage room door.Ensure all doors leading to roof access have appropriate signs.
13589 | NoData
13590 | NoData
13591 | NoData
13592 | NoData
13593 | NoData
13594 | All extinguishers on site require an annual inspection/test from a certified fire protection company. Ensure that new inspection tags are placed after the inspection. (the last annual inspection tag was January 2019)
13595 | The "K" type (silver) extinguisher in the kitchen must be mounted where it is easily visible and readily accessible. (At the time of inspection it was found to be on a low shelf behind items)
13596 | Ensure that ALL marked exits are unlocked while the building is occupied, and free of any storage at all times. (The secondary main doors were unlocked while inspector was on site and a warning was issued. Any future occurrence will result in an immediate citation)
13597 | The kitchen hood suppression system was red tagged on 11/24/2020 for multiple impairments. Repairs shall be initiated within 72 hours to complete all required corrections in order to bring the system into a fully operational status. Confirmation of initiation must be relayed to the inspector within 72 hours.
13598 | have the annual inspection/test performed on the k type extinguisher in the kitchen. Ensure that a new annual inspection tag is placed.
13599 | Test and Repair/Replace as needed all exit signs to ensure they are illuminated at all times and remain illuminated when the test button is pressed. (specifically noted was the rear exit and main front exit as needing repair)
13600 | The required annual P2: Public Assembly permit expired 3/13/2021. Utilize the attached permit renewal notice and instructions to make payment.
13601 | NoData
13602 | Begin a fire-watch for the open/exposed corridor wall on 1st floor.A Fire Department stand-by may be required if repairs to corridor fire rated walls are not completed in a timely matter.
13603 | Have alarm company come out to service alarm going off in Pump Room
13604 | Electrical panels exposed in first floor electrical room.
13605 | Exposed/Open corridor wall 1st floor. THIS IS A PRIORITY and must be repaired as soon as possible!
13606 | All door closers to stairs, fire doors etc. must be checked for reliability.No door stops are allowed to be used to prop open fire doors
13607 | Failure to service systems will be subject to citations and re-inspection fees.
13608 | Repair emergency lighting to electrical rooms.
13609 | All magnetic locks need to be serviced and repaired.
13610 | Informed the event manager that fire extinguishers will need to be placed at various locations on the field and the main concourse for the use of the L.P. Gas appliances.
13611 | Met with the event manager to inform her of the need for and Inspector standby permit for the use of the L.P. Gas appliances inside the stadium.
13612 | P2 permit expired
13613 | NoData
13614 | NoData
13615 | NoData
13616 | Key box permit K1) expired on 03/17/21. Please contact the HPC office at 832-394-8811 (dial 0) if you require an invoice for amount owed.
13617 | Last inspection 5/2019.Have all portable fire extinguishers inspected.2/22/2021 - OK
13618 | Correct all violations within 60 calendar days. Provide action plan for items that can't be corrected by reinspection date on Page 1.
13619 | Ensure that kitchen ANSUL system is inspected every six months.2/22/2021 - OK
13620 | Provide documentation that all employees received required annual fire safety training.12/18/2020 - OK
13621 | Last egress lighting test 10/24/2019.Have egress lighting system tested and provide documentation that any deficiencies were corrected.12/29/2021 - OK
13622 | Correct all violations within 60 calendar days.
13623 | Remove all combustible items stored in mechanical room above office.
13624 | Conduct and document required annual fire safety training.2/26/2021 - OK
13625 | Repair hole in fire wall in mechanical room above office.Wires that penetrate fire wall must be in conduit, and gaps around conduit must be sealed with approved fire-stopping material.
13626 | Only one obstructed drill documented. At least 50% of fire drill must be obstructed and force occupants to use secondary exits.Conduct and document obstructed drills.
13627 | Have egress lighting tested and document the correction of any deficiencies.2/5/2021 - Tested and repaired - OK
13628 | NoData
13629 | NoData
13630 | NoData
13631 | NoData
13632 | 3-way plugs, multiple outlet adapters and multi-outlet cords are not allowed unless they are "resettable" type (overcurrent protected)
13633 | Portable fire extinguisher(s) annual maintenance expired; requires current inspection
13634 | Mounted portable fire extinguishers are required to meet code
13635 | Min rating for extinguishers in business are 2A:10BC and tagged annually
13636 | NoData
13637 | Commercial Kitchen Hood 6-month (ANSUL) extinguisher maintenance expired; requires current inspection
13638 | Approved multi-outlet power taps must be plugged directly into an outlet. No daisy-chaining of power taps allowed
13639 | Extension cords not allowed as a replacement for permanent wiring
13640 | All junction boxes, light switches and plug outlets must have cover plates installed
13641 | Commercial Kitchen hood requires minimum 6-MONTH inspection for business operations. Sticker needs to be affixed to hood
13642 | Commercial cooking with solid fuel or oil fryers requires Class K rated extinguisher within 30 ft
13643 | Based on size of fryer equipment, a minimum of _1_ extinguisher with at least _1.5__ Gal capacity Class K rated extinguisher is required
13644 | Additional fire extinguisher(s) required. Place ABC red extinguisher - (1) in main sales area, (1) in private room area, (1) in kitchen areas
13645 | Extinguisher(s) missing required labeling
13646 | 5 year gast test required and green tag presented to inspector; Ensure plumber pulls a permit or test will be invalid
13647 | Gas Test Permit required to obtained prior to test
13648 | REMOVE bolt lock from door, not allowed
13649 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs
13650 | Finaled CO in ILMS Proj# 02051284 '97 COR; referred to building dept.
13651 | NoData
13652 | NoData
13653 | NoData
13654 | Owner's responsibility. Comply with the above fire code.
13655 | The fire alarm system has been red tagged dated 3./8/2021.The sprinkler system has also been red tagged and have no water pressure.Have the fire alarm and sprinkler systems repaired to compliant status.A continuous in house fire watch shall be implemented 24 hours 7 days a week until both systems have been repaired.Sign Fire Watch Assignment Agreement form.
13656 | NoData
13657 | Fire hydrants need to be tested every year by fire sprinkler co. Show proof of inspection.
13658 | Fire extinguishers need to be tested every year. Last inspection was in July of 2015.
13659 | For your information.
13660 | Label exterior electrical boxes with the unit number they operate.
13661 | Need to see access gate permit.
13662 | Need to see key box permit.
13663 | Post main address numbers off Galveston rd.
13664 | Need site map near main entrance.
13665 | Entrance gate- Need failsafe pin installed. auto feature not working. paint box red. Need to place failsafe key in 911 box. Exit gate-Repair auto feature. need failsafe pin installed. pain box red. need key to failsafe and manual gate to be placed in 911 box.
13666 | NoData
13667 | NoData
13668 | NoData
13669 | NoData
13670 | NoData
13671 | NoData
13672 | NoData
13673 | NoData
13674 | NoData
13675 | NoData
13676 | NoData
13677 | NoData
13678 | NoData
13679 | NoData
13680 | NoData
13681 | NoData
13682 | NoData
13683 | NoData
13684 | NoData
13685 | NoData
13686 | NoData
13687 | NoData
13688 | Provide address numbers on the front of the business.
13689 | Remove obstructions in front of the class K fire extinguisher located in the kitchen.
13690 | NoData
13691 | NoData
13692 | NoData
13693 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
13694 | NoData
13695 | NoData
13696 | All sprinkler heads shall be free from all obstructions.
13697 | Compliance: 30 calendar days.
13698 | Issued permits shall be kept on the premises designated therein at all times and shall be readily available for inspection.Compliance: 30 calendar days.
13699 | NoData
13700 | NoData
13701 | Have a licensed fire protection company service and tag the fire extinguishers.
13702 | Have a licensed fire protection company service and tag the vent hood suppression system.
13703 | Repair the emergency illumination on the exit signs.
13704 | NoData
13705 | NoData
13706 | NoData
13707 | NoData
13708 | Expired Hazardous Material Permit(h1)
13709 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
13710 | NoData
13711 | Investigated report of a small electrical outlet fire 4 days ago, in apartment #502. Appears the dryer outlet began arcing and smoking. Management was contacted and the dryer outlet was replaced. No signs of further danger and dryer is working correctly. Apartment is occupied. No further action is required.
13712 | - RENEW M3 PERMIT (FUEL DISPENSING) - EXP. 3/17
13713 | The fire alarm system must have an emergency lighting test performed on it.
13714 | All fire extinguishers should be serviced and have a current service tag placed on them.
13715 | The ansul system in the kitchen must have a current inspection performed on it.
13716 | The assembly permit must be renewed.
13717 | Discontinue the use of "piggyback" extension cords in the kitchen area.
13718 | Repair the main entrance door to ensure all doors swing in direction of egress.
13719 | NoData
13720 | NoData
13721 | NoData
13722 | NoData
13723 | NoData
13724 | required label "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING ISOCCUPIED"
13725 | Remove old untagged extinguishers from the property.
13726 | The Vent hoods require professional cleaning. Ensure stickers with the date of cleaning are placed on the vent hoods.
13727 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
13728 | Repair or replace the inoperable emergency illumination on the exit sign located in the kitchen.
13729 | Post the occupant load (98).
13730 | Expired Key/Fire Depository Box(k1)
13731 | no violation found at this time
13732 | NoData
13733 | Please have the fire extinguishers in Boiler Rooms serviced.
13734 | Please sign the Owners Statement of Compliance document and return back to the Fire Marshal.
13735 | NoData
13736 | Please have the fire extinguishers in Boiler Rooms serviced.
13737 | Please sign the Owners Statement of Compliance document and return back to the Fire Marshal.
13738 | Please provide documentation that the Boiler room, or any other building with a gas meter, have had a five year gas test. If it has been over five years please provide a gas leak test. To be performed by a licensed plumbing contractor.
13739 | Ensure locking bars are removed from the exits while the building is occupied.
13740 | Remove obstructions in front of exits.
13741 | NoData
13742 | Red tagged fire alarm panel needs to be repaired.
13743 | NoData
13744 | NoData
13745 | Fire extinguishers are required to have inspection tag with date of service. Repair or replace the red tagged fire extinguisher.
13746 | Repair or replace the inoperable emergency illumination on the exit signs.
13747 | Fire Extinguishers are out of date or missing annual tag.
13748 | Obtain a P2 Places of Assembly Permit for the assembly places in excess of 49 maximum occupant load.
13749 | Fire Sprinklers Do not have Current Tags:Annual TagSprinkler Data Plate is missing
13750 | Install Key Boxes on all secured exterior exits/entrances and place access keys/fobs in the boxes.
13751 | Place a Fire Depository Box as required by LSB #6Place all required information and keys in the Fire Depository Box as per LSB #6
13752 | Maintain and Update the Building File Check List. Comply with all required tests as they come due.
13753 | NoData
13754 | The Fire Alarms in each building Annual Inspection tag is out of date by more than a year. Perform the Fire Alarm Annual Inspection as required by code.
13755 | Make Repairs to the Fire Alarm SystemMaintain Self-Fire Watch until the repairs are made and the fire alarm system is back in service.
13756 | NoData
13757 | NoData
13758 | NoData
13759 | NoData
13760 | NoData
13761 | NoData
13762 | NO VIOLATIONS DISCOVERED DURING FMA INSPECTION CONDUCTED ON 4/5/2021. FMA PERMIT #21019380 APPROVED THIS DATE.CO #19089634 DATED 10/23/2019 1/B/BFACP: ANNUAL INSPECTION CONDUCTED ON 10/9/2020 "ACCEPTABLE"FIRE PUMP: ANNUAL INSPECTION CONDUCTED ON 11/25/2020 "ACCEPTABLE"FIRE EXTINGUISHER: ANNUAL INSPECTION CONDUCTED ON 2/2021 "ACCEPTABLE"
13763 | NoData
13764 | NoData
13765 | FIRE PANEL IN COMPLIANCE 7-1-2020FIRE EXTINGUISHERS IN COMPLIANCE 10-2020SPRINKLER IN COMPLIANCE 6-2020CLASS K IN COMPLIANCE 10-2020BOILER EXPIRE IN 2022
13766 | NEED TO BE SERVICE 6-19 LAST DATE
13767 | NEED TO PUT UP FDC SIGN OUTSIDE
13768 | NoData
13769 | NoData
13770 | NoData
13771 | NoData
13772 | NoData
13773 | NoData
13774 | NoData
13775 | NoData
13776 | NoData
13777 | NoData
13778 | Repair/Replace emergency exits and lights.Comply: Within 30 day.
13779 | Have trouble alarm corrected and annual inspection done for FACP. Date noted on alarm panel was 05/22/2020Comply: Within 72 hours.
13780 | Comply: Within 30 days.
13781 | Comply: Within 72 hours.
13782 | Comply: Within 30 days.
13783 | Repaint the keybox and fail safe box. Add a falcon lock to each one of the boxes.Comply: Within 30 days.
13784 | Comply: Within 30 days.
13785 | Comply: Within 30 days.
13786 | Repair/Replace ceiling tile located in building #2.Comply: Within 30 days.
13787 | Comply: Within 30 days.
13788 | Provide an FDC sign for this building.Comply: Within 30 days.
13789 | NoData
13790 | NoData
13791 | NoData
13792 | NoData
13793 | NoData
13794 | NEED SERVICE , LAST DATE 11-2019
13795 | NEED SERVICE, LAST DATE 2-2019
13796 | NEED SERVICE, LAST DATE 5-2020
13797 | All spare propane bottles shall be stored outside of building in cages 10 ft. away from buildingCompliance: 30 calendar days.
13798 | Move all dumpsters at least 10 ft. away from building.Compliance: 30 calendar days.
13799 | Compliance: 30 calendar days.
13800 | NoData
13801 | NEED SERVICE. 7-2019 LAST DATE
13802 | NoData
13803 | NoData
13804 | NoData
13805 | NEED SERVICE . LAST DATE 6-21-19
13806 | NEED SERVICE . 8-19 LAST DATE
13807 | NoData
13808 | NoData
13809 | NoData
13810 | NoData
13811 | Shall have all portable fire extinguishers inspected and tagged by a licensed fire protection company.
13812 | Cannot place portable fire extinguishers on the ground. They must be mounted according to the fire code listed above. Remove any fire extinguishers that are not being used.
13813 | Must add one 2-A, 10-B:C fire extinguisher to the top and bottom floor of the office.
13814 | Must obtain a S1(Spraying and Dipping Permit) from the Fire Permit Section of the Houston Permitting Center.
13815 | The owner/occupant must obtain all necessary Certificates, permits, and correct all fire code violations.
13816 | Must have a licensed fire protection company to inspect and tag the sprinkler system according to LSB "Inspection and Testing Of Fire Protection and Life-Safety Equipment".
13817 | Must have a licensed fire protection equipment company inspect and tag the spray booth. This must take place every six months according to the LSB standard "Inspection and Testing Of Fire Protection and Life-Safety Equipment".
13818 | Must have a minimum of 3' clearance on all sides of the spray booth. Remove all items that are within three feet of the spray booth.
13819 | Must remove all combustibles and combustible waste throughout the office and warehouse that is accumulating and creating a fire hazard. Remove all empty containers, tires, wood, paper, cardboard, plastics that are creating a fire hazard.
13820 | All compressed gas containers shall have caps and be secured to a fixed object.
13821 | Must remove any items that are blocking or obstructing any fire extinguishers.
13822 | Have all exit signs and emergency lights inspected and repaired as needed.
13823 | Need at least two more No smoking signs in the warehouse around the spray booth.
13824 | Must obtain a H3 and S1 permit from the Permitting Center located at 1002 Washington Avenue Houston Texas 77002. Fire Permit section on the second floor. Phone is 832-394-8811.
13825 | Shall apply for correct occupancy classification according to the City of Houston building department. Apply for occupancy first by emailing the building department and include the business address in the body of the email. occupancy.inspections@houstontx.gov Occupancy phone number is 832-394-8880.
13826 | Must obtain a hot works permit if you are going to have a welding machine or a cutting rig in the business. If you don't want to purchase a hot works permits, remove all spark producing equipment from the building such as the welding machine and cutting rig.
13827 | Must place "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED" on the inside of the marked exit door from the warehouse.
13828 | Garage Storage Room.
13829 | NoData
13830 | Provide Current Annual Service Tags for the Fire Alarm System, Fire Sprinkler System and the Fire Extinguishers.
13831 | NoData
13832 | NoData
13833 | NoData
13834 | Central Plant.
13835 | Provide current Emergency Contact List.
13836 | 1) Repair Sheetrock Holes inside 1st floor Mechanical Room. 2) Replace Ceiling Tile inside 1st floor Mechanical Room.
13837 | Central Plant.
13838 | NoData
13839 | NoData
13840 | HAVE THE EXIT SIGN ABOVE THE LEFT SIDE DOOR OF THE PORTABLE OFFICE BUILDING SERVICED TO ENSURE IT IS OPERATIONAL UNDER BATTERY BACK UP POWER.
13841 | ONCE RECEIVED, POST THE PERMIT IN A CLEARLY VISIBLE PLACE ON THE PREMISES, PREFERABLY NEAR THE CERTIFICATE OF OCCUPANCY..
13842 | REINSPECTION FEES CAN BE APPLIED IF VIOLATIONS ARE NOT CORRECTED PRIOR TO THE FOLLOW UP INSPECTION.
13843 | THE CITY OF HOUSTON REQUIRES AN OCCUPANCY THAT STORES LIQUID CORROSIVES IN QUANTITIES GREATER THAN 50 GALLONS TO OBTAIN A: -HAZARDOUS MATERIALS STORAGE PERMIT
13844 | HAVE ALL EMERGENCY LIGHTING SERVICED BY A LICENSED FIRE PROTECTION COMPANY TO ENSURE THEY ARE 100% OPERATIONAL.
13845 | CITATIONS CAN BE ISSUED IF COMPLIANCE IS NOT OBTAINED.
13846 | INSTALL BREAKER BOX FILLER PLATES INSIDE BREAKER BOXES WITH MISSING BREAKERS/OPEN SPACES.
13847 | REPLACE ALL MISSING OR DAMAGED CEILING TILES. WHERE CEILING TILES ARE PENETRATED BY PIPING OR WIRES, SEAL THE PENETRATION WITH A FIRE STOPPING FOAM/CAULK.
13848 | ENSURE EACH FORKLIFT IS EQUIPPED WITH A FIRE EXTINGUISHER WITH A MINIMUM RATING OF 10:BC AND HAS A CURRENT SERVICE TAG ATTACHED.
13849 | IT IS THE OWNER/OCCUPANTS RESPONSIBILITY TO CORRECT ALL VIOLATIONS FOUND.
13850 | NoData
13851 | NoData
13852 | Renew the required annual permits which expired 2/7/2021: H3: Hot works, S1: Spraying, F7: Flammable/combustible liquids. (see the attached pdf for the permit renewal notice)
13853 | Permits Expired 2/7/2021; Unpaid $921.50
13854 | Have the spray booth extinguishing system 6 mo. inspection/test performed by a certified fire protection company -OR- provide proof of a completed test. (the inspection tag was found to be missing upon inspection)
13855 | Place 704 hazard placards at the point of storage of the oil, antifreeze, and mek. Also place a minimum 12" 704 hazard placard at the main entrance gate using the highest hazard designation per category of all hazardous materials on site.
13856 | Test and Repair/Replace all exit signs to verify they are illuminated normally and when the test button is depressed, to include the integrated emergency exit lights. (specifically noted at the time of inspection was the rear shop exit door)
13857 | ALL FIRE EXTINGUISHERS SHALL BE SERVICED AND TESTED BY A QUALIFIED FIRE PROTECTION COMPANY ANNUAL.
13858 | COMPLY WITHIN ABOVE CODE.
13859 | COMPLY WITHIN ABOVE CODE.
13860 | ONE 2A 10B:C EXTINGUISHER IS NEEDED FOR YOUR LOCATION.
13861 | KAYAN ORIGINAL COPY OF THE CERTIFICATE OF OCCUPANCY MUST BE POSTED IN AVISIBLE PLACE ON THE PREMISES.
13862 | COMPLY WITH ABOVE CODE.
13863 | MOUNT THE FIRE EXTINGUISHER FOLLOWING THE ABOVE CODE. FIRE EXTINGUISHERS ARE REQUIRED TO BE MOUNTED IN AN AREA WHERE IT IS READILY VISIBLE, EASILY ACCESSIBLE, NEAR A COMMON PATH OF TRAVEL, AND NOT SUBJECT TO DAMAGE.
13864 | THE EXIT PATHWAYS AND EXIT STAIRWAYS LEADING AWAY FROM THE WAREHOUSE SHALL HAVE A CLEAR PATH TO AN AREA OF SAFE REFUGE.COMPLIANCE: WITHIN 7 CALENDAR DAYS.
13865 | USING THE FORMAT PROVIDED, A CURRENT HMIS STATEMENT SHALL BE SUBMITTED TO THE HAZMAT / HIGH-PILED 180 TEAM FOR REVIEW. THE HMIS FORM AND INSTRUCTIONS ON HOW TO FILL OUT THE FORM CAN BE FOUND AT THE CITY OF HOUSTON WEBSITE: HTTP://WWW.HOUSTONTX.GOV/FIRE/FORMS/HMISCORRECTLY FILL OUT A NEW HMIS FOR ALL HAZARDOUS MATERIALS STORED INSIDE THE BUILDING. THE WAREHOUSE AREA AND THE HAZARDOUS MATERIALS STORAGE ROOM REQUIRE SEPARATE HMIS’S. THE CLASSIFICATION OF THE HAZARDOUS MATERIALS SHALL COMPLY WITH THE 2012 INTERNATIONAL FIRE CODE CLASSIFICATIONS SYSTEM.IT IS HIGHLY ADVISABLE TO SEEK TECHNICAL ASSISTANCE IN CORRECTLY COMPLETING THE HMIS FOR THE HAZARDOUS MATERIAL BEING STORED ON THE FACILITY.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
13866 | ISSUED PERMITS SHALL BE KEPT AT FACILITY AT ALL TIMES AND SHALL BE READILY AVAILABLE FOR INSPECTION BY THE FIRE CODE OFFICIAL.APPLY FOR AND OBTAIN A F7 (FLAMMABLE/COMBUSTIBLE LIQUIDS STORAGE), H1 (HAZARDOUS MATERIALS), H2 (HIGH-PILED), K1 (KEYBOX), A4 (ACESS GATE),OPERATIONAL PERMIT FROM THE CITY OF HOUSTON PERMITTING CENTER LOCATED AT 1002 WASHINGTON AVE. (832-394-9000). COMPLIANCE: WITHIN 30 CALENDAR DAYS.
13867 | NoData
13868 | # feet of clearance around electrical panels.
13869 | Compliance letters are needed.
13870 | Remove table and chairs from 12th floor mechanical room.
13871 | Update mobility impairment list.Update emergency contact list
13872 | Remove mag locks from stair doors until the can be unlocked remotely.
13873 | NoData
13874 | NoData
13875 | NoData
13876 | NoData
13877 | NoData
13878 | NoData
13879 | Provide documentation/report for 3 year audibility testing and any necessary repairs dated 3/15/2021 Service Tag
13880 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
13881 | Provide documentation/report for fire damper testing and any necessary repairs.
13882 | Repaint Fire Lane
13883 | NoData
13884 | NoData
13885 | NoData
13886 | NoData
13887 | NoData
13888 | NoData
13889 | NoData
13890 | Semi-annual tag expired on kitchen hood systemlast inspected 6/2020
13891 | NoData
13892 | NoData
13893 | Its the owner/occupant responsibility to correct all fire code violations.
13894 | Must remove, clean up, and organize combustibles in the second story loft up the stairs.
13895 | Varnett Charter School
13896 | FDC TEST REQUIRED EVERY 5 YEARS; IF TEST COMPLETED PROVIDE DOCUMENTATION FROM FIRE SPRINKLER COMPANY
13897 | correct the yellow tagged fire sprinkler system
13898 | SIGN REQUIRED TO IDENTIFY THE FIRE DEPARTMENT CONNECTION
13899 | re-inspection fee issued for non compliance with Inspection Report
13900 | NoData
13901 | NoData
13902 | APPLY TO PERMIT ANY SPECIAL SUPPRESSION SYSTEMS IN THE BUILDING
13903 | MAKE REPAIRS NEEDED TO CLEAR ALL RED/YELLOW TAGS FROM ALARM PANEL
13904 | REPAIR AND RETURN TO SERVICE GENERATOR AND TRANSFER SWITCH
13905 | REPAIR AND RETURN TO SERVICE GENERATOR AND TRANSFER SWITCH
13906 | REPAIR AND RETURN GARAGE SPRINKLER AND STANDPIPE SYSTEMS TO SERVICE
13907 | UPDATE FDC SIGN (EXAMPLE PDF IN EMAIL SENT)
13908 | ENSURE 911 KEY BOXES HAVE UP TO DATE KEYS/CARDS
13909 | UPDATE - SUPPLEMENTAL INFORMATION, MOBILITY IMPAIRMENT, ELEVATOR DIAGRAM, FLOOR MAPS
13910 | MAKE SURE ALL KEY SETS ARE OPERATIONAL AND ORGANIZED IN ACCORDANCE WITH LSB 6
13911 | INSTALL SIGN NEAR FIRE DEPOSITORY BOX WITH INDEPENDENT SERVICE KEYS
13912 | NoData
13913 | NoData
13914 | NoData
13915 | NoData
13916 | NoData
13917 | ENSURE PROPER OPENING/CLOSING FORCE ON STAIRWAY DOORS. REMOVE LOCKS FROM RE-ENTRY DOORS
13918 | REPAIR AND RETURN GARAGE SPRINKLER AND STANDPIPE SYSTEMS TO SERVICE
13919 | ENSURE ALL STAIRWAY AND ROOF ACCESS SIGNAGE IS CORRECT
13920 | REPAIR AND RETURN GARAGE SPRINKLER AND STANDPIPE SYSTEMS TO SERVICE
13921 | A DESIGNATED FIRE WATCH MUST BE MAINTAINED. MAKE NEEDED REPAIRS TO ALARM SYATEM TO CLEAR ALL RED/YELLOW TAGS.
13922 | IDENTIFY MANUAL DOOR LOCK OVERRIDE SWITCH IN FCC
13923 | IDENTIFY MANUAL DOOR LOCK OVERRIDE SWITCH IN FCC
13924 | ENSURE ALL STAIRWAY AND ROOF ACCESS SIGNAGE IS CORRECT
13925 | ENSURE ALL STAIRWAY AND ROOF ACCESS SIGNAGE IS CORRECT
13926 | NoData
13927 | NoData
13928 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a gas test permit.
13929 | Repair the broken exit sign located above the exit in the kitchen.
13930 | Repair the inoperable emergency illumination.
13931 | Electronic access gates are required to have a Knox Box and a fail safe/manual disconnect to provide access to the property for first responders. The Knox Box should be securely mounted to a post at the front gate and have a micro switch or toggle switch installed which opens the gate. The Knox Box should house the keys to the lock on the fail safe/manual disconnect. The fail safe/manual disconnect should be mounted to the gate so that the cable can be disconnected and the gate can be manually opened in the event of a power outage, or gate opener failure. There are no additional requirements for the manual access gate on the east end.
13932 | NoData
13933 | Secure a NFPA 704 placard to both front entrance gates. DO NOT use placards that are specific to one particular chemical/substance. The numbers in each section of the placard should represent the highest hazard level of all hazardous materials present at this location.
13934 | The following permits are required for this location: C7 (compressed gas) A4 (access gate) Tier II F7 (flammable/combustible liquid storage)Permits can be obtained atthe Houston Permitting Center:1002 Washington AveHouston, Tx 77002832-394-8811
13935 | Please renew your expired key box (k1) permit. k1 permit expired on 03/18/2021.
13936 | NoData
13937 | Please renew your expired access gate (a4) and key box (k1) permit that expired on 03/22/2021.
13938 | Mr. Womack 7135237402
13939 | 911 keybox is needed by gate
13940 | replace all missing fire extinguisher in all unit 1A:10BC
13941 | Required every 5 years and must be completed with an approved permit from theBuilding Department.
13942 | Replace unapproved lock on main gate.
13943 | obtain keybox permit
13944 | when exiting pre connecting wires for smoke alarm is present it should be utilize. After January 1, 2017, as a battery-operated singlestationalarm is replaced, that smoke alarm shall be replaced with a tamperresistantbattery-operated single-station smoke alarm. Provided, however,nothing in this section shall require an owner to replace an operationalbattery-operated single-station smoke alarm
13945 | Please renew your expired key box (k1) permitfrom 03/22/2021.
13946 | NoData
13947 | NoData
13948 | NoData
13949 | Permit Expired 2/16/2021; Unpaid $267.53
13950 | NoData
13951 | NoData
13952 | NoData
13953 | NoData
13954 | NoData
13955 | NoData
13956 | Foster Home Safety Survey performed: No Violations found at the time of the inspection.
13957 | Throughout facility.
13958 | A written fire drill logshall be kept at premises for review by the fire marshal.Once classes resume.
13959 | Access Gate 3/8/22Assembly 2/5/22
13960 | NoData
13961 | NoData
13962 | NoData
13963 | NoData
13964 | Replace missing fire extinguishers in laundry rooms.
13965 | Need gas leak test performed every 5 years. Last test performed 11/13/2014. Call licenced plumber. Permits required.
13966 | Make sure all boiler rooms are labeled.
13967 | 1st gate on Bessemer- Need new falcon pad lock, unable to open box to check gate function. All other gates had missing or wrong keys to fail safes and manual gate inside 911 box.
13968 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
13969 | Renewal of the assembly permit is required.
13970 | PROVIDE EXIT SIGNS IN KITCHEN
13971 | CURRENT-UP TO DATE FIRE ALARM SYSTEM ANNUAL INSPECTION DATE: 3/5/2019 ACCEPTABLE BLUE TAG SPRINKLER SYSTEM INSPECTION DATE: N/A ANNUAL FIRE EXTINGUISHER INSPECTION DATE: 7/2018 ANSUL SYSTEM BI-ANNUAL INSPECTION DATE: N/A
13972 | MAINTAIN ADEQUATE CLEARANCE BELOW CEILING AT ALL TIMES. 2 FEET OR MORE BELOW THE CEILING IN NONSPRINKLERED AREAS OF BUILDINGS -PE STORAGE (GYM)
13973 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL OF THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY 3 YEARS. PROVIDE WRITTEN DOCUMENTATION OF AUDIBILITY TESTING AND ANY DOCUMENTATION REGARDING REPAIRS OF ANY FAILURES
13974 | PROVIDE REPORT OF TEST RESULTS IF DECORATIVE MATERIALS ARE TO MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701. CERTIFICATE OF FLAME RESISTANCE SHALL INDICATE THE COLOR AND/OR NUMBER FOR ALL DECORATIVE MATERIALS THROUGHOUT SCHOOL. -BLUE AND BLACK STAGE CURTAINS
13975 | ALL EXIT SIGNS SHALL BE ILLUMINATED AT ALL TIMES. -THROUGHOUT SCHOOL
13976 | REMINDER: ALL CURTAINS, DRAPERIES, HANGINGS AND OTHER DECORATIVE MATERIALS SHALL MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701 OR BE NONCOMBUSTIBLE. PROVIDE CERTIFICATE OF FLAME RESISTANCE (SEE FIRE CODE BELOW, 807.2) OR REMOVE ALL THAT DO NOT MEET THE CRITERIA.
13977 | AN APPROVED LICENSED MASTER ELECTRICIAN OR LICENSED ELECTRICAL SERVICE COMPANY SHALL TEST ALL EMERGENCY LIGHTING SYSTEMS ANNUALLY. PROVIDE WRITTEN DOCUMENTATION OF TESTING AND RESULTS. ANY FAILURES OF THE EMERGENCY LIGHTING SYSTEM SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
13978 | REPAINT FIRE LANE
13979 | AN APPROVED HVAC COMPANY SHALL CONDUCT A FULL-FUNCTION TEST AND MAINTENANCE ON ALL FIRE DAMPERS AT LEAST EVERY 4 YEARS. PROVIDE DOCUMENTATION FOR TESTING AND ALL NECESSARY REPAIRS.
13980 | PROVIDE SMOKE DETECTOR -MECHANICAL 1 UPSTAIRS -MECHANICAL 3 UPSTAIRS
13981 | REPAIR ALL DAMAGED, ALTERED, BREACHED OR PENETRATED AREAS OF FIRE-RESISTANCE-RATED CONSTRUCTION. -MECHANICAL 4 CEILING/WALL
13982 | NoData
13983 | NoData
13984 | NoData
13985 | NoData
13986 | NoData
13987 | NoData
13988 | NoData
13989 | A4 and K1 permits expired
13990 | NoData
13991 | NoData
13992 | K1 (911 BOX) PERMIT EXPIRED 1-15-21. RENEW PERMIT WITHIN 10 BUSINESS DAYS
13993 | Place the open breaker in the electrical panel with a metal or plastic spacer and replace the missing switch plates throughout the business.
13994 | Remove all combustibles within 3 feet of the electrical panels.
13995 | Have the existing fire extinguisher inspected by a Licensed Fire Suppression Company and a have a current tag affixed to the extinguisher.
13996 | Owner/Occupant is responsible for Obtaining Certificate of Occupancy, correcting all fire code violations, and purchasing necessary permits listed in this report. Apply for Occupancy by sending the building department the address needing Occupancy(1570 Telephone Rd) at this email address: occupancy.inspections@houstontx.gov
13997 | Must purchase the Flammable/Combustible Liquid Storage and Use permit at the City of Houston Permitting Center. 1002 Washington Avenue. 2nd Floor
13998 | Must obtain and purchase F7 permit for the 300 gallon waste oil tank in the rear of the business.
13999 | NoData
14000 | NEED SERVICE. 9-19 LAST DATE
14001 | NoData
14002 | NoData
14003 | NoData
14004 | NoData
14005 | NoData
14006 | NoData
14007 | NoData
14008 | NoData
14009 | NoData
14010 | NoData
14011 | NoData
14012 | NoData
14013 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY
14014 | EVIDENCE OF INCOMPLETE ORNON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONINGSYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRECODE
14015 | ENSURE ALL CONTENTS ARE FULLY COMPLIANT WITH LSB 5 (INCLUDED IN DOCUMENTS ATTACHED TO THE EMAIL) SUBMIT A FIRE DEPOSITORY KEY BOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THE FIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION; THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED
14016 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED "Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIREDIF THE HIGH-RISE DOES NOT HAVE ANY OF THESESYSTEMS, PLEASE PROVIDE A LETTER ON COMPANY LETTERHEAD (SIGNED AND DATED)DETAILING THE ABSENCE OF THE SYSTEM COMPLIANCE WITHIN 30 CALENDAR DAYS
14017 | NoData
14018 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
14019 | NoData
14020 | NoData
14021 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTIONFEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90DAYS
14022 | NoData
14023 | NEED SERVICE. 8-2018 LAST DATE
14024 | FAILURE TO GET THE FIRE EXTINGUISHERS SERVICE. 8-18 LAST DATE
14025 | NoData
14026 | Correct the yellow tag deficiencies on the fire sprinkler system.
14027 | ITS THE OWNER/AGENT RESPONSIBILITY TO CORRECT AND ABATE ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES. ABIDE BY CERTIFICATE OF OCCUPANCY AT ALL TIMES.
14028 | MAKE ALL CORRECTIONS/REPAIRS PER YELLOW TAG ON SPRINKLER SYSTEM.
14029 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES AND KEEP UPDATED. TRAIN QUARTERLY.
14030 | Replace the missing breaker cover on the breaker panel located in the pool service closet.
14031 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
14032 | NoData
14033 | NoData
14034 | NoData
14035 | Install a fire extinguishers of minimum size 2A:10BC rating on a wall bracket in a easily visible and readily accessible location. (the code sections below give further detail if needed) Also ensure that the extinguisher has a current annual inspection hang tag.
14036 | Repair ASAP.
14037 | Residents must be informed on the proper use of outdoor cooking equipment.
14038 | Please keep all debris from inside all riser rooms. Also, check all heaters for proper operations.
14039 | Toggle switch located inside 911 box does not open electric swing gate.
14040 | Please repair the toggle switch located inside 911 box and add master lock key that secures the Fail Safe pull cord.
14041 | Please label all shutoff with correct unit numbers
14042 | Visually inspect all draft stops located in the attic space.
14043 | verify all sleeping units are supplies with working smoke alarms.
14044 | Please provide last Gas Test date. Gas test shall be done every 5 years.
14045 | Please verify updated Key box permit. My records show permit expired in 2020.
14046 | 2nd fee. FAILURE TO SERVICE SPRINKLER SYSTEM 5-18 AND FIRE EXTINGUISHERS 3-19
14047 | FAILURE TO SERVICE SPRINKLER SYSTEM 5-18 AND FIRE EXTINGUISHERS 3-19
14048 | NoData
14049 | NEED TO BE SERVICE 5-18 LAST DATE
14050 | NEED SERVICE 3-19 LAST DATE
14051 | Wrong code text
14052 | Shop and Boiler Room have wires out of code. Have a Licensed Electrician bring the electrical wiring into compliance with the code.
14053 | The minimum width of the gates is not in compliance. Check that both gates are 13 feet or more in clear opening width.
14054 | Check all units for proper smoke alarm placement.
14055 | The 5 year natural gas test is out of date. The last test on file is 12-11-2009Obtain a natural gas test permit and complete a natural gas test with a licensed plumber.
14056 | Please repair the fire alarm system. Repair any system deficiencies.
14057 | NoData
14058 | P2 permit is expired. Expired on 1/22/2021. Amount owed 503.95 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
14059 | NoData
14060 | NoData
14061 | NoData
14062 | The vent hood suppression system is due for service before the end of 03/2021.
14063 | Fire extinguishers are due for annual service before the end of 03/2021.
14064 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a permit.
14065 | NoData
14066 | Please renew the A4, access gate permit. Expired 3/21/21.
14067 | NoData
14068 | NoData
14069 | NoData
14070 | NoData
14071 | NoData
14072 | NoData
14073 | Semi-annual tag expired on kitchen hood systemlast inspected 6/2020
14074 | NoData
14075 | Repair ASAP.
14076 | Have a licensed fire protection company repair the red tagged alarm panel and correct any deficiencies.
14077 | NoData
14078 | Nonrequired fire protection systems shall be maintained or removed.
14079 | The exceptions listed in the IFC2012.903.2 must be met in order to be considered nonrequired.
14080 | NoData
14081 | Install an exit sign above the main exit to ensure it is identifiable from all points.
14082 | NoData
14083 | Please renew the A4, access gate permit. Expired 1/26/2020.
14084 | NoData
14085 | Complaint was submitted to the building department due to this business not having a certificate of occupancy. Reference# 101004631882
14086 | Properly mount a fire extinguisher to the fork lift with a minimum rating of 10:BC and ensure it has a current service tag attached.
14087 | The front of the occupancy is required to display address numbers that meet the following requirements: At least four (4) inches in height, one half (0.5) inch in stroke width, color that contrasts with the background, and high enough off the ground so that it is not obstructed from view by parked cars.
14088 | The only fire extinguisher in the office at the time of inspection was found in the bottom kitchen cabinet. Relocate this fire extinguisher to the main hall so that it is more centrally located. Properly mount 2 additional fire extinguishers in the warehouse with a minimum rating of 2:A 10:BC. These fire extinguishers are required to be mounted in a location where they are readily visible, easily accessible, and not subject to damage. All 3 fire extinguishers are required to be serviced annually by a licensed fire protection company and have a current service tag attached.
14089 | Install an exit sign with emergency lighting over the exit door near the kitchen/vacant offices. Ensure the exit sign is illuminated at all times under regular service power and battery back up power.
14090 | CERTIFICATE OF FLAME RESISTANCE SHALL INDICATE THE COLOR AND/OR NUMBER FOR ALL DECORATIVE MATERIALS THROUGHOUT SCHOOL. PROVIDE UPDATED CERTIFICATE OF FLAME RESISTANCE -STAGE
14091 | REMOVE ALL THAT ARE NOT IN OPERATIVE CONDITION. -PUSH BUTTON INTERCOM: MECHANICAL ROOM 512, INCLUDING UPSTAIRS
14092 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL OF THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY 3 YEARS. LAST AUDIBILITY TEST DATED: UNKNOWN. PROVIDE WRITTEN DOCUMENTATION OR SERVICE TAG ON FIRE ALARM PANEL SHOWING RESULT OF AUDIBILITY TESTING. ANY FAILURES OF THE AUDIBILITY TESTING SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
14093 | PROVIDE DOCUMENTATION AND/OR REPORT OF TESTING RESULTS AND MAINTAIN ON FILE FOR FIRE CODE OFFICIAL. ALL FAILURES OF THE FIRE DAMPER TESTING SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
14094 | CURRENT INFORMATION -FPS FIRE ALARM SYSTEM ANNUAL INSPECTION DATE: 1/16/2020 ACCEPTABLE BLUE TAG SPRINKLER SYSTEM INSPECTION DATE: 7/19/2019 ACCEPTABLE BLUE TAG ANNUAL FIRE EXTINGUISHER INSPECTION DATE: 7/2019
14095 | REMINDER: ALL CURTAINS, DRAPERIES, HANGINGS AND OTHER DECORATIVE MATERIALS SHALL MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701 OR BE NONCOMBUSTIBLE. PROVIDE CERTIFICATE OF FLAME RESISTANCE (SEE FIRE CODE BELOW, 807.2) OR REMOVE ALL THAT DO NOT MEET THE CRITERIA.
14096 | CORRECT TROUBLE ALERT ON FIRE ALARM SYSTEM CORRECT 1/28/20 ALIEF ISD YELLOW TAG ON FIRE ALARM SYSTEM
14097 | PROVIDE PORTABLE FIRE EXTINGUISHER -115 LOUNGE
14098 | NoData
14099 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES. ABIDE BY CERTIFICATE OF OCCUPANCY AT ALL TIMES.
14100 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES AND KEEP UPDATED. TRAIN QUARTERLY.
14101 | NoData
14102 | NoData
14103 | no violations found at this time
14104 | NoData
14105 | FIRE ALARM PANEL NEEDS ANNUAL TESTING
14106 | LAST FIRE EXTINGUISHER INSPECTION EXPIRED SEPTEMBER 2020
14107 | INFORMATION
14108 | INFORMATION
14109 | POST THE CERTIFICATE OF OCCUPANCY
14110 | FIRE ALARM PANEL YELLOW TAGGED BRING UP TO CODE
14111 | FIRE ALARM PANEL YELLOW TAGGED
14112 | ANSUL SYSTEM NEEDS SEMI-ANNUAL INSPECTION
14113 | FIRE ALARM PERMIT NEEDS TO BE UPDATEDEXPIRED 10-27-2020
14114 | NoData
14115 | no violations at this time
14116 | UPDATE FIRE MARSHAL BINDER
14117 | CHECK ALL EMERGENCY LIGHTS
14118 | INFORMATION
14119 | AS PER CODE
14120 | INFORMATION
14121 | INFORMATION
14122 | NoData
14123 | NoData
14124 | NoData
14125 | NoData
14126 | NoData
14127 | mount all fire extinguishers
14128 | remove all old and use tires from shop area that can create a fire hazards.
14129 | provide and install metal can with a metal lid stating oily rags in red color
14130 | label all breakers to identified in case of fire and or other emergencies
14131 | all fire extinguishers shall be inspected by a certified company once a year and tag.
14132 | provide and install metal brackets and mount all fire extinguishers
14133 | apply for a certificate of occupancy application at 1002 Washington bldg. department section and post
14134 | provide and install exit sign above exit door
14135 | remove all waste oil from ground area where waste oil is been stored in (55) gallon drums and install sign indicating WASTE OIL.
14136 | remove all trash and rubbish away at lease (3) ft such as paper ,rubber ,plastics ,cloth materials from main electrical panel.
14137 | apply for flammable and combustible liquid permit if storing more than (25) gallons of waste oil inside garage or (55) gallons outside at 1002 Washington fire permits section.
14138 | provide and install sign on middle of the exit door inside part
14139 | Please correct deficiencies noted on red tag within 72hrs.
14140 | Audibility test required every 3 years.
14141 | Sprinkler due for 5 year test.
14142 | NoData
14143 | Sign on FDC must indicate which building is covered.
14144 | NoData
14145 | NoData
14146 | NoData
14147 | An Owner Statement of Intended Use was signed on 12-22-2020 as a non-high piled facility. A re-inspection fee has been issued because of this. Lower all high piled storage to 12 feet or below by 4-20-2021. Daily citation can be issued if not in compliance by this date.
14148 | NoData
14149 | Mount the fire extinguishers accordingly.
14150 | A thumb latch lock is only permitted at the main entrance and is required to be unlocked while the building is occupied. All other doors are required to have panic hardware. Remove latch locks on side and rear exits. Panic hardware is required at the side exit.
14151 | Remove curtain in front of the side exit door.
14152 | Clear and maintain space in front of breaker panels.
14153 | Obtain and mount at least 2 fire extinguishers with a minimum rating of 2A:10BC.
14154 | Repair inoperable emergency illumination.
14155 | An assembly permit is required to operate. Obtain permit from the Houston Permitting Center at 1002 Washington Ave. Houston, TX.
14156 | It is the owner/occupants responsibility to correct all fire code violations prior to follow up inspection.
14157 | Must maintain the FACU and Sprinkler system in a normally operative condition, not malfunctioning in any way.
14158 | The Fire Alarms are not powered. Continue self-initiated self-fire watch until all fire protection systems are in normal functioning condition.
14159 | A complaint was submitted to the building department due to this business not having a valid certificate of occupancy. Reference# 101004631953
14160 | Repair ASAP.
14161 | Make sure all evacuation maps are room specific.
14162 | Create and maintain a clear path of travel to all exits inside the occupancy with a minimum width of 36 inches.
14163 | Ensure a clear distance of twenty-four (24) inches between stored commodity and the ceiling surface.
14164 | The front of the occupancy is required to display address numbers that meet the following requirements: At least four (4) inches in height, one half (0.5) inch in stroke width, color that contrasts with the background, and high enough offthe ground so that it is not obstructed from view by parked cars.
14165 | Discontinue/discard the use of damaged extension cords found with open wiring. Ensure all light fixtures are properly secured and NOT hanging by the electrical wires.
14166 | This location is required to have one (1) fire extinguisher with a minimum rating of 2:A 10:BC for every 3000 sq ft of space and every 75 feet of travel. All fire extinguishers are required to be properly mounted in a place where they are readily visible, easily accessible, not subject to damage, and have a current service tag attached from a licensed fire protection company.
14167 | Ensure all exits are properly marked with an exit sign with attached emergency lighting that is illuminated at all times under regular service power and battery back up power.
14168 | NoData
14169 | NoData
14170 | NoData
14171 | NoData
14172 | NoData
14173 | NoData
14174 | NoData
14175 | NoData
14176 | NoData
14177 | provide lubrication to 911 locks for fire department entry. several locks rusted shut.
14178 | provide letter stating that drafstops have no penetrations.
14179 | provide 911 keybox permit.
14180 | NoData
14181 | NoData
14182 | NoData
14183 | Portable fire extinguisher(s) annual maintenance expired; requires current inspection
14184 | Commercial Kitchen Hood 6-month (ANSUL) extinguisher maintenance expired; requires current inspection
14185 | K-rated [Kitchen] (Silver) portable fire extinguisher(s) annual maintenance expired; requires current inspection
14186 | 24" clearance must be maintained between ceiling and combustible materials (Non-sprinkled building)
14187 | Commercial Kitchen hood requires minimum 6-MONTH inspection for business operations. Sticker needs to be affixed to hood
14188 | Could not find CO on site. Finaled CO in ILMS Proj# 96118486 '91 UBC, referred to building dept.
14189 | NoData
14190 | Extension cords not allowed as a replacement for permanent wiring
14191 | 5 year gast test required and green tag presented to inspector; Ensure plumber pulls a permit or test will be invalid
14192 | Gas Test Permit required to obtained prior to test
14193 | REMOVE bolt lock from door, not allowed. Also remove all locks from gate. See 1008.1.9.3 for additional information.
14194 | Please ensure all exit signs and lighting meet code; fix broken or non-working signs
14195 | Door handle twist locks not allowed, replace with approved door locking mechanism
14196 | Approved locking device on door for business must meet requirements 2, 2.1 and 2.2 or use panic / hotel room type hardware
14197 | Portable fire extinguisher(s) annual maintenance expired; requires current inspection
14198 | NoData
14199 | Commercial Kitchen Hood 6-month (ANSUL) extinguisher maintenance expired; requires current inspection
14200 | K-rated [Kitchen] (Silver) portable fire extinguisher(s) annual maintenance expired; requires current inspection
14201 | 3-way plugs, multiple outlet adapters and multi-outlet cords are not allowed unless they are "resettable" type (overcurrent protected). See also 605.4.1
14202 | 3-way plugs, multiple outlet adapters and multi-outlet cords are not allowed unless they are "resettable" type (overcurrent protected)
14203 | Extension cords not allowed as a replacement for permanent wiring
14204 | No missing spacers allowed in electrical panels; All junction boxes, light switches and plug outlets must have cover plates installed
14205 | Commercial Kitchen hood requires minimum 6-MONTH inspection for business operations. Sticker needs to be affixed to hood
14206 | REMOVE bolt lock from door, not allowed
14207 | Finaled CO in ILMS Proj# 94068125, referred to building dept.
14208 | Portable Fire Extinguisher(s) annual maintenance Dt: 2/21
14209 | NoData
14210 | F7 Tier 1 permit required for flammable adhesives used in process. Due to amount (55 gal drum), it must be stored in flammable cabinet
14211 | Definitions for information only. Both gates require access via motorized access (primary) and a fail safe (backup).
14212 | Definitions for information only. Both gates require access via motorized access (primary) and a fail safe (backup).
14213 | NoData
14214 | Existing 911 box on 2nd gate containing fail safe requires functional falcon lock. If door is rusted shut, box needs replacement.1st access gate requires either knox key access for motor and 911 box containing fail safe for compliance.
14215 | Both gates require a main 911 box or knox key activation for the gate motorized function. Additionally both gates require a functioning "fail safe" 911 box that allows manual gate manipulation in the event of a power failure.
14216 | Requirements for using a "911" style box for motorized activation of gate
14217 | Have alarm system serviced and restored to operational readiness condition
14218 | NoData
14219 | ALL FIREEXTINGUISHERS NEEDS TO BE HUNG AND SERVICED
14220 | NEED TO SERVICE THE SPRINKLER SYSTEM ANNUAL
14221 | NEED TO PAY ALL PERMITS DUE
14222 | NEED TO ADD THE EVACUATION SIGN MAP TO ELEVATOR 1ST FLOOR
14223 | NoData
14224 | NEED TO REPLACE /REPAIR ALL EXIT SIGN LIGHTS
14225 | NEED TO DO ANNUAL SERVICE TO THE FIRE PUMP
14226 | NEED TO UPDATE KEYS IN KEY BOX AT ENRTANCE
14227 | NEED TO MAINTAIN ALL PERMITS REQUIRED
14228 | NoData
14229 | NoData
14230 | NoData
14231 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES. ABIDE BY CERTIFICATE OF OCCUPANCY AT ALL TIMES.
14232 | KEPP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES AND KEEP UPDATED. TRAIN QUARTERLY.
14233 | All violations listed in this report must be corrected within 30 DAYS in order to avoid citations and re-inspection fees.
14234 | On 6/12/2020 the fire alarm was yellow tagged for deficiencies. Have a certified fire alarm company correct all deficiencies to bring the system back into full operation with no impairments within 30 DAYS, ensuring that a correction tag is placed once repairs are complete.
14235 | NoData
14236 | NEED TO ADD A SERVICE TAG TO THE FIRE PUMP
14237 | NEED TO REPLACE THE CAPS ON THE FDC
14238 | NEED TO ADD NEW KEYS TO THE KEY BOX
14239 | NEED TO MAINTAIN ALL PERMITS REQUIRED
14240 | NoData
14241 | NoData
14242 | NoData
14243 | NoData
14244 | P2 (ASSEMBLY) AND K1 (911 BOX) PERMITS EXPIRED 1-15-2021. RENEW PERMITS WITHIN 10 BUSINESS DAYS.
14245 | NoData
14246 | A spraying/dipping permit is required for dipping operations. A hazardous material permit is required for the solvent used in the dipping operations. Permits can be obtained at 1002 Washington Ave. Houston TX.
14247 | Ensure dip-tank covers are compliant.
14248 | Ensure transferring of solvent is compliant.
14249 | Complete and return HMIS forms.
14250 | Repair or replace the inoperable emergency illumination.
14251 | An approved automatic fire extinguishing system or dip-tank cover is required in accordance with sec. 2405.3.4
14252 | Ensure ventilation is adequate to prevent the dangerous accumulation of vapors.
14253 | Ensure proper bonding is in place prior to transferring solvent.
14254 | Fire extinguishers are due for annual service before the end of 04/2021.
14255 | Place NFPA 704 hazard identification signs on the door leading to the dipping room and at the main entrance to the building.
14256 | No Violations found at the time of inspection - Annual in home daycare permit approved.
14257 | Label extinguisher cabinet on level 10 by freight elevator per code.
14258 | Ensure levels 18 and 15 have adequate extinguisher coverage per code. If existing extinguishers meet the above requirement then the cabinets missing extinguishers are not required per code.
14259 | Correct exit sign so it is illuminated per code.
14260 | The tanks are showing to be outside the normal pressure range. Have fire protection company inspect the tanks.
14261 | This is a 72 hour notice to correct the restricted re-entry on the above listed locations. If after 72 hours the re-entry is still not compliant, the re-entry doors are to remain unlocked until the re-entry doors can be unlocked from a remote location per code.
14262 | Add 704 diamond to the side of BP generator facing I-10. Add numbers to generator on level B-1 per code.
14263 | Update mobility impaired list in the large fire depository binder per code.
14264 | Unable to access level 12 Stair A. Correct the lock in order for the key on the key ring to work or add a swipe cards to the fire department key rings for access.
14265 | Replace missing independent service key making a total of 2 per code.
14266 | Label door per code.
14267 | Go through the mechanical, electrical and data rooms and return them to their fire resistance rating per code.
14268 | Correct the above fire door so it closes and latches from the open position per code. Go through stairways and correct any additional doors that do not close and latch from the open position.
14269 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriateinspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualEmergency radio coverage- AnnualFire Extinguishers- AnnualDry pipe partial- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualDry pipe full- 3 YearFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearClean agent – Semi-annualKitchen Hood System- Semi-annualBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
14270 | Move items stored in front of mainline disconnects per code.
14271 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. • Present Permits that apply to facility Address listed • on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS.
14272 | NoData
14273 | NoData
14274 | NoData
14275 | Renew the S1 and H3 permits.
14276 | Propane storage within the building is prohibited.
14277 | Have a licensed fire protection company service and tag the spray booth suppression system.
14278 | NoData
14279 | Remove old fire extinguishers or have them inspected with a current inspection tag.
14280 | Remove the exit sign leading to the shop.
14281 | Remove obstructions in front of exits.
14282 | Clear and maintain space around the spray booth.
14283 | Ensure compressed gas cylinders are secured.
14284 | Ensure the exit signs are illuminated in the shop.
14285 | NoData
14286 | NoData
14287 | NoData
14288 | Store all propane tanks outside of building.
14289 | Replace all missing cover plates and junction box covers.
14290 | Cover all fire wall penetrations with fire resistance caulking.
14291 | Remove deadbolts.
14292 | Apply for certificate of occupancy at 1002 Washington ave.
14293 | Remove deadbolts from egress doors.
14294 | Electronic door locks on level 9 by stair A and level 9 stair B are missing the approval stickers from the building department. Contact the city of Houston Occupancy team to verify that the doors have been permitted and approved. Go through building and ensure all electronic locks have approval stickers. If doors are found that have not been permitted, have them permitted through the City of Houston Occupancy team. 1. Electromechanical Locks Question: Are electric strikes, electric mortise and other electromechanical locks required to be permitted? Answer: No, electric mortise sets which do not obstruct the path of egress travel in any way are not required to be permitted in most cases by the City unless placed in elevator lobbies or on exit stair doors of high-rise buildings. Electric strikes which do not obstruct the path of egress travel in any way are not required to be permitted in most cases by the City unless placed in elevator lobbies. Electric strikes have been ruled illegal for use in exit stairs of high-rise buildings under the International Building Code. Note: All plans submitted for an Electric Lock Permit shall show all existing and proposed electric locks on doors in the path of egress travel, including the locks that may not require permitting, so that the City can verify that no combination of locked doors will block egress. Locks within privately leased or inaccessible spaces that are not part of the contract and are not part of the commonly shared egress system are not required to be shown on the plans. 403.12 Stairway door operation. Stairway doors other than the exit discharge doors shall be permitted to be locked from stairway side. Stairway doors that are locked from the stairway side shall be capable of being unlocked simultaneously without unlatching upon a signal from the fire command center. Add electronic lock override switch to the fire alarm panel/fire command center per above code. Compliance in 60 days.
14295 | Post Occupancy load sign in Kulture restaurant per above code. Compliance in 60 days.
14296 | Chairs in Kulture restaurant are blocking exit access. Move tables in order to keep exit access clear. Immediate compliance.
14297 | Secure compressed gas cylinders in Kulture restaurant per above code. Compliance in 60 days.
14298 | Remove chains and locks from Fire department connection in all stairways. Compliance in 1 day.
14299 | Label test connection on roof per above code. Compliance in 60 days.
14300 | Have FM 200 system located on level 2 inspected per above code. Compliance in 60 days.
14301 | Update swipe cards on all fire depository key sets per above code. Compliance in 60 days.
14302 | Level 1 vacant space near main entrance. Compliance gained during inspection.
14303 | Re-label the elevator car motor mainline disconnects in the 8th floor elevator room so they match the car number/letter posted for each car. Compliance in 60 days.
14304 | Correct identification signs leading into domestic tank rooms per above code. Compliance in 60 days.
14305 | Level 1 vacant space near main entrance. Compliance gained during inspection.
14306 | Return the following areas to their designed fire resistance rating per above code. Room 10eo1. By room 8do1 above door to occupancy space. Level 4 mechanical. Room 4m01. Level 1 by IDF room. Go through all mechanical, electrical and IDF rooms and make additional corrections as needed. Compliance in 60 days.
14307 | Update the FDC per above code and example given during notice delivery. Compliance in 60 days.
14308 | Update standardized floor plans for the fire depository binder per above code. Compliance in 60 days.
14309 | Add building specific supplemental information sheet to the fire depository binder. Compliance in 60 days.
14310 | Label Independent service keys per above code. Compliance in 60 days.
14311 | Inspect the fire extinguishers in Kulture restaurant per above code. Compliance in 60 days.
14312 | PERMITS - Permits the Inspector will be looking for are as follows: " Key Box Permit " Flammable and Combustible Permit " Fire Alarm Permit " Elevator Operating Permit " Boiler Permit " Other - Assembly, Access Gates, Batteries, etc. " Certificate of Occupancies " Fire Depository Box / Key Boxes " These are some but not all of the Permits available. " Present Permits that apply to facility Address listed " on Notice. Assembly permit for Kulture Restaurant COMPLIANCE WITHIN 60 CALENDAR DAYS.
14313 | HFC 901.6.2-Records Facility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file). Certificate of Occupancy: Core of Building C of O only Active Fire Permits: Up to date and Paid. Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation. Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards. Fire Alarm Permit: Sprinkler Percentage Letter and Form: Building System Test Documentation LSB # 2 Electronic Locks-Semi Annual Sprinkler System- Annual Fire Alarm System Test- Annual Fire Extinguishers- Annual Fire Hoses- Annual Fire Pumps Flow Test- Annual Emergency Power & Lighting- Annual Generator Test (ATS) - Annual Fire Alarm Audibility Test- 3 Year Fire Hose Pressure Test- 3 year Fire Dampers- 4 Year Fire Alarm Sensitivity- 5 Year FDC Test (Bldg. & Garage) - 5 Year PRV / PRD Test- 5 Year Stair pressurization Test- 5 Year Standpipe System- 5 Year Water Supply Tank Inspection- 5 Year Boiler- Permit Elevator-Annual Permit Dry Partial or Full Trip Test Gas Test- 5 Year COMPLIANCE WITHIN 60 CALENDAR DAYS.
14314 | Add key box per above code. Compliance in 60 days.
14315 | NoData
14316 | NoData
14317 | last annual inspection 4/2017
14318 | last annual inspection 10/2018
14319 | ansul system expired last tested 8/2020
14320 | NoData
14321 | No Violations found at the time inspection: In Home Daycare Inspection
14322 | NoData
14323 | The standpipe hose valves located on the occupant side of levels 44 and 45 need to comply with the above code and NFPA 14. The Horizontal standpipe system, hose valves and hose valve cabinets need to be approved by HFD plans checking.Compliance in 30 days.
14324 | LAST INTERCOM INSPECTION REPORT 12-5-2017BRING UP TO CODE
14325 | FIRE ALARM PANEL RED TAGGED 72 HRS. TO BRING UP TO CODE
14326 | LAST EMERGENCY LIGHTING TEST IN FIRE MARSHAL BINDER WAS 10-23-2019
14327 | LAST ANSUL INSPECTION MAY 2020PAST DUE, BRING UP TO CODE
14328 | INFORMATION
14329 | INFORMATION
14330 | AS PER CODE
14331 | LAST ELEVATOR PERMIT EXPIRED 2ND QUARTER 2020
14332 | Note: Mark the appropriate Type of Inspection/Test Performed on the Blue Tag for the Fire Alarm System. (pic included)
14333 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
14334 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
14335 | Provide documentation/report for fire damper testing and any necessary repairs.
14336 | NoData
14337 | BOTH SYSTEMS YELLOW TAGGED BRING UP TO CODE
14338 | FIRE ALARM YELLOW TAGGED
14339 | SPRINKLER SYSTEM YELLOW TAGGED
14340 | NoData
14341 | RADIO COVERAGENO FIRE FIGHTER PHONES ARE PRESENT IN THE BUILDING. BUILDING MANAGEMENT NEEDS TO SEEK ADVICE ON TESTING THE BUILDING FOR EMERGENCY RADIO COVERAGE BASED ON CHAPTER 10 OF THE FIRE CODE AND 2012 IFC HOUSTON AMENDMENTS.(Follow link to HFD High Rise Team web site with information.)https://www.houstonhighriseflst.org/high-rise-documents/COMPLIANCE WITHIN 60 CALENDAR DAYS.
14342 | MISSING FIRE EXTINGUISHER IN THE CABINET ON UPPER LEVEL #1.COMPLIANCE WITHIN 60 CALENDAR DAYS.
14343 | GARAGE ELEVATOR MECHANICAL ROOM NEEDS UL OILY RAG CAN EMPTIED OF TRASH.COMPLIANCE WITHIN 60 CALENDAR DAYS.
14344 | MOBILITY IMPAIRMENT LIST NEEDS TO BE UPDATED EVERY 6 MONTHS.EMERGENCY CONTACTS LIST NEEDS TO BE UPDATED.COMPLIANCE WITHIN 60 CALENDAR DAYS.
14345 | ANY COMBO LOCKS ON THE PROPERTY NEED TO HAVE THE SAME COMBINATION DIGITS. THAT COMBINATION TAG NEEDS TO BE PLACED ON EACH OF THE 5 KEY SETS IN THE FIRE DEPOSITORY BOX AND LABELED SO IT IS CLEARLY IDENTIFIED AS SUCH.COMPLIANCE WITHIN 60 CALENDAR DAYS.
14346 | FIRE PUMP IS PAST DUE FOR ANNUAL INSPECTION.(MARCH 2020)COMPLIANCE WITHIN 60 CALENDAR DAYS.
14347 | TENANT GENERATOR LOCATED AT BACK OF PARKING GARAGE NEEDS TO HAVE LOOSE DEBRIS AND LEAVES CLEARED OUT. DRY VEGETATION COULD PRESENT A FIRE HAZARD WITH RUNNING MECHANICAL EQUIPMENT. RECOMMEND AREA BE CHECKED MONTGHLY TO KEEP CLEAR.COMPLIANCE WITHIN 60 CALENDAR DAYS.
14348 | STAIRWAY SIGNS ON FLOOR # 6 NEED TO BE CORRECTED TO MIRROR THE REST OF THE STAIR SIGNS.COMPLIANCE WITHIN 60 CALENDAR DAYS.
14349 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriate inspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualFire Extinguishers- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
14350 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice.COMPLIANCE WITHIN 60 CALENDAR DAYS.
14351 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES. ABIDE BY CERTIFICATE OF OCCUPANCY AT ALL TIMES.
14352 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES AND KEEP UPDATED. TRAIN QUARTERLY.
14353 | NoData
14354 | REMOVE COMBUSTIBLE MATERIALS 1. EMPTY BOXES2. TIRES
14355 | COMPLIANCE DATE: 30 CALENDAR DAYS
14356 | REMOVE COMBUSTIBLE MATERIALS 1. EMPTY BOXES2. TIRES
14357 | REMOVE COMBUSTIBLE MATERIALS 1. EMPTY BOXES2. TIRES
14358 | LABEL BREAKERS IN BREAKER BOX
14359 | NoData
14360 | NoData
14361 | Correct all issues with fire alarm (red and yellow tags) within 3 days of this notice.
14362 | Correct all issues with sprinkler system (red and yellow tags) within 3 days of this notice.
14363 | NoData
14364 | NoData
14365 | NoData
14366 | NoData
14367 | NoData
14368 | NoData
14369 | NoData
14370 | NoData
14371 | NoData
14372 | NoData
14373 | NoData
14374 | NoData
14375 | NoData
14376 | NoData
14377 | NoData
14378 | Need updated permit for access gates.
14379 | Required permit
14380 | NoData
14381 | ALL FIRE EXTINGUISHERS SHALL BE SERVICED AND TESTED BY A QUALIFIED FIRE PROTECTION COMPANY ANNUAL.
14382 | MOUNT THE FIRE EXTINGUISHER FOLLOWING THE ABOVE CODE. FIRE EXTINGUISHERS ARE REQUIRED TO BE MOUNTED IN AN AREA WHERE IT IS READILY VISIBLE, EASILY ACCESSIBLE, NEAR A COMMON PATH OF TRAVEL, AND NOT SUBJECT TO DAMAGE.
14383 | COMPLY WITH ABOVE CODE.
14384 | ONE 2A:10BC FIRE EXTINGUISHER IS NEEDED FOR YOU LOCATION.
14385 | SUNJOY RAI
14386 | COMPLY WITH ABOVE CODE.
14387 | MOUNT THE FIRE EXTINGUISHER FOLLOWING THE ABOVE CODE. FIRE EXTINGUISHERS ARE REQUIRED TO BE MOUNTED IN AN AREA WHERE IT IS READILY VISIBLE, EASILY ACCESSIBLE, NEAR A COMMON PATH OF TRAVEL, AND NOT SUBJECT TO DAMAGE.
14388 | NoData
14389 | NoData
14390 | NoData
14391 | Annual Fire Extinguisher inspection required for all fire extinguishers not located inside units.
14392 | all residents shall be informed on the proper use of all outdoor cooking grills
14393 | Please provide a 24" x 24" all weather sign showing building name, address, and contact number in case of emergency.
14394 | please identify the outside electrical panel with proper unit number
14395 | Please make sure all units have 2 working smoke detectors inside units. 1 - bedroom, 2 - path of exit
14396 | 5 year gas test required
14397 | NoData
14398 | key box permit is required for 911 box with Falcon lock
14399 | omit
14400 | omit
14401 | Please replace key lock with a thumb lock on the inside of both exit gates.
14402 | NoData
14403 | NoData
14404 | Provide NFPA 704 signs for the access gates and entrances to buildings.
14405 | Fill out and return HMIS forms. Exempted amounts of flammable/combustible liquids can increase 100% with an approved automatic sprinkler system. Amounts can be increased an additional 100% if stored in approved storage cabinets.
14406 | Remove propane storage from within the building.
14407 | The nonrequired fire sprinkler system and fire alarm system need to be maintained or removed.
14408 | Ensure MSDS are available on premises or electronically.
14409 | Repair or replace the emergency illumination on the exit signs.
14410 | Fire extinguishers were found to be mounted incorrectly. Ensure all fire extinguishers are mounted so that the top of the fire extinguishers are NO HIGHER than 5 feet off the floor and the bottom is AT LEAST 4 inches off of the floor.
14411 | Ensure all exit signs are properly illuminated at all times, under regular service power and battery back up power.
14412 | The A4 (access gate) and K1 (key box) permits on file for this location are not required as the electronic gate does not cross a required apparatus access road. Once the red "911" box is removed from the right hand side of the gate, the A4 and K1 permits will be cancelled.
14413 | Jennifer Tellepsen 7138999442
14414 | service out of date fire extinguisher
14415 | fail safe required on automatic gates
14416 | replace unapproved multiplug
14417 | Show proof of current k1 (keybox permit)
14418 | NoData
14419 | NoData
14420 | NoData
14421 | NoData
14422 | NoData
14423 | NoData
14424 | COMPLIANCE DATE:30 CALENDAR DAYS
14425 | MOUNT (CLASS K) FIRE EXTINGUISHER TO KITCHEN.
14426 | MOUNT A (CLASS K) FIRE EXTINGUISHER TO KITCHEN
14427 | MOUNT A (CLASS K) FIRE EXTINGUISHER TO KITCHEN
14428 | NoData
14429 | NoData
14430 | NoData
14431 | MISSING (10: B/C) FIRE EXTINGUISHER(S) ON THE FORKLIFT(S) SHALL BE REPLACED WITH INSPECTION TAGS APPILED.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14432 | PROVIDE THE APPROPRIATE IDENTIFICATION NFPA 704 PLACARD SIGNS.704 PLACARD SIGNS SHALL BE AT LOCATIONS APPROVED BY THE AUTHORITY HAVING JURISDICTION AND AS A MINIMUM SHALL BE POSTED AT THE FOLLOWING LOCATIONS: (1) TWO EXTERIOR WALLS OR ENCLOSURES CONTAINING A MEANS OF ACCESS TO A BUILDING OR FACILITY.(MINIMUM DIMENSION: 20" PLACARD WITH 8" BLACK NUMBERS)(MINIMUM HEIGHT: 10 FEET) (2) EACH ACCESS TO A ROOM OR AREA. (MINIMUM DIMENSION:12" PLACARD WITH 4" BLACK NUMBERS) (3) EACH PRINCIPAL MEANS OF ACCESS TO AN EXTERIOR STORAGE AREA. (4) NFPA HAZARD RATINGS CAN BE FOUND ON THE MSDS FOR A GIVEN CHEMICAL. ALSO, THIS SYMBOL, OR A FORM OF THIS SYMBOL, OFTEN APPEARS ON THE LABEL OF COMMERCIAL CHEMICAL PRODUCTS. (5)MATERIALS THAT POSSESS OXIDIZING PROPERTIES SHALL BE IDENTIFIED BY THE LETTERS "OX".SPECIAL HAZARDS SYMBOLS SHALL BE SHOWN IN THE FOURTH (WHITE) SPACE OF THE SIGN. (6) MATERIALS THAT POSSESS CORROSIVE PROPERTIES SHALL BE IDENTIFIED BY THE LETTERS "COR".SPECIAL HAZARDS SYMBOLS SHALL BE SHOWN IN THE FOURTH (WHITE) SPACE OF THE SIGN. (7) WHERE MANY CHEMICALS ARE PRESENT, A SINGLE SIGN SHALL SUMMARIZE THE MAXIMUM RATINGS CONTRIBUTED BY THE MATERIAL(S) IN EACH CATEGORY AND THE SPECIAL HAZARD CATEGORY FOR THE BUILDING AND/OR THE AREA.COMPLIANCE WITHIN 30 DAYS
14433 | WHERE REQUIRED ALL HAZARDOUS MATERIALS BARRLES SHALL BE PLACED AND MAINAINED IN APPROPRIATE POSITION AT ALL TIMES.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14434 | ALL LP-GAS CONTAINERS/CYLINDERS AND TANKS SHALL REMAINSECURED ACCORDING TO THE FIRE CODE AT ALLTIMES.IMMEDIATE COMPLIANCE
14435 | A LICENSED FIRE PROTECTION SERVICE COMPANY SHALL CONDUCTHYDROSTATIC AND FLOW TESTS OF ALL FIRE DEPARTMENT CONNECTIONS, PIPING AND CHECKVALVE ASSEMBLIES, NOT LESS THAN EVERY FIVE (5) YEARS.PROVIDE WRITTEN REPORT OF INSPECTION FINDINGS IF COMPLETED WITHINTHE LAST FIVE (5) YEARS.COMPLIANCE: WITHIN 30CALENDAR DAYS.
14436 | APPROVED PLANS ARE TO BE KEPT ON SITE AT ALL TIMES. IF APPROVED PLANS CANNOT BE LOCATED, AREQUEST TO THE BUILDING DEPARTMENT MAY BE ABLE TO DUPLICATE THE ORIGINAL 1002 WASHINGTON AVE HOUSTON TEXAS 77002COMPLIANCE WITHIN 30 CALENDAR DAYS.
14437 | NFPA 13: 12.12.1.1 - PALLETS SHALL BE PERMITTED TO BE STORED IN THEFOLLOWING ARRANGEMENTS:(1) STORED OUTSIDE.(2) STORED IN A DETACHED STRUCTURE.(3) STORED INDOORS WHERE ARRANGED IN ACCORDANCE WITH 12.12.1.2. NFPA 13: 12.12.1.2–PALLETS, WHERE STORED INDOORS, SHALL MEET THEFOLLOWING:(1) PALLETS SHALL BE STORED NO HIGHER THAN 6 FEET.(2) EACH PALLET PILE OF NO MORE THAN 4 STACKS SHALL BE SEPARATED FROM OTHERPALLET PILES BY AT LEAST 8 FEET OF CLEAR SPACE OR 25 FEET OF COMMODITY.COPLIANCE WITHIN 7 DAYS IMMEDIATE COMPLIANCE IS REQUIRED. (NFPA 13 Table A 12.12.1.1)OUTDOOR STORAGE OF IDLE PALLETS:- MINIMUM DISTANCE OF RECOMMENDED CLEARANCE BETWEEN OUTSIDE IDLE PALLET STORAGEAND METAL BUILDING:UNDER 50 PALLETS - 20 FEET50 - 200 PALLETS - 30 FEETOVER 200 PALLETS– 50FEETCOMPLIANCE: WITHIN 30 CALENDAR DAYS.(NFPA 13 11.1.7)High speed low volume fans (HSLV) 24' max diameter shall shut down immediately upon receiving analarmCOMPLAINCE WITHIN 30 DAYS
14438 | HAVE ACERTIFIED RACKING COMPANY REPAIR AND OR REPLACE ANY AND ALL DAMAGED RACKS.COMPLIANCE WITHIN 30 CALENDAR DAYS.
14439 | A WORKING SPACE (CLEARED OF ALL COMBUSTIBLE MATERIAL) OF NOT LESS THAN 30 INCHES IN WIDTH, 36 INCHES IN DEPTH AND 78 INCHES IN HEIGHT SHALL BE PROVIDED IN FRONT OF ELECTRICAL SERVICE EQUIPMENT.COMPLIANCE WITHIN 30 DAYS
14440 | THERE ARE SEVERAL BUILDING WITH OUTSTANDING OR INACTIVE PROJECT NUMBER FOR THE CERTIFICATE OF OCCUPANCY. THIS NEEDS TO BE CLEARED UP WITH THE BUILDING DEPARTMENT TO DETERMINE HOW TO PROCEED. COMPLIANCE WITHIN 30 DAYS.
14441 | NoData
14442 | NoData
14443 | NoData
14444 | NoData
14445 | Need updated permit for access gates.
14446 | NoData
14447 | Correct all the sheet rock and ceiling tiles that is missing through out the building on all floors and rooms that was done during the water damage.
14448 | Required permit
14449 | NoData
14450 | NoData
14451 | NoData
14452 | NoData
14453 | NoData
14454 | NoData
14455 | NoData
14456 | NoData
14457 | INFORMATION
14458 | INFORMATION
14459 | Need sign on door FIRE ALARM PANEL
14460 | INFORMATION
14461 | Library exits down stairs and up stairs, bring up to code
14462 | NoData
14463 | LAST INSPECTION ON FIRE ALARM PANEL2-11-2020
14464 | LAST SPRINKLER RISER INSPECTION2-01-2020
14465 | NoData
14466 | NoData
14467 | NoData
14468 | NoData
14469 | P2 permit is expired. Expired on 3/13/2021. Amount owed 267.53 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
14470 | K-1 permit is expired. Renew permit per code.
14471 | NoData
14472 | Provide Boiler Permits #265332, 265333 (Expired 1/4/21)
14473 | Provide smoke detectors in both rooms.
14474 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
14475 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
14476 | Provide documentation/report for fire damper testing and any necessary repairs.
14477 | Provide certificate of flame resistance, it shall indicate the color for all decorative materials. 1. New curtains, new certificate or 2. New certificate showing retesting of flame resistance
14478 | NoData
14479 | REPAIR ASAP.
14480 | COMPLIANCE DATE: 15 CALENDAR DAYS
14481 | (f7) Houston Fire Prevention Permit is EXPIRED at this time and should be updated immediately.
14482 | NoData
14483 | COMPLIANCE DATE: 15 CALENDAR DAYS
14484 | Houston Fire Prevention (h3) permit is expired at this time and must be updated immediately.
14485 | P2 permit is expired. Expired on 3/16/2021. Amount owed 386.44 Please pay for permit within 10 days of this notice. If more information is needed about permit contact Fire Prevention Permit Office.
14486 | NoData
14487 | NoData
14488 | NoData
14489 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES.
14490 | ALARM SYSTEMS MUST BE INSPECTED AND TAGGED YEARLY.
14491 | NoData
14492 | NoData
14493 | NoData
14494 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
14495 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
14496 | Repaint Fire Lane
14497 | Failed to correct fire code violations before compliance date.
14498 | All emergency door exits need illuminated exit signs, with emergency lighting installed.
14499 | No tag for annual inspection and yellow tagged corrected.
14500 | Need to find if both panels are connected and if so correct the Audibility failure.
14501 | Need annual test for emergency lights.
14502 | Remove all storage that is keep in classroom and exit pathway clear of any obstructions.
14503 | Needs updated tags for testing.
14504 | Tag shows yellow tagged with blue tag. Confusing tags need to be updated.
14505 | Door must open in the direction of travel.
14506 | The exterior gate needs to open in direction of travel and panic hardware installed.
14507 | All interior exit emergency exit doors in older wing and exterior gate need panic hardware installed
14508 | All doors with black mesh need to be removed.
14509 | Needs to be removed and panic hardware installed.
14510 | All exit obstructions need to be cleared and the exterior gate needs to open in direction of travel and panic hardware installed.
14511 | #NAME?
14512 | As an A2 occupancy type with a designated occupant load of 136, as stipulated on your issued Certificate of Occupancy, your facility must hold an annual P2: Public Assembly permit. Obtain the required P2: Public Assembly permit from the Houston Permitting Center and post on site.Houston permitting Center: Fire Permits1002 Washington Ave., 2nd floorHouston, TX 77002Mailing Address:PO Box 3625Houston, TX 77253P: 832.394.8811F: 832.394.9645hfd.permitoffice@houstontx.gov8 am to 3:30 pm
14513 | NoData
14514 | Provide annual test and service tag for fire alarm system.
14515 | Provide annual test and service tag for sprinkler system.
14516 | Provide signage "Sprinkler Riser" on back door
14517 | NoData
14518 | NoData
14519 | NoData
14520 | NoData
14521 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFE AND CODE VIOLATIONS AT ALL TIMES.
14522 | ALL CORRECTIONS MUST BE MADE TO GET YELLOW TAG REMOVED FROM SPRINKLER.
14523 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AND TRAIN QUARTERLY.
14524 | NoData
14525 | NoData
14526 | NoData
14527 | NoData
14528 | NoData
14529 | NoData
14530 | The owner/occupant shall be held responsible for thecorrection and abatement of all violations listed in this notice of violationsreport.
14531 | All fire protection systems and equipment must be tested annually licensed personnel. Have extinguishers and automatic sprinklers properly tested and tagged.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14532 | Lower the pallets of empty plastic containers to below 6 feet.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14533 | Fill out the provided HMIS forms in order to assure that you are below maximum allowed quantities (MAQs). Take care to fill out the forms correctly paying particular attention to the measurements required (i.e., gallons or pounds as required).COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14534 | NoData
14535 | NoData
14536 | NoData
14537 | NoData
14538 | NoData
14539 | NoData
14540 | NoData
14541 | NoData
14542 | NoData
14543 | NoData
14544 | NoData
14545 | Post the evacuation route map in the Schooley Room.Compliance by 4-16-2021
14546 | At least half (6) of all fire drills shall be obstructed and using the secondary routes.
14547 | NoData
14548 | NoData
14549 | ALL OPEN SPACES IN THE BREAKER PANEL SHALL HAVE CIRCUIT BREAKER FILLER PLATES ADDED TO FILL EMPTY SPACES IN THE BREAKER PANEL.
14550 | ALL FIRE EXTINGUISHERS SHALL BE SERVICED AND TESTED BY A QUALIFIED FIRE PROTECTION COMPANY ANNUAL.
14551 | COMPLY WITH ABOVE CODE.
14552 | NoData
14553 | Repair or replace any inoperable EXIT/Emergency lights.
14554 | MAMLEY OLANREWAJUAN ORIGINAL COPY OF THE CERTIFICATE OF OCCUPANCY MUST BE POSTED IN AVISIBLE PLACE ON THE PREMISES.
14555 | Repair or replace any inoperable EXIT/Emergency lights.
14556 | ALL FIRE EXTINGUISHERS SHALL BE SERVICED AND TESTED BY A QUALIFIED FIRE PROTECTION COMPANY ANNUAL.
14557 | COMPLY WITH ABOVE CODE.
14558 | Fix or replace all breaches/holes in ceiling tiles and walls with fire foam or fire caulk.REPLACE ALL MISSING CEILING TILES IN SPRINKLER RISER ROOM.
14559 | COMPLY WITH ABOVE CODE.
14560 | COMPLY WITH ABOVE CODE.
14561 | COMPLY WITH ABOVE CODE. MAKE A BINDER WITH THIS INFORMATION TO SHOW TO THE FIRE MARSHAL WHEN REQUESTED.
14562 | SPRINKLER SYSTEM SHALL BE MAINTANIED IN AN OPERATIVE CONDITION AT ALL TIMES AND SHALL BE REPLCED OR REPAIRED WHERE DEFECTIVE. SPRINKLER SYSTEM IS YELLOW TAG.
14563 | NoData
14564 | NoData
14565 | MOUNT THE FIRE EXTINGUISHER FOLLOWING THE ABOVE CODE. FIRE EXTINGUISHERS ARE REQUIRED TO BE MOUNTED IN AN AREA WHERE IT IS READILY VISIBLE, EASILY ACCESSIBLE, NEAR A COMMON PATH OF TRAVEL, AND NOT SUBJECT TO DAMAGE.
14566 | COMPLY WITH ABOVE CODE.
14567 | The FDC connection must have a sign with 6 inch reflective white lettering on a red background.
14568 | DOOR TO THE SPRINKLER ROOM NEEDS TO BE LABELED. LABEL DOOR WITH SIGN THAT READS "SPRINKLER RISER ROOM"
14569 | NoData
14570 | NoData
14571 | NoData
14572 | NoData
14573 | NoData
14574 | NoData
14575 | NoData
14576 | NoData
14577 | NoData
14578 | NoData
14579 | NoData
14580 | NoData
14581 | NoData
14582 | NoData
14583 | NoData
14584 | NoData
14585 | NoData
14586 | NoData
14587 | NoData
14588 | NoData
14589 | NoData
14590 | NoData
14591 | NoData
14592 | NoData
14593 | NoData
14594 | NoData
14595 | NoData
14596 | NoData
14597 | NoData
14598 | NoData
14599 | NoData
14600 | NoData
14601 | NoData
14602 | NoData
14603 | NoData
14604 | NoData
14605 | NoData
14606 | NoData
14607 | NoData
14608 | NoData
14609 | NoData
14610 | NoData
14611 | FIRE EXTINGUISHERS EXP: AUGUST 2021
14612 | NO VIOLATIONS FOUND AT THIS TIME.
14613 | F7 (FLAMMABLE/COMBUSTIBLE) PERMIT UP TO DATE UNTIL 8-15-21.
14614 | NoData
14615 | Owner's responsibility. Comply with the above fire code.
14616 | The fire alarm system has been red tagged dated 3./8/2021.The sprinkler system has also been red tagged and have no water pressure.Have the fire alarm and sprinkler systems repaired to compliant status.A continuous in house fire watch shall be implemented 24 hours 7 days a week until both systems have been repaired.Sign Fire Watch Assignment Agreement form.
14617 | Mount the fire extinguisher that's been placed on the ground.
14618 | A compressed gas permit is required for O2 storage greater than 504 cu. ft.
14619 | Repair the fail safe on the access gate.
14620 | Repair the toggle switch on the access gate.
14621 | Provide NFPA 704 signs for the access gate and building entrances.
14622 | Fill out and return HMIS forms.
14623 | Provide exit signs in the shop area where the exit signs aren't visible.
14624 | Repair or replace the inoperable emergency illumination on the exit signs.
14625 | NoData
14626 | Must be readable and if missing doors must be retested and tagged
14627 | Make sure tag are readable and those tags that or missing need to have those door tested and tags replaced.
14628 | tags clean
14629 | Do for annual testing
14630 | Must be tested
14631 | Must be tested
14632 | All fire doors must be up to code refer to code NFPA 80
14633 | Due for annual test
14634 | If you want to have fire lanes you must get a permit other then that you must have all curves painted a different color and the words fire lane re moved.
14635 | Remove all excess waste from building
14636 | All items in pump room must be removed
14637 | Place the Houston key boxes in all location that or not the correct box
14638 | Need to place 4 to 6 inches from center of street same side as hydrant
14639 | required to have on location
14640 | Make your FDC signs is replace with one we can read
14641 | Repair damage exits signs and those that or not working
14642 | Required to be on location
14643 | Make sure all keys are placed in 911 boxes
14644 | Post in book or on wall
14645 | Gasoline power washer machine must be remove from building
14646 | NoData
14647 | NoData
14648 | NoData
14649 | Please renew the A4, access gate permit. Expired 3/20/21.Please renew the K1, key box permit. Expired 3/20/21.
14650 | NoData
14651 | NoData
14652 | NoData
14653 | NoData
14654 | HAVE ALL FIRE EXTINGUISHERS INSPECTED AND TAGGED BY AN APPROVED LICENSED FIRE PROTECTION EQUIPMENT COMPANY.
14655 | FIRE EXTINGUISHERS ARE REQUIRED TO BE LOCATED IN THE OFFICE AND WAREHOUSE.
14656 | POST CERTIFICATE OF OCCUPANCY IN A PLACE THAT IS READILY AVAILABLE FOR INSPECTION.
14657 | NoData
14658 | THE DOOR LATCH SHALL RELEASE WHEN SUBJECTED TO A 15-POUND FORCE. THE DOOR SHALL SWING TO A FULL-OPEN POSITION WHEN SUBJECTED TO A 15-POUND FORCE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14659 | CORRECTION AND ABATEMENT OF VIOLATIONS OF THIS CODE SHALL BE THE RESPONSIBILITY OF THE OWNER/OCCUPANT.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14660 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY THREE YEARS.WRITTEN DOCUMENTATION SHALL BE PROVIDED THAT AUDIBILITY MEETS REQUIREMENTS AS SET FORTH IN NFPA 72.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14661 | DOORS IN ELECTRICAL CONTROL PANEL ROOMS SHALL BE MARKED WITH A PLAINLY VISIBLE AND LEGIBLE SIGN STATING "ELECTRICAL ROOM".COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14662 | APPROVED COVERS (SPACERS) SHALL BE PROVIDED FOR ALL SWITCH AND ELECTRICAL OUTLET BOXES.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14663 | SMOKE DETECTOR SENSITIVITY SHALL BE CHECKED WITHIN ONE YEAR AFTER INSTALLATION AND EVERY ALTERNATE YEAR THEREAFTER. AFTER THE SECOND CALIBRATION TEST, WHERE SENSITIVITY TESTS INDICATE THAT THE DETECTOR HAS REMAINED WITHIN ITS LISTED AND MARKED SENSITIVITY RANGE, THE LENGHT OF TIME BETWEEN CALIBRATION TESTS SHALL BE PERMITTED TO BE EXTENDED TO A MAXIMUM OF FIVE YEARS.WRITTEN DOCUMENTATION SHALL BE PROVIDED THAT SMOKE DETECTOR SENSITIVITY MEETS REQUIREMENTS.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14664 | THE POWER SUPPLY FOR MEANS OF EGRESS ILLUMINATION SHALL NORMALLY BE PROVIDED BY THE PREMISES' ELECTRICAL SUPPLY. IN THE EVENT OF POWER SUPPLY FAILURE, AN EMERGENCY ELECTRICAL SYSTEM SHALL AUTOMATICALLY ILLUMINATE ALL THE THE FOLLOWING AREAS: (1-5).ENSURE ALL EMERGENCY EGRESS ILLUMINATION LIGHTS FUNCTION PROPERLY.COMPLIANCE: INFORMATIONAL PURPOSES ONLY.
14665 | THE DOOR LATCH SHALL RELEASE WHEN SUBJECTED TO A 15-POUND FORCE. THE DOOR SHALL SWING TO A FULL-OPEN POSITION WHEN SUBJECTED TO A 15-POUND FORCE.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14666 | CORRECTION AND ABATEMENT OF VIOLATIONS OF THIS CODE SHALL BE THE RESPONSIBILITY OF THE OWNER/OCCUPANT.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14667 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY THREE YEARS.WRITTEN DOCUMENTATION SHALL BE PROVIDED THAT AUDIBILITY MEETS REQUIREMENTS AS SET FORTH IN NFPA 72.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14668 | DOORS IN ELECTRICAL CONTROL PANEL ROOMS SHALL BE MARKED WITH A PLAINLY VISIBLE AND LEGIBLE SIGN STATING "ELECTRICAL ROOM".COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14669 | APPROVED COVERS (SPACERS) SHALL BE PROVIDED FOR ALL SWITCH AND ELECTRICAL OUTLET BOXES.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14670 | A LISTED MANUAL FIRE ALARM BOX PROTECTIVE COVER TO PROVIDE THE MANUAL FIRE ALARM BOX WITH PROTECTION FROM PHYSICAL DAMAGE SHALL BE INSTALLED. THE PROTECTIVE COVER SHALL BE TRANSPARENT OR RED IN COLOR WITH A TRANSPARENT FACE TO PERMIT VISIBILITY OF THE MANUAL FIRE ALARM BOX.EACH COVER SHALL INCLUDE PROPER OPERATING INSTRUCTIONS.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14671 | SMOKE DETECTOR SENSITIVITY SHALL BE CHECKED WITHIN ONE YEAR AFTER INSTALLATION AND EVERY ALTERNATE YEAR THEREAFTER. AFTER THE SECOND CALIBRATION TEST, WHERE SENSITIVITY TESTS INDICATE THAT THE DETECTOR HAS REMAINED WITHIN ITS LISTED AND MARKED SENSITIVITY RANGE, THE LENGHT OF TIME BETWEEN CALIBRATION TESTS SHALL BE PERMITTED TO BE EXTENDED TO A MAXIMUM OF FIVE YEARS.WRITTEN DOCUMENTATION SHALL BE PROVIDED THAT SMOKE DETECTOR SENSITIVITY MEETS REQUIREMENTS.COMPLIANCE: WITHIN 30 CALENDAR DAYS.
14672 | THE POWER SUPPLY FOR MEANS OF EGRESS ILLUMINATION SHALL NORMALLY BE PROVIDED BY THE PREMISES' ELECTRICAL SUPPLY. IN THE EVENT OF POWER SUPPLY FAILURE, AN EMERGENCY ELECTRICAL SYSTEM SHALL AUTOMATICALLY ILLUMINATE ALL THE THE FOLLOWING AREAS: (1-5).ENSURE ALL EMERGENCY EGRESS ILLUMINATION LIGHTS FUNCTION PROPERLY.COMPLIANCE: INFORMATIONAL PURPOSES ONLY.
14673 | Fire protection service contractors shall provide the most recent inspection report to the fire code official. Provide most recent sprinkler system repair report.
14674 | Owner's responsibility. Comply with the above fire code.
14675 | Comply with the above fire code. Repair fire resistance rated construction (drywall) throughout the entire apartment community.
14676 | The fire alarm system has been red tagged dated 3./8/2021.The sprinkler system has also been red tagged and have no water pressure.Have the fire alarm and sprinkler systems repaired to compliant status.A continuous in house fire watch shall be implemented 24 hours 7 days a week until both systems have been repaired.Sign Fire Watch Assignment Agreement form.
14677 | The sprinkler system shall be evaluated by a qualified Fire Protection Engineer or a minimum NICET Level 3 Fire Sprinkler Technician to determine if the system is adequate for the original design of the structure.
14678 | Provide NFPA 704 signs on the access gates and building entrances.
14679 | Fill out and return HMIS forms.
14680 | Repair or replace the inoperable emergency illumination on the exit signs.
14681 | Ensure the exit door hardware is fully operational.
14682 | NoData
14683 | NoData
14684 | NoData
14685 | Fire protection systems shall be maintained in accordance with the original installation standards for that system.
14686 | ALL FIRE EXTINGUISHERS SHALL BE INSPECTED AND TAGGED BY A LICENSED FIRE PROTECTION EQUIPMENT COMPANY "ANNUALLY".
14687 | MOUNT FIRE EXTINGUISHERS SO THAT THEY ARE NOT HIGHER THAN 5FT AND NO LOWER THAN 4 INCHES FROM THE FLOOR.
14688 | ADD 2 FIRE EXTINGUISHERS WITH A MINIMUM FIRE RATING OF 2A-10B:C INSIDE WAREHOUSE. 1 FIRE EXTINGUISHER IS REQUIRED INSIDE AND 2 WITHIN WAREHOUSE.
14689 | provide and install falcon lock on 911 emergency red box with an extra key from your gate lock for fire marshal inspector to put inside.
14690 | NoData
14691 | fire extinguishers to be inspected by a certifide company and tag .
14692 | mount at lease one 2a 10 bc fire extinguisher
14693 | NoData
14694 | NoData
14695 | provide and install an extra key from your gate lock to be install the fire marshal inside the 911 emergency red box.
14696 | need to apply for an application for a certificate of occupancy
14697 | NoData
14698 | no building shall be occupy unless a certificate of occupancy had been issue by the building dept.
14699 | provide and install sign on main exit door on the inside middle of door
14700 | Add new exit sign with emergency light to infant room.
14701 | These lights must be tested annually by a licensed electrician and a documents showing he/she license number and all lights pass or failed.
14702 | Fire Extinguisher tag expired
14703 | Storage must be keep under the 24 inches in non sprinklered buildings.
14704 | NoData
14705 | NoData
14706 | No storage allowed
14707 | any where there is electrical problem please have a certified electrician fix them
14708 | Remove excess waste from property
14709 | remove all combustibles from boiler room and mech room
14710 | place by pedestrian gates
14711 | make sure all gas meters are protected from impact
14712 | cover up all open wiring with cover plates
14713 | All damage sheet rock or missing sheet rock needs to be repaired or replaced in maintenance shop ,boiler room, laundry room for example .
14714 | place on entrance gate
14715 | place in center of street 4 to 6 inches on same side of hydrant .
14716 | Hang up in proper place do not leave on ground and where every missing replace.
14717 | key box with keys or codes located inside with 911 locks on them
14718 | Site map needed with placement of hydrants on map also make sure it can be seen at night .
14719 | Make door numbers a different color
14720 | NoData
14721 | #NAME?
14722 | NoData
14723 | NoData
14724 | NoData
14725 | NoData
14726 | NoData
14727 | NoData
14728 | NoData
14729 | NoData
14730 | NoData
14731 | NoData
14732 | Done on 04/13/2021
14733 | all residents shall be informed on the proper use of all outdoor cooking grills
14734 | done on 04/13/2021
14735 | please identify the outside electrical panel with proper unit number
14736 | Please make sure all units have 2 working smoke detectors inside units. 1 - bedroom, 2 - path of exit
14737 | 5 year gas test required
14738 | NoData
14739 | key box permit is required for 911 box with Falcon lock
14740 | DONE ON 04/13/2021
14741 | omit
14742 | omit
14743 | Done on 04/13/2021
14744 | NoData
14745 | NoData
14746 | NoData
14747 | NoData
14748 | NoData
14749 | NoData
14750 | NoData
14751 | NoData
14752 | NoData
14753 | NoData
14754 | NoData
14755 | NoData
14756 | NoData
14757 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a gas test permit.
14758 | NoData
14759 | NoData
14760 | NoData
14761 | NoData
14762 | NoData
14763 | NoData
14764 | F-7 permit is expired. Renew permit per code.
14765 | NoData
14766 | NoData
14767 | NoData
14768 | NoData
14769 | NoData
14770 | NoData
14771 | Permit Expired 3-2-2021; Unpaid $267.53
14772 | NoData
14773 | NoData
14774 | NoData
14775 | NoData
14776 | NoData
14777 | The 5 year hydrostatic flow test must be completed and passed. Any deficiencies must be corrected.(Compliance in 30 days)
14778 | The required 5 year test must be completed on the water storage tank. Any deficiencies must be corrected.(Compliance in 30 days)
14779 | Ensure that when restocking aisles, product is placed on one side of the aisle before placing in the racks and access is maintained as required by code.
14780 | The required mechanical ventilation failed the "paper test" and requires service. They system must run continuously as required by code. Have all deficiencies corrected and ensure proper ventilation is maintained.(Compliance within 30 days)
14781 | An HMIS must be completed for each control area in the facility in the format provided with this notice.(Compliance in 30 days)
14782 | Ensure separation of incompatible materials is sufficient and all hazardous chemicals are stored as required by approved plans.
14783 | NoData
14784 | NoData
14785 | PERMIT IS 2 YEARS PAST DUE AND REQUIRES RENEWING.
14786 | Upon follow up inspection performed by Inspector Hopkins, a red tag was placed on the sprinkler system dated 1/15/2021 by the fire protection service company. I initiated a 72 hours notice to have the sprinkler system repaired to compliant status. I also notify management to start a in house fire watch until the sprinkler system is returned to compliant status.Upon follow up inspection dated January 22, 2021 the sprinklers system has been repaired. A white service tag is attached replacing the red tag dated 1/15/2021. Supporting photos attached. In house fire watch discontinued.
14787 | NoData
14788 | Fire Alarm System needs annual, audibility and sensitivity test done.
14789 | Provide documentation for sprinkler system annual and 5 year hydrostatic test. All components of system should have a compliance tag attached.
14790 | Remove items (bicycles) blocking means of egress.
14791 | Remove combustible storage from all equipment rooms.
14792 | Fire Depository Box is required for all midrise buildings.
14793 | Identify fire hydrants with square blue reflectors.
14794 | Fire extinguishers are required in the courtyard near the cooking appliances.
14795 | Provide signs for pump room and elevator control room (shutoff).
14796 | 911 Keyboxes are required at all stairwell discharge doors.
14797 | Provide signage for rainwater pit under parking garage.Provide documentation and signage for Permeable Grass required for fire access road.Provide signage identifying the number of hydrants inside of complex.Provide signage for FDC according to LSB # 2.5.4.3
14798 | Provide clearance from electrical panels.
14799 | NoData
14800 | NoData
14801 | NoData
14802 | NoData
14803 | NoData
14804 | NoData
14805 | NoData
14806 | NoData
14807 | NoData
14808 | NoData
14809 | NoData
14810 | NoData
14811 | NoData
14812 | NoData
14813 | NoData
14814 | NoData
14815 | NoData
14816 | NoData
14817 | NoData
14818 | NoData
14819 | NoData
14820 | NoData
14821 | NoData
14822 | NoData
14823 | NoData
14824 | NoData
14825 | NoData
14826 | NoData
14827 | NoData
14828 | NoData
14829 | NoData
14830 | NoData
14831 | NoData
14832 | NoData
14833 | NoData
14834 | NoData
14835 | Babara Mulugeta 713783 1881
14836 | NoData
14837 | NoData
14838 | NoData
14839 | NoData
14840 | required label "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING ISOCCUPIED"
14841 | NoData
14842 | NoData
14843 | NoData
14844 | NoData
14845 | NoData
14846 | NoData
14847 | NoData
14848 | NoData
14849 | NoData
14850 | NoData
14851 | NoData
14852 | NoData
14853 | Oily rag can needed.
14854 | Mobility Impairment list needs to be updated every 6 months and placed in the binder, even if no one is on the list.
14855 | 1 more Independent service key is needed.
14856 | 1 door needed to latch. It is already being worked on.
14857 | NoData
14858 | NoData
14859 | NoData
14860 | NoData
14861 | NoData
14862 | NoData
14863 | NoData
14864 | PERMIT EXPIRED 2/20/2021; UNPAID $267.53
14865 | P2 PERMIT IS EXPIRED AT THIS TIME AND SHOULD BE UPDATED IMMEDIATELY.
14866 | COMPLIANCE DATE: 15 CALENDAR DAYS
14867 | NoData
14868 | NoData
14869 | NoData
14870 | NoData
14871 | NoData
14872 | NoData
14873 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
14874 | NoData
14875 | NoData
14876 | NoData
14877 | NoData
14878 | Please renew the K1, key box permit. Expired 3/29/21.
14879 | NoData
14880 | FIRE PANEL IN COMPLIANCE 7-1-2020FIRE EXTINGUISHERS IN COMPLIANCE 10-2020SPRINKLER IN COMPLIANCE 6-2020CLASS K IN COMPLIANCE 10-2020BOILER EXPIRE IN 2022
14881 | NEED TO BE SERVICE 6-19 LAST DATE
14882 | NEED TO PUT UP FDC SIGN OUTSIDE
14883 | Repair ASAP.
14884 | NoData
14885 | NoData
14886 | NoData
14887 | Remain unlock when occupied" sign must be poste
14888 | NoData
14889 | NoData
14890 | Please renew the A4, access gate permit. Expired 2/23/21.Please renew the K1, key box permit. Expired 3/29/21.
14891 | NoData
14892 | NoData
14893 | Provide documentation for the latest plant evacuation training.Compliance by 5-13-2021
14894 | Provide the annual documentation for all fire alarm and fire suppression systems designated during my inspection.Compliance by 5-13-2021
14895 | Have qualified fire suppression company address the yellow tag issues (semi-annual and annual testing, hydraulic information) and bring the system back into compliance. Compliance by 5-13-2021
14896 | All magnetic locks located within the City Limits of Houston need to be approved by the City Building Department. Information for this process will be provided.Process needs to be started by 5-13-2021
14897 | ALL FIRE EXTINGUISHERS SHALL BE SERVICED AND TESTED BY A QUALIFIED FIRE PROTECTION COMPANY ANNUAL AND HAVE ANNUAL INSPECTION TAG ATTACHED.
14898 | COMPLY WITH ABOVE CODE.
14899 | COMPLY WITH ABOVE CODE.
14900 | COMPLY WITH GROUP S1 REPAIR GARAGE FOR FIRE EXTINGHISHERS.
14901 | PHILLIP MCALILEY.AN ORIGINAL COPY OF THE CERTIFICATE OF OCCUPANCY MUST BE POSTED IN AVISIBLE PLACE ON THE PREMISES.
14902 | ADD ADDRESS NUMBERS TO FRONT DOOR ALONG WITH SUITE NUMBER.4245 RICHMOND AVE. #600
14903 | ALL CONTAINERS WITH FLAMMABLE AND COMBUSTIBLE LIQUIDS SHALL BE STORED IN A FLAMMABLE & COMBUSTIBLE LIQUID CABINET WHEN NOT IN USE.
14904 | MAX AMOUNT OF FLAMMABLE & COMBUSTIBLE LIQUIDS ALLOWED INSIDE IS 5 GALLONS WITHOUT A PERMIT. IF YOU WANT TO HAVE MORE THAN 5 GALLONS STORED INSIDE AN F7 PERMIT WILL BE REQUIRED.
14905 | MOUNT THE FIRE EXTINGUISHER FOLLOWING THE ABOVE CODE. FIRE EXTINGUISHERS ARE REQUIRED TO BE MOUNTED IN AN AREA WHERE IT IS READILY VISIBLE, EASILY ACCESSIBLE, NEAR A COMMON PATH OF TRAVEL, AND NOT SUBJECT TO DAMAGE.
14906 | Go to the Fire Prevention Permit Office 832-394-8811 to obtain a H3 Permit. Business hours: 8:00-3:30 P.M. Mon-Fri. Location: 1002 Washington Ave. Houston Tx. 77002.H3 PERMIT IS REQUIRED FOR CUTTING AND WELDING.
14907 | Please renew the K1, key box permit. Expired 3/29/21.
14908 | NoData
14909 | SERVICE VENT HOOD BY CERTIFIED COMPANY AND HAVE A TAG AFFIXED.
14910 | SERVICE VENT HOOD BY CERTIFIED COMPANY AND HAVE A TAG AFFIXED.
14911 | MOUNT CLASS K FIRE EXTINGUISHER TO KITCHEN AREA.
14912 | MOUNT CLASS K FIRE EXTINGUISHER TO KITCHEN AREA.
14913 | SERVICE VENT HOOD BY CERTIFIED COMPANY AND HAVE A TAG AFFIXED.
14914 | MOUNT CLASS K FIRE EXTINGUISHER TO KITCHEN AREA.
14915 | LABEL CIRCUIT BREAKERS, REMOVE DAMAGED CIRCUIT.
14916 | NoData
14917 | NoData
14918 | NoData
14919 | NoData
14920 | NoData
14921 | NoData
14922 | Owner's responsibility. Comply with the above fire code.
14923 | The fire alarm panel has an yellow tag attached for 4300 and 4310 Dunlavy. Have fire alarm system serviced to achieve compliant status. Sprinkler system shows to be compliant at this time. Performed reinspection on 3/29. The F/A system at 4300 Dunlavy has been repaired. Supporting photos is attached. The F/A system at 4310 Dunlavy is red tagged as of 3/22. Spoke with Savanna of monitoring and she state F/A system was still receiving and sending notifications. Spoke with Jeff of Wilson fire and he stated that they would repaired the panel on 4/5/2021.
14924 | NoData
14925 | NoData
14926 | NoData
14927 | NoData
14928 | NoData
14929 | The fire alarm and sprinkler systems are due for an annual inspection. Have both systems inspected to achieve compliance.Sprinkler system in building 2 and 11 have no water pressure due to pipe rupture from inclement weather.A 24 hrs. 7 days a week inhouse firewatch is required until both systems are back in compliance.
14930 | NoData
14931 | NoData
14932 | NoData
14933 | NoData
14934 | NoData
14935 | Please provide and secure all air conditioning disconnect covers.
14936 | Please mark the unit numbers on exterior of all electric disconnects servicing the apartments.
14937 | NoData
14938 | Note: Required permits shall be obtained. 1. The Houston Fire Department Permit Office is located at 1002 Washington Ave. Houston Texas and may be contacted at 832-394-9083. 2. Contact the Permit Office for any question regarding permits. 3. Required permits shall be renewed annually. Please provide a new K1, key box permit. Permit was canceled 11/14/2016 by Vicky Morris at the permit office because of new ownership at the property. This is a required permit.
14939 | Please repair the micro switch or toggle switch in the "9-1-1" box located at the main entrance to the property. Be advised when fire department access gates are inoperable, gates shall remain open for "9-1-1 emergencies until it can be repaired.
14940 | Please provide City of Houston Fire Marshal's Office the Owners Statement of Compliance. (document will be provided to you to sign)
14941 | Please have the fire hydrants located inside the complex flow tested. All testing shall be performed by a licensed sprinkler company. Provide documentation on all maintenance/service repairs.
14942 | NoData
14943 | NoData
14944 | NoData
14945 | NoData
14946 | NoData
14947 | NoData
14948 | NoData
14949 | NoData
14950 | NoData
14951 | NoData
14952 | NoData
14953 | NoData
14954 | NoData
14955 | NoData
14956 | NoData
14957 | NoData
14958 | NoData
14959 | NoData
14960 | NoData
14961 | NoData
14962 | NoData
14963 | NoData
14964 | NoData
14965 | NoData
14966 | NoData
14967 | NoData
14968 | NoData
14969 | NoData
14970 | NoData
14971 | Permits Expired 3/8/2021; Unpaid $535.06
14972 | 5 YEAR STAIRWELL PRESSURIZATION TEST HAS A LETTER OF CONTENT.
14973 | 4yr DAMPER INSPECTION IS DUE
14974 | 5 YEAR NATURAL GAS TEST IS DUE
14975 | Please provide a sign on the outside of the maintenance room in parking garage "SPRINKLER SYSTEM". Provide an additional sign, the door to the right, inside the maintenance room, "SPRINKLER SYSTEM".
14976 | Please have the hose cabinets stand pipe systems in the parking garage HYDRO tested.
14977 | Repair ASAP.
14978 | NoData
14979 | NoData
14980 | Provide illuminated exit signs in the shop.
14981 | Have a licensed fire protection company inspect and tag the fire extinguishers.
14982 | Replace the inoperable rusted padlock with a replacement Knox or Falcon padlock.
14983 | CITATIONS CAN BE ISSUED IF COMPLIANCE IS NOT OBTAINED.
14984 | IT IS THE OWNER/OCCUPANTS RESPONSIBILITY TO CORRECT VIOLATIONS.
14985 | THE FOLLOWING PERMITS NEED TO BE RENEWED FOR 2018: L1 - LIQUID GAS K1 - KEY/FIRE DEPOSITORY BOX H3 - HOT WORKS OPERATIONS C8 - COMPRESS GAS NON FLAM C7 - COMPRESS GAS A4 - ACCESS GATES IF ANY CHANGES HAVE OCCURED IN THE FACILITY AND IT IS DETERMINED A PERMIT IS NO LONGER NEEDED, CONTACT FIRE INSPECTOR JEREMY SMITH. SEE CONTACT INFORMATION ON PAGE ONE
14986 | POST NEW PERMITS ONCE RECEIVED.
14987 | REINSPECTION FEES CAN BE APPLIED IF VIOLATIONS ARE NOT CORRECTED UPON FOLLOW UP INSPECTION.
14988 | P2 permit is expired. Expired on 2/28/2021. Amount owed 267.53 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
14989 | Your key box permit expired on 3-28-2021.Renew this permit using the options listed on the expired permit renewal form by the date listed.Total amount due is $267.53
14990 | Please renew your expired key box (k1) permitfrom 03/29/2021
14991 | Please renew your expired key box (k1 03/29/2021) permit with HPC at 832-394-8811
14992 | Whererequired by the code official, an application for a permit shall include anHMIS, such as Superfund Amendments and Reauthorization Act of 1986 (SARA) TitleIII, Tier II Report or other approved statement. The HMIS shall include thefollowinginformation: 1. Product Name. 2. Component. 3. Chemical Abstract Service (CAS)number. 4. Location where stored or used. 5. Container size. 6. Hazardclassification. 7. Amount in storage. 8. Amount in use-closed systems. 9.Amount in use-open systems. Use the forms provided. Additional forms may befound at:http://houstontx.gov/fire/formsandpermits/index.htmlhttp://www.houstontx.gov/fire/business/hmisinstructions.pdfBasedupon the amounts and classifications provided on the required HMIS, asupplemental Notice of Violation may be issued to require additionaloperational permits.THEFORM SUBMITTED SHALL SHOW THE PROPERTY ADDRESS, CONTROL AREA ID, PRINTED NAMEOF THE PERSON SUBMITTING THE FORM AND THEIR SIGNATURE, AND DATE. IF THEBUILDING HAS MULTIPLECONTROL AREAS THE FORMS SHALL SHOW THE AMOUNTS IN EACH CONTROL AREA. THEFORM, AS SUBMITTED, SHOWS AMOUNTS IN EXCESS OF THE MAQ FOR THE OCCUPANCYCLASSIFICATION AND COULD RESULT IN MOVING THIS OCCUPANCY TYPE TO AN HOCCUPANCY.COMPLIANCEWITHIN 30 DAYS.
14993 | NoData
14994 | Please renew your expired key box (k1) permit 03/29/2021 with HPC office at 832-394-8811.
14995 | Whererequired by the code official, an application for a permit shall include anHMIS, such as Superfund Amendments and Reauthorization Act of 1986 (SARA) TitleIII, Tier II Report or other approved statement. The HMIS shall include thefollowinginformation: 1. Product Name. 2. Component. 3. Chemical Abstract Service (CAS)number. 4. Location where stored or used. 5. Container size. 6. Hazardclassification. 7. Amount in storage. 8. Amount in use-closed systems. 9.Amount in use-open systems. Use the forms provided. Additional forms may befound at:http://houstontx.gov/fire/formsandpermits/index.htmlhttp://www.houstontx.gov/fire/business/hmisinstructions.pdfBasedupon the amounts and classifications provided on the required HMIS, asupplemental Notice of Violation may be issued to require additionaloperational permits.THEFORM SUBMITTED SHALL SHOW THE PROPERTY ADDRESS, CONTROL AREA ID, PRINTED NAMEOF THE PERSON SUBMITTING THE FORM AND THEIR SIGNATURE, AND DATE. IF THEBUILDING HAS MULTIPLECONTROL AREAS THE FORMS SHALL SHOW THE AMOUNTS IN EACH CONTROL AREA. THEFORM, AS SUBMITTED, SHOWS AMOUNTS IN EXCESS OF THE MAQ FOR THE OCCUPANCYCLASSIFICATION AND COULD RESULT IN MOVING THIS OCCUPANCY TYPE TO AN HOCCUPANCY.COMPLIANCEWITHIN 30 DAYS.
14996 | A WORKING SPACE (CLEARED OF ALL COMBUSTIBLEMATERIAL) OF NOT LESS THAN 30 INCHES IN WIDTH, 36 INCHES IN DEPTH AND 78 INCHESIN HEIGHT SHALL BE PROVIDED IN FRONT OF ELECTRICAL SERVICE EQUIPMENT.COMPLIANCE WITHIN 30 DAYS
14997 | NoData
14998 | NoData
14999 | NoData
15000 | NoData
15001 | NoData
15002 | NoData
15003 | Fire alarm needs annual inspection.
15004 | Jayson Vincent (manager)
15005 | See above-maintain the exit pathway free from obstructions
15006 | NoData
15007 | last annual inspection: 11/2015 by Addick's Fire & Safety
15008 | Please label on the outside of every electrical panel the proper unit number.
15009 | Please add a 2-A, 10-B:C size ABC (red) fire extinguisher in the laundry room.
15010 | Please have at least 2 working smoke detectors inside all units. One smoke detector shall be located inside the bedroom.
15011 | please replace all non-working exit lights on property.
15012 | Please replace batteries and/or detectors in all units and landing areas.
15013 | NoData
15014 | NoData
15015 | Amount Due: $1010.67
15016 | ENSURE ALL STAIRWAY DOORS HAVE PROPER CLOSING FORCE SO THAT THEY CLOSE AND LATCH COMPLETELY ON THEIR OWN POWER.
15017 | ENSURE ALL JUNCTION BOXES AND CONTROL PANELS ARE PROPERLY CLOSED
15018 | EXTINGUISHERS DUE FOR INSPECTION IN MAY 2021
15019 | NO COMBUSTIBLES IN EQUIPMENT ROOMS.
15020 | ENSURE ALL STAIRWAY DOORS HAVE PROPER CLOSING FORCE SO THAT THEY CLOSE ANDLATCH COMPLETELY ON THEIR OWN POWER.
15021 | ENSURE CONTENTS OF THE FIRE DEPOSITORY BOX ARE IN ACCORDANCE WITH LSB STANDARD 6
15022 | ENSURE CONTENTS OF THE FIRE DEPOSITORY BOX ARE IN ACCORDANCE WITH LSB STANDARD 6
15023 | ENSURE CONTENTS OF THE FIRE DEPOSITORY BOX ARE IN ACCORDANCE WITH LSB STANDARD 6
15024 | ENSURE CONTENTS OF THE FIRE DEPOSITORY BOX ARE IN ACCORDANCE WITH LSB STANDARD 6
15025 | ENSURE CONTENTS OF THE FIRE DEPOSITORY BOX ARE IN ACCORDANCE WITH LSB STANDARD 6
15026 | ENSURE CONTENTS OF THE FIRE DEPOSITORY BOX ARE IN ACCORDANCE WITH LSB STANDARD 6
15027 | NoData
15028 | NoData
15029 | NoData
15030 | ENSURE STANDPIPE ROOF TEST CONNECTION HAS A SIGN
15031 | UPDATE GARAGE ELEVATOR CAR NUMBER TO NON-REPEATING NUMBER AND PROPERLY LABEL RECALL FLOOR HOISTWAY DOOR
15032 | INSTALL LOCKOUT/TAGOUT KIT IN GARAGE AND MAIN ELEVATOR CONTROL ROOMS.
15033 | ENSURE ALL EXIT SIGNS ARE PROPERLY ILLUMINATED
15034 | NO COMBUSTIBLES IN EQUIPMENT ROOMS.
15035 | INSTALL ELEVATOR PICTORAL SIGNS IN GARAGE
15036 | NoData
15037 | NoData
15038 | NoData
15039 | NoData
15040 | NoData
15041 | NoData
15042 | Have the exit sign over the exit door on the east side of the building serviced to ensure it is properly illuminated and 100% operational.
15043 | Ensure the microwave and all extension cords are plugged directly into a wall outlet.
15044 | NoData
15045 | LOWER AND MAINTAIN ALL COMMODITIES BELOW 12 FEET UNTILTHE HAZMAT/HIGH-PILED STORAGE TEAM CAN REVIEW AND APPROVAL FOR HIGH-PILED COMBUSTIBLE STORAGE. AT ANY TIME UNTIL THIS AUTHORIZATION IS COMPLETED, IF AN INSPECTION IS DONE AND IT IS NOTED THAT COMMODITIES ARE ABOVE 12 FEET, CITATIONS WILL BE ISSUED AT THAT TIME.COMPLIANCE:WITHIN 7 CALENDAR DAYS AN OWNER'S STATEMENT MUST BE SIGNED
15046 | THE OWNER / OCCUPANT SHALL BE HELD RESPONSIBLE FOR THE CORRECTIONAND ABATEMENT OF ALL VIOLATIONS LISTED IN THIS NOTICE OF VIOLATIONS REPORT.COMPLIANCEWITHIN 7 CALENDER DAYS
15047 | SUBMIT PLANS TO THE BUILDINGDEPT AND THE HAZ-MAT/HIGH PILED 180 TEAM FOR REVIEW AND APPROVAL FORH-OCCUPANCY STORAGE. IT IS ADVISABLETHAT YOU ACQUIRE ASSISTANCE FROM A FIRE PROTECTION ENGINEER FOR THIS PROCESS. STATEINTENDED USE ON APPLICATION.COMPLIANCE: WITHIN 7CALENDAR DAYS.
15048 | NoData
15049 | NoData
15050 | NoData
15051 | NoData
15052 | NoData
15053 | NoData
15054 | NoData
15055 | NoData
15056 | NoData
15057 | NoData
15058 | NoData
15059 | NEED TO DO ANNUAL FIRE EXTINGUISHER SERVICE
15060 | NEED TO DO ANNUAL TEST ON THE FIRE PUMP
15061 | NEED TO UPDATE ALL KEYS IN KEY BOXES
15062 | NEED TO MAINTAIN AND PAY ALL PERMITS REQUIRED AS PER HOUSTON FIRE CODE
15063 | 3-way plugs, multiple outlet adapters and multi-outlet cords are not allowed unless they are "resettable" type (overcurrent protected)
15064 | Portable Fire Extinguisher(s) annual maintenance Dt: 1/21
15065 | 36" Working clearance must be maintained in front of electrical panels
15066 | NoData
15067 | Doors to electrical room(s) must be identified - ELECTRICAL ROOM
15068 | Extension cords not allowed as a replacement for permanent wiring
15069 | All junction boxes, light switches and plug outlets must have cover plates installed
15070 | Additional exit sign required for man door exit from mechanic shop area.
15071 | Portable Fire Extinguisher(s) annual maintenance Dt: 1/21
15072 | Keep all exit door(s) and pathways clear. Please remove any obstacles in front of exit
15073 | NoData
15074 | Hydrants require documented annual flow test
15075 | Doors to electrical room(s) must be identified - ELECTRICAL ROOM
15076 | 3-way plugs, multiple outlet adapters and multi-outlet cords are not allowed unless they are "resettable" type (overcurrent protected)
15077 | Approved multi-outlet power taps must be plugged directly into an outlet. Approved multiplug outlets cannot be powered by extension cord
15078 | Extension cords not allowed as a replacement for permanent wiring
15079 | NO LP or PROPANE storage allowed inside building; Group B, M type occupancy not allowed
15080 | Missing fire extinguisher, please replace
15081 | a4 - Access gate permit required
15082 | k1 - keybox permit required
15083 | 36" Working clearance must be maintained in front of electrical panels and transformers
15084 | Permits required for access gate and key box (a4, k1) were not completed. Reference 2018 inspection #17136399
15085 | D1 permit expired
15086 | All marked exits will be free from obstructions and the doors must be reliable to be opened .
15087 | Last inspected in August/2020. No action required at this time. Must be inspected yearly.
15088 | Shall not store equipment inside the restaurant that is powered by any kind of fuel. Must remove the power washer.
15089 | No combustible storage allowed in electrical rooms according to fire code.
15090 | Must maintain a 3 foot clearance around all electrical panels and transformers.
15091 | Must post occupant load sign near the front entrance. Occupant load is 112.
15092 | NoData
15093 | Have all portable fire extinguishers inspected and tagged. Last inspected was February/2020. This is a yearly inspection.
15094 | It is the owner/occupants responsibility to correct all fire code violations and renew all permits prior to follow up inspection.
15095 | Last inspected August/2020. Must have kitchen suppression system inspected and tagged every six months.
15096 | Must label the door leading into the electrical room as ELECTRICAL ROOM.
15097 | Must have a gas test performed every five years by a licensed plumber with the City of Houston. Last gas test performed was 2/9/2011 according to ILMS.
15098 | Prior to the gas test, the licensed plumber shall purchase a gas test permit from the City of Houston Permitting Center located at 1002 Washington Avenue.
15099 | Make sure all exits signs are operating properly and correct if needed.
15100 | Must renew the expired Assembly/P2 permit prior to follow up inspection.
15101 | NoData
15102 | Obtain the following Fire prevention permits: Flammable liquids, Fuel dispense, LPG, Cryogenic fluids, Key box, Access gate.
15103 | Ensure emergency fuel disconnect is properly installed and labeled.
15104 | Have a licensed fire protection company perform an annual inspection on the fire sprinkler system.
15105 | Ensure exits are free from obstructions.
15106 | Have a licensed fire protection company perform an annual fire alarm inspection.
15107 | Provide FDC sign next to the FDC.
15108 | Provide warning sign for fueling station.
15109 | Repair the inoperable emergency illumination on the exit signs.
15110 | Ensure exits are unlocked while the building is occupied.
15111 | NoData
15112 | NoData
15113 | NoData
15114 | NoData
15115 | NoData
15116 | Renew the fire prevention assembly permit before the end of 02/2021.
15117 | Have vent hoods cleaned by a professional cleaning service. Ensure date of cleaning sticker is placed on the vent hoods.
15118 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a gas test permit.
15119 | NoData
15120 | NoData
15121 | NoData
15122 | 3-year audibility test needs to be performed, correct any deficiencies and report provided to fire marshal
15123 | ITS THE OWNER/AGEN RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES. COMPLY WITH CERTIFICATE OF OCCUPANCY AT ALL TIMES.
15124 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES AND KEEP UPDATED. TRAIN QUARTERLY.
15125 | Amount Due: $386.44
15126 | NoData
15127 | NoData
15128 | Mount the class K fire extinguisher located on the ground in the kitchen area.
15129 | Correct the yellow tagged sprinkler deficiencies.
15130 | Repair or replace the inoperable emergency illumination.
15131 | NoData
15132 | NoData
15133 | NoData
15134 | NoData
15135 | Apply for fire alarm permit.
15136 | THIS LOCATION HAS AN HISD HIGH SCHOOL ON THE SECOND FLOOR WITH NO CERTIFICATE OF OCCUPANCY FOR THE SCHOOL. (MIDDLE COLLEGE HIGH SCOOL HISD)
15137 | NEED TO APPLY FOR AN EDUCATIONAL CERTIFICATE OF OCCUPANCY FOR THE HIGH SCHOOL ON THE SECOND FLOOR(MIDDLE COLLEGE HIGH SCOOL HISD)
15138 | FIRE EXTINGUISHERS NEED TO BE SERVICE TO REPLACE THE RED TAGS ON THEM (HCC)
15139 | NEED TO ADD SIGNS FOR THE FIRE ALARM ROOM AND RISER ROOM (HCC)
15140 | NoData
15141 | Remove all combustible items inside this room
15142 | NoData
15143 | Remove all combustibles from room.
15144 | Alarm Panel must be keep free from any objects or picture covering in order to hide the view of the fire alarm panel. Picture must be removed.
15145 | All doors inside class room must be kept in its original use. It appears that the glass window was removed from theses doors. I am asking for the City of Houston approved plans identifying that these doors were installed without the protective glass window.
15146 | NoData
15147 | NoData
15148 | door must open freely and not be stuck when using panic hardware. Door must be corrected within 24 hrs.
15149 | Blocked Exit door must be corrected within 24 hrs.
15150 | All emergency exit doors must open, close and latch on its own. Panic hardware must not have more than 5 lb. of pressure when opening.
15151 | Fail to correct fire code violations by compliance date. Reinspect must be paid and follow up in 30 days from this date 3/5/2021
15152 | All extra tables and chairs must be remove from room and cleared from exit door.
15153 | NoData
15154 | NEED TO BE SERVICE , HAS TROUBLE LIGHT ON. 9-20-20 LAST DATE
15155 | IN COM[PLIANCE. 8-20 LAST DATE
15156 | IN COM[PLIANCE. 7-20 LAST DATE
15157 | IN COM[PLIANCE. 9-20 LAST DATE
15158 | IN COM[PLIANCE. 7-20 LAST DATE
15159 | FIRE EXTEINGUISHER NEED SERVICE 4-19 LAST DATE
15160 | NEED SERVICE 4-19 LAST DATE
15161 | NoData
15162 | NoData
15163 | not more then 5ft from the floor.
15164 | Jeremy Haar 7025581545
15165 | install 911 keybox on main gate.
15166 | Label circuit breaker
15167 | Replace 10years old smoke detector, replace missing battery
15168 | last annual inspection: 11/2015 by Addick's Fire & Safety
15169 | NoData
15170 | Please add a 2-A, 10-B:C size ABC (red) fire extinguisher in the laundry room.
15171 | Please have at least 2 working smoke detectors inside all units. One smoke detector shall be located inside the bedroom.
15172 | please replace all non-working exit lights on property.
15173 | Please replace batteries and/or detectors in all units and landing areas.
15174 | NoData
15175 | THIS LOCATION HAS BEEN CLOSED FOR BUISNESS DUE TO COVID-19. I CANT CONTACT ANY OFFICIALS FOR THIS LOCATION 713-654-1400
15176 | NoData
15177 | NEED SERVICE. 5-18 LAST DATE
15178 | NoData
15179 | NoData
15180 | remove all trash and rubbish including old tires ,papers, and any other trash from premises
15181 | Remove all extension cords that are been use on permanet
15182 | replace ceiling tile missing in the office area.
15183 | Remove all obstructions or relocate fire extinguisher.
15184 | Remove all gas plastic containers from inside of shop area and replace with an approved metal gas can for storing gasoline up to (5) gallons with out having to apply for a permit.
15185 | Parovide and install sign at the middle part of the official exit door.
15186 | Sign letter provided.
15187 | Have fire hydrants tested by a fire sprinkler co. and provide proof of inspection.
15188 | Sign letter provided.
15189 | Sign letter provided.
15190 | 5/2020Have ANSUL system inspected and have any deficiencies corrected.2/2021 - OK
15191 | Per code.
15192 | Provide documentation that required annual fire safety training was conducted.Training conducted 1/26/2021 - OK
15193 | Place "Sprinkler Riser" sign on outside of hallway door that leads to storage area under/behind stage.
15194 | Replace all missing/damaged ceiling tiles (including inside riser room)
15195 | Some rooms are missing evacuation maps. Ensure maps are posted near all classroom exits.
15196 | 1/23/2021 - Fire alarm RED TAGCorrect red tag conditions within 72 hours (see inspection report 321799 e-mailed on 1/27/2021).Corrected 1/26/2021 - OK
15197 | Pay reinspection fee within 10 calendar days.
15198 | 6/2018Have all portable fire extinguishers inspected
15199 | Add one fire extinguisher to hallway near nurse's office.
15200 | Remove all tables from auditorium egress hallway.
15201 | Correct all violations within 60 calendar days.
15202 | 6/2/2015Have sprinkler system inspected and any deficiencies corrected.
15203 | 12/18/2015Have 5-year hydro performed and have any deficiencies corrected.
15204 | Remove all obstructions that prevent access to riser room. Remove items blocking electrical panels in storage area under/behind stage.
15205 | Remove open wire splice on refrigerator in kitchen (top-rear of refrigerator near kitchen hood).Cover open junction box in boiler room.
15206 | Renew expired elevator permit.
15207 | Have egress lighting test performed and provide documentation that any deficiencies were corrected.
15208 | Disregard
15209 | Please provide four signs. (1st sign)"FIRE ALARM PANEL ACCESS USE SIDE PEDETRIAN GATE", with an arrow pointing to the left. Place on main entrance door to leasing office. (2nd sign)"FIRE ALARM PANEL". Pedestrian gate. Place on outside double doors accessing the building/ stairs. (3rd sign) "FIRE ALARM PANEL." Place on the wall to the right of door, in stairwell with an arrow pointing up. (4th sign) "FIRE ALARM PANEL" Place on fire alarm panel room DOOR.
15210 | Please provide a 911 access with a KNOX box at the rear gate. Feeder road off the 610 Loop.Remove chain from the gate and repair the drop down bar. Place key/keys inside KNOX box to access property.
15211 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
15212 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
15213 | Provide documentation/report for annual 'Load Test' and any necessary repairs.
15214 | Provide report for annual inspection, test and service tag for sprinkler system.
15215 | Provide report for annual inspection, test and service tag for sprinkler system.
15216 | Provide Documentation/Report and tag for the 5th Year FDC Hydrostatic test.
15217 | Provide documentation/report for fire damper testing and any necessary repairs.
15218 | Provide annual inspection and service tag of fire extinguishers.
15219 | Repaint Fire Lane
15220 | Provide Portable Fire Extinguisher Signage on door
15221 | Provide Signage for Sprinkler Riser on/by door
15222 | Inspect and Service tag commercial kitchen hood system. Correct all red tag impairments immediately.
15223 | 5/2020Have ANSUL system inspected.2/2021 - OK
15224 | Obstructed drills documented - OK
15225 | Pay reinspection fee within 10 calendar days.
15226 | 9/2019Have all portable fire extinguishers inspected.
15227 | Correct all violations within 60 calendar days.
15228 | 2/14/2018 - HAVE SPRINKLER SYSTEM INSPECTED
15229 | Have dampers tested and provide documentation that deficiencies were corrected.
15230 | Conduct and document required annual fire safety training.
15231 | Provide updated EOP for 20-21 school year.
15232 | Updated expired elevator permit.
15233 | 1/17/2020Have egress lighting test performed and provide documentation that deficiencies were corrected.
15234 | NoData
15235 | Please provide four new HFD 2 signs for the access gates. Provides incoming fire apparatus knowledge that fire hydrants are inside the complex.
15236 | The manual gate under sign nearest to Hollister Rd., needs chain removed and a drop down bar with hasp and lock to secure gate. Key for that lock shall be placed in 911 box for the fire departmentThe manual gate by the park needs updated key placed in 911 box. Did not open the lock, wrong key. The 911 box was very hard to open and close needs repair.Automatic exit gate by bldg. #1, key provided in 911 box did not open the lock on the manual gate to the right of the automatic gate.Automatic entrance gate by bldg. #2B. Please change the switch out in 911 box to a micro switch or toggle switch. (Household switch not allowed.) Repair the manual gate next to the automatic gate someone in a pick-up truck today bumped the gate, and moved it about a foot.
15237 | Please have the two fire hydrants inside the complex, in the very back, flow tested. To be performed by a licensed sprinkler company. Upon completion, provide test results to the fire inspector.
15238 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES. COMPLY WITH CERTIFICATE OF OCCUPANCY AT ALL TIMES.
15239 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES AND KEEP UPDATED. TRAIN QUARTERLY.
15240 | Amount Due: $267.53
15241 | NoData
15242 | NoData
15243 | Exit Sign needed above doors.
15244 | NoData
15245 | Need to be tested and results placed into FMB.
15246 | Needs updated service tags.
15247 | Remove any obstruction during cooking service. Pull station shall not be block during cooking times.
15248 | Heavy accumulation of clutter must be removed and brought back to the approved load. Excess boxes and material shall be moved to a storage area away from the school.
15249 | General fuel shall not be stored inside storage area including used burned wood that is used for camp fire.
15250 | Remove any combustible material from electrical room.
15251 | Permits required
15252 | Access Gates Permit required.
15253 | Heavy accumulation of clutter must be removed and brought back to the approved load. Excess boxes and material shall be moved to a storage area away from the school.
15254 | All pathways leading to emergency exit doors shall never be obstructed by tables or book shelfs.
15255 | Dampers Tested every 4 yrs.
15256 | All exit doors need to open and close and latch on it's own without any assistants.
15257 | IFC2012.B1027.5, Describes the requirement for installation of panic hardware to the public way. If your area does not meet the requirements then you will have to install panic hardware on those gates.
15258 | Exit gate to public way.
15259 | Exit Gates to the public way need to have panic hardware install and shall never be chained or pad locked.
15260 | Any blinds installed on exit doors need to be removed.
15261 | NoData
15262 | NoData
15263 | The Fire Alarms are not powered. Continue self-initiated self-fire watch until all fire protection systems are in normal functioning condition.
15264 | NoData
15265 | NoData
15266 | NoData
15267 | NoData
15268 | Repair all doors that stick in their frames or that make contact with the floor.
15269 | Add one fire extinguisher to gym.
15270 | Document fire extinguisher and fire code training.1/12/2021 - OK
15271 | Remove all items stored in hallway that leads to riser room. Path to riser room must remain unobstructed at all times.
15272 | Provide copy of Emergency Operations Plan for inspector to review.
15273 | Ensure that all rooms have evacuation maps that show at least two routes from building.
15274 | Document obstructed fire drills.
15275 | Provide fire drill log for inspector to review.
15276 | Remove all curtains, drapes, fabrics, and combustible 3D decorations that do not have certificates of flame resistance.
15277 | Have 90 minute egress test performed and provide documentation that any deficiencies were corrected.Repair non-working exit signs.1/2021 - OK
15278 | Correct all violations within 60 calendar days.
15279 | Have hydrostatic test of FDC and internal inspection of piping system performed.
15280 | s1, f7 permits expired
15281 | NoData
15282 | Gaby ShaftelNO VIOLATIONS FOUND AT THIS TIME.
15283 | Five year test due for sprinkler riser.
15284 | Submit proof of annual damper testing.
15285 | NoData
15286 | NoData
15287 | NoData
15288 | Make all code violation corrections prior to the re-inspection date on page one. All corrections made. Audibility Test Passed 3/31/21
15289 | Provide current audibility test documentation within the last 3 years for the fire alarm system.Test documentation must have one of two things to be acceptable. A) Must show each audibility device’s ambient decibel level and the decibel level when the device is active. The difference in DB level must fall within NFPA 72’s acceptable range for the device to pass the test. OR B) A document from their company on company’s letter head that has the following information – 1) Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all audibility devices passed the audibility test as required by NFPA 72. All corrections made. Audibility Test Passed 3/31/21
15290 | NoData
15291 | Proper permanent post and sign need to be added facing the street.
15292 | Fail to comply with violations
15293 | Obtain a P2 Public Assembly permit for 10635 Homestead Rd #A.
15294 | Last inspected April/2021. No action needed at this time.
15295 | Is active and expires 4/21/2022
15296 | The owner/occupant is responsible for correcting all fire code violations prior to follow up inspection.
15297 | Remove all equipment that is powered by some kind of fuel. It cannot be store in any portion of the building.
15298 | Must maintain proper ceiling clearances.
15299 | Cannot block access to electrical panel and cannot place combustibles within specifications listed in the code.
15300 | Please place "THIS DOOR TO REMAIN UNLOCKED WHEN BUILDING IS OCCUPIED" somewhere on the door or door frame.
15301 | Provide proof of Natural Gas test in the last 5 years.
15302 | Check all units and ensure that the smoke detectors are in the required area.
15303 | Provide for current gas test or a gas test within the last 5 years.
15304 | Gates keys in the 911 boxes do not fit the locks on the gates.Corrected during Inspection
15305 | NoData
15306 | Have a licensed fire protection company perform an annual fire alarm inspection and correct any deficiencies.
15307 | Have a licensed fire protection company perform an annual inspection on the sprinkler system and correct any deficiencies.
15308 | NoData
15309 | Exit and entry signs on gates would be helpful.
15310 | Make sure all 911 emergency features work on all gates. All gates will be left open until all emergency features work properly.
15311 | NoData
15312 | NoData
15313 | Mr. Joseph Shum, of USA HomeMax Inc.,is designated the responsible party for abating the violations at 9400 Harwin Dr. Ste A
15314 | IFC 2012 FIRE CODE as adopted by the City of Houston defines High Piled storage as the following:HIGH-PILEDCOMBUSTIBLE STORAGE. Storage of combustible materials in closely packed pilesor combustible materials on pallets, in racks or on shelves where the top of storageis greater than 12 feet (3658 mm) in height. When required by the fire code official,high-piled combustible storage also includes certain high-hazardcommodities. such as rubber tires. Group A plastics. Flammable liquids, idlepallets and similar commodities, where the top of storage is greater than 6feet (1829 mm) in height.HIGH-PILEDSTORAGE AREA. An area within a building which isdesignated. intended, proposed or actually used for high-piled combustiblestorage.
15315 | 9400 Harwin Dr, Ste ACertificate of Occupancy dated 1/25/2007 (project number 5206287)80,000 square feet of retail storage; classified as an S1.High Piled storage has NOT been approved for this facility.An Owner's Statement of Intended Use has been requested multiple times and not produced. Attached to this notice is the statement that must be completed and returned within 7 calendar days.Storage over 12’ for ordinary combustibles and 6’ for high hazards is considered a change of use because it places the occupancy in a different division of the same S1 group or occupancy, as stated in the code above. Plan submittal with approvals and approved final onsite inspections are required prior to operating as High Piled.
15316 | FOR REFERENCEAs a High Piled storage facility, approved plans must be maintained on site for inspection.
15317 | Failure to abate the violations in the designated timeindicated on this report will result in the following: Re-Inspection Fee assessed after failure tolower commodity to the approved height in 7 calendar days. 2.Re-Inspection Fee and Citation assessed afterfailure to lower commodity to the approved height in 14 calendar days (7calendar days will be added to the initial re-inspection fee3.Reinspection Fee and Citations will be issuedevery 7 calendar days for failure to abate the violations
15318 | This building does not currently have a Certificate ofOccupancy designated high piled, a sprinkler system installed, detection, ornotification. Any storage over 12’ or 6’ respectively poses an unsafe conditionas defined by code in this notice. 500 square feet of high piled storage is allowed until allof the following have been completed:1. 1. Plans submitted to Commercial Plan Review for achange of use to HIGH PILED STORAGE2. 2.Such plans are approved without rejection by allrespective plan review teams3. 3.Construction is completed according to theapproved plans 4. 4.FINAL ONSITE INSPECTION is completed andapproved by the High Piled plan review teamUntil all of the above are completed ALL COMMODITY is to be restoredto the originally approved height of 12’ for ordinary combustibles and 6’ forHigh HazardsCompliance within 7 calendar days
15319 | Commodity must be stored at 12' and 6' as required by code to abate the unsafe condition that currently exists until all plans are approved and final onsite inspections are completed.
15320 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES. COMPLY WITH CERTIFICATE OF OCCUPANCY AT ALL TIMES.
15321 | Renew Public Assembly Permit within 10 Business Days
15322 | NoData
15323 | NoData
15324 | NoData
15325 | NoData
15326 | NoData
15327 | NoData
15328 | NoData
15329 | NoData
15330 | NoData
15331 | NoData
15332 | NoData
15333 | NoData
15334 | NoData
15335 | NoData
15336 | NoData
15337 | Permit Expired 2/6/2021; Unpaid $267.53
15338 | NoData
15339 | NoData
15340 | NoData
15341 | C1 permit is expired. Expired on 3/1/2021. Amount owed 178.34 Please pay for permit within 10 days of this notice. If more information is needed about permit contact the Fire Prevention Permit Office.
15342 | HAVE RED TAGGED REPAIRED AND REMOVED WITHIN 7 BUSINESS DAYS.
15343 | NoData
15344 | NoData
15345 | Obtain a P2 Public Assembly permit for 10635 Homestead Rd #A.
15346 | EXPIRED PERMIT RENEWAL REQUIRED K1
15347 | Please renew the K1, key box permit. Expired 3/31/21.Please renew the A4, access gate permit. Expired 5/30/2019.
15348 | last annual 1/2019
15349 | re-inspection fee issued for noncompliance of inspection report
15350 | last semi-annual 12/2018
15351 | NoData
15352 | NoData
15353 | NoData
15354 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES. COMPLY WITH CERTIFICATE OF OCCUPANCY AT ALL TIMES.
15355 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES AND KEEP UPDATED. TRAIN QUARTERLY.
15356 | Numbers must be in color contrast of background
15357 | Maintain readily available records
15358 | Maintain readily available records
15359 | Fire Alarm Permit expired
15360 | CORRECT YELLOW TAG ON SPRINKLER SYSTEM.
15361 | re-inspection fee for yellow tagged alarm system
15362 | correct yellow tagged fire alarm system
15363 | NoData
15364 | NoData
15365 | NoData
15366 | NoData
15367 | NoData
15368 | NoData
15369 | NoData
15370 | NoData
15371 | NoData
15372 | The kitchen hood suppression system was red tagged on 11/24/2020 for multiple impairments. Repairs shall be initiated within 72 hours to complete all required corrections in order to bring the system into a fully operational status. Confirmation of initiation must be relayed to the inspector within 72 hours.
15373 | The required annual P2: Public Assembly permit expired 3/13/2021. Utilize the attached permit renewal notice and instructions to make payment.
15374 | All extinguishers on site require an annual inspection/test from a certified fire protection company. Ensure that new inspection tags are placed after the inspection. (the last annual inspection tag was January 2019)
15375 | The "K" type (silver) extinguisher in the kitchen must be mounted where it is easily visible and readily accessible. (At the time of inspection it was found to be on a low shelf behind items)
15376 | Ensure that ALL marked exits are unlocked while the building is occupied, and free of any storage at all times. (The secondary main doors were unlocked while inspector was on site and a warning was issued. Any future occurrence will result in an immediate citation)
15377 | have the annual inspection/test performed on the k type extinguisher in the kitchen. Ensure that a new annual inspection tag is placed.
15378 | Test and Repair/Replace as needed all exit signs to ensure they are illuminated at all times and remain illuminated when the test button is pressed. (specifically noted was the rear exit and main front exit as needing repair)
15379 | NoData
15380 | NoData
15381 | NoData
15382 | NoData
15383 | NoData
15384 | NoData
15385 | NoData
15386 | NoData
15387 | NoData
15388 | K1, P2, C1 permits are expired. Expired on 11/12/2020. Amount owed 859.67 Please pay for permits within 10 days of this notice. If more information is needed about permits contact the Fire Prevention Permit Office.
15389 | NoData
15390 | Have a licensed fire protection company service and tag the fire extinguishers.
15391 | Mount the fire extinguisher in the shop area.
15392 | The fork lift is required to have a fire extinguisher with a minimum rating of 10BC.
15393 | Provide an exit sign for the emergency exit in the shop area that is either internally or externally illuminated. Internally illuminated exit signs are required to be listed and labeled in accordance with UL924.
15394 | Remove the LPG cylinder from within the building and store it outside in a protected enclosure.
15395 | Repair or replace the inoperable emergency illumination on the exit sign located in the office area.
15396 | NoData
15397 | Failed to correct all violation on compliance date>
15398 | Emergency lights must be tested yearly. Documentation must be added into the FMB of last test date.
15399 | It's the owner/management to maintain all required inspections and permits up to date.
15400 | Fire alarm audibility testing must be done every 3 yrs. and alarm panel tagged showing last date. Copy of results entered into FMB
15401 | All emergency lights need to be tested once a yr and results entered into the FMB.
15402 | Damper testing must be done every 4 yrs. and placed into the FMB
15403 | All fire extinguisher must be tested once a yr. and tagged with current date.
15404 | An access gate key box must be install for apparatus access.
15405 | All fire rated exit doors must open and return to the closed position without any assistance. Proper swing arms need to be installed and if necessary doors adjusted.
15406 | All class rooms need updated evacuation routes per example given.
15407 | Smoke detector testing must be done and results placed into the FMB and Alarm Panel tagged.
15408 | Access Gate permit needed.
15409 | Exterior gates in play ground/court yard must open in the direction of travel and never to be lock or chained. Access to public way must be maintain and made available for the occupancy of the building.
15410 | At no time can exit doors leading to public way be chained and pad locked.
15411 | Exit signs with emergency lights must be installed above all emergency exit doors.
15412 | K-1 permit needed.
15413 | All class room emergency exit doors must have panic hardware UL approved.In addition all exterior gates to the public way and leading to the public way must open in the direction of travel and have panic hardware installed. UL approved.
15414 | All updated permits and certificate of occupancy must be placed inside binder.
15415 | Large tree needs to be removed or maintained so that the exit door opens the required clear width.
15416 | All exterior doors exit pathway of egress, must be kept clear of obstruction and hazards. All debris obstructing the path of travel to the public way must be removed.Example. falling broken fence, wood pickets, grocery cart and any other large obstacles along the path.
15417 | NoData
15418 | NoData
15419 | NoData
15420 | NoData
15421 | NoData
15422 | NoData
15423 | NoData
15424 | NoData
15425 | NoData
15426 | NoData
15427 | NoData
15428 | NoData
15429 | NoData
15430 | NoData
15431 | NoData
15432 | NoData
15433 | NoData
15434 | NoData
15435 | NoData
15436 | NoData
15437 | NoData
15438 | NoData
15439 | NoData
15440 | NoData
15441 | NoData
15442 | NoData
15443 | NoData
15444 | NoData
15445 | NoData
15446 | NoData
15447 | NoData
15448 | NoData
15449 | NoData
15450 | NoData
15451 | NoData
15452 | NoData
15453 | NoData
15454 | NoData
15455 | NoData
15456 | NoData
15457 | NoData
15458 | NoData
15459 | NoData
15460 | NoData
15461 | NoData
15462 | NoData
15463 | NoData
15464 | NoData
15465 | NoData
15466 | NoData
15467 | NoData
15468 | NoData
15469 | NoData
15470 | NoData
15471 | NoData
15472 | NoData
15473 | NoData
15474 | NoData
15475 | NoData
15476 | The restricted re-entry system is not working. Either repair system so re-entry doors can be unlocked from a remote location or unlock the re-entry doors per code.
15477 | Add 911 key box per code.
15478 | Update mobility impaired every 6 months. Update emergency contacts.
15479 | Key for fire phone box is not working. Add swipe cards to key rings per code.
15480 | Add 1 elevator hoist way key making a total of 2 in the fire depository box per code.
15481 | Add 1 Independent service key making a total of 2. Place either in FCC outside fire depository box or at security desk per code.
15482 | Label the garage elevator room per code.
15483 | Add cover plate to junction box in FCC per code.
15484 | Go through all electrical and telecom rooms and return them to their designed fire resistance rating per code.
15485 | Correct the above fire doors so they close and latch from the open position per code.
15486 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriateinspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualEmergency radio coverage- AnnualFire Extinguishers- AnnualDry pipe partial- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualDry pipe full- 3 YearFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearClean agent – Semi-annualKitchen Hood System- Semi-annualBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
15487 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. • Present Permits that apply to facility Address listed • on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS.
15488 | Correct egress lighting per code.
15489 | NoData
15490 | Permit has expired and requires renewing.
15491 | Provide documentation/report for 3 year audibility testing and any necessary repairs.
15492 | Provide documentation/report for 90 min emergency light testing and any necessary repairs.
15493 | Provide documentation/report for fire damper testing and any necessary repairs.
15494 | Address Numbers shall constrast with their background. Provide Address Numbers as to be visible from the street or road.
15495 | NoData
15496 | NoData
15497 | NoData
15498 | NoData
15499 | Internally illuminated exit signs are required to be UL924 compliant.
15500 | Proper ventilation is required.
15501 | Ensure exits are clear of obstructions.
15502 | Limited spraying spaces shall comply with sections 2404.9.1 through 2404.9.4 or spray booth will need to be brought up to code.
15503 | Limited spraying spaces shall comply with sections 2404.9.1 through 2404.9.4 or spray booth will need to be brought up to code.
15504 | Limited spraying spaces shall comply with sections 2404.9.1 through 2404.9.4 or spray booth will need to be brought up to code.
15505 | Limited spraying spaces shall comply with sections 2404.9.1 through 2404.9.4 or spray booth will need to be brought up to code.
15506 | Limited spraying spaces shall comply with sections 2404.9.1 through 2404.9.4 or spray booth will need to be brought up to code.
15507 | Ensure exits are unlocked while the building is occupied.
15508 | Internally illuminated exit signs are required to be UL924 compliant.
15509 | NoData
15510 | NoData
15511 | NoData
15512 | NoData
15513 | NoData
15514 | NoData
15515 | NoData
15516 | NoData
15517 | NoData
15518 | NoData
15519 | NoData
15520 | NoData
15521 | NoData
15522 | NoData
15523 | NoData
15524 | 6/2019 - Have all portable fire extinguishers inspected.3/2021 - OK
15525 | Relocate propane cage that is currently placed in exit pathway outside welding class.
15526 | Conduct and document required annual fire safety training.8/2020 - OK
15527 | Remove all items blocking access to fire alarm panel in IT room.
15528 | 5/16/2019 - OK
15529 | Provide updated EOP for 20-21 school year.
15530 | Provide documentation of sensitivity report performed within the past five years and provide documentation that any deficiencies were corrected.12/24/2020 - Passed, OK
15531 | Expired 3/31/2020 - Renew elevator permit.Expires 3/31/2021 - OK
15532 | Pay reinspection fee within 10 calendar days.
15533 | 2/4/2015 - Have 5 year hydrostatic test and internal inspection performed, and provide documentation that deficiencies were corrected.New school 2018 - Not due until 2023
15534 | Have dampers tested, provide report, and provide documentation that deficiencies were corrected.New school 2018. Not needed until 2022.
15535 | Correct all violations within 60 calendar days.
15536 | 7/2/2019 - Have sprinkler system inspected and have any deficiencies corrected.
15537 | Boilers have never been registered with TDLR. Register boilers, have them inspected, and provide boiler certificates.
15538 | Have egress lighting tested and provide documentation that deficiencies were corrected.
15539 | Correct all violations within 60 calendar days.
15540 | Have hydrostatic test of FDC and internal inspection of piping system performed.3/28/2019 - OK
15541 | NoData
15542 | Have the existing fire extinguisher inspected by a Licensed Fire Suppression Company and a have a current tag affixed to the extinguisher.
15543 | Owner/Occupant is responsible for Obtaining Certificate of Occupancy, correcting all fire code violations, and purchasing necessary permits listed in this report. Apply for Occupancy by sending the building department the address needing Occupancy(1570 Telephone Rd) at this email address: occupancy.inspections@houstontx.gov
15544 | Must purchase the Flammable/Combustible Liquid Storage and Use permit at the City of Houston Permitting Center. 1002 Washington Avenue. 2nd Floor
15545 | Must obtain and purchase F7 permit for the 300 gallon waste oil tank in the rear of the business.
15546 | NoData
15547 | Amount due: $267.53
15548 | All fire extinguishers must be mounted.
15549 | Place fire extinguishers in a visible location.
15550 | Fire extinguishers must be minimum rating of 2A10BC
15551 | Place fire extinguisher with a minimum rating of 2A 10BC
15552 | Remove structure blocking emergency exit.
15553 | NoData
15554 | Cover all exposed wires and replace missing junction covers.
15555 | Apply for certificate of occupancy.
15556 | Inspect and Service tag commercial kitchen hood system. Correct all red tag impairments immediately.
15557 | 5/2019 - Have all portable fire extinguishers inspected.3/2021 - OK
15558 | 5/2020 - Have ANSUL system inspected.3/2021 - OK
15559 | Conduct and document required annual fire safety training.8/2021
15560 | 6/17/2019 - OK
15561 | Pay reinspection fee within 10 calendar days.
15562 | Correct all violations within 60 calendar days.
15563 | 7/11/2019 - Have sprinkler system inspected and have deficiencies corrected.
15564 | Original FDC sign faded and illegible. This violation was listed on the last inspection report for this school, but was never corrected. Have new sign made and attached to building. Sign MUST include which portions of the building are served by the main (original) FDC.Recently added portion of building has its own FDC. Install sign that indicates which portions of building are served by new FDC (west end of building).
15565 | Place "Roof Access" sign on door to room 408. Sign must be PERMANENT.
15566 | 2/6/2020 - Multiple fails with not documentation of corrected.Have new egress lighting test performed and provide documentation that deficiencies were corrected.
15567 | Install panic hardware on all courtyard gates.
15568 | Immediately remove chains and padlocks from gates leading from BOTH courtyards.Prohibit future use of chains and padlocks on gates.Install panic hardware on all courtyard gates.
15569 | NoData
15570 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
15571 | NoData
15572 | NoData
15573 | Please renew the K1, key box permit which expired 6/7/2020.
15574 | Please renew the K1, key box permit. Expired 6/7/2020.
15575 | NoData
15576 | Compliance: 30 calendar days.
15577 | NoData
15578 | ITS THE OWNER/AGENT RESPONSIBILITY TO ABATE AND CORRECT ALL LIFE SAFETY AND CODE VIOLATIONS AT ALL TIMES. COMPLY WITH CERTIFICATE OF OCCUPANCY AT ALL TIMES.
15579 | KEEP EMERGENCY EVACUATION PLANS ON PROPERTY AT ALL TIMES AND KEEP UPDATED. TRAIN QUARTERLY.
15580 | Remove accumulation of dust.
15581 | Place fire extinguishers with a rating of 4A 40B.C
15582 | Apply for a certificate of occupancy at 1002 Washington ave. Telephone # 832-394-8880.
15583 | NoData
15584 | NoData
15585 | NoData
15586 | NoData
15587 | Amount Due: $653.97
15588 | The business shall go through the process of completing the automatic fire sprinkler system and ensuring it has been approved and in working order.
15589 | The installation of the fire alarm system is to be completed. The business shall submit plans for their fire alarm system for approval through the building department. The business shall also provide a plan of action including dates of plan submittal, installation, and final completion to the fire code official. The plan of action may be revised as necessary.
15590 | The business shall obtain a Certificate of Occupancy by application through the Building Department.
15591 | The building is not to be occupied or open to the public without a fire watch from HFD inspectors per the Fire Marshal. After plan submittal, installation, and an approved fire alarm system is in working order, the fire watch may be discontinued. At NO time shall the basement level of the building be occupied (even with fire watch) until the building has an approved fire alarm system, approved automatic fire sprinkler system, and the building has been issued a Certificate of Occupancy.
15592 | Mount all fire extinguishers
15593 | Use fire extinguisher with a minimum rating of 2A 10 BC
15594 | Replace all missing electrical cover plate.
15595 | NoData
15596 | NEED TO BE SERVICE 5-18 LAST DATE
15597 | NEED SERVICE 3-19 LAST DATE
15598 | NoData
15599 | NEED TO BE SERVICE, HAS A TROUBLE SIGNAL ON. LAST DATE 6-11-20. FIX ALL TAGS
15600 | NEED TO BE SERVICE. LAST DATE 3-19
15601 | FAILURE TO GET THE SPRINKLER SYSTEM SERVICE AND FIRE PANEL HAS TROUBLE LIGHT ON
15602 | NoData
15603 | NoData
15604 | NoData
15605 | NoData
15606 | NoData
15607 | PERMIT HAS EXPIRED AND REQUIRES RENEWING.
15608 | Have a licensed plumber perform a 5 year gas test. The plumber is required to obtain a gas test permit.
15609 | Ensure the side exit is unlocked while the building is occupied. Repair the hardware if necessary.
15610 | PROVIDE EXIT SIGNS -SERVING ENTRY (BACK EXIT DOOR)
15611 | ALL TWO WAY COMMUNICATION NOT IN OPERATIVE CONDITION SHALL BE REMOVED. -PHONES AND PUSH BUTTONS
15612 | CURRENT INFORMATION -FPS FIRE ALARM SYSTEM ANNUAL INSPECTION DATE: 7/3/2019 ACCEPTABLE BLUE TAG SPRINKLER SYSTEM INSPECTION DATE: N/A ANNUAL FIRE EXTINGUISHER INSPECTION DATE: 6/2019 ANSUL SYSTEM BI-ANNUAL INSPECTION DATE: 12/2018 EXPIRED
15613 | PROVIDE REPORT OF TEST RESULTS IF DECORATIVE MATERIALS ARE TO MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701. CERTIFICATE OF FLAME RESISTANCE SHALL INDICATE THE COLOR AND/OR NUMBER FOR ALL DECORATIVE MATERIALS THROUGHOUT SCHOOL. -STAGE (BROWN AND BEIGE)
15614 | DOORS INTO ELECTRICAL CONTROL PANEL ROOMS SHALL BE MARKED WITH A PLAINLY VISIBLE AND LEGIBLE SIGN STATING 'ELECTRICAL ROOM' OR SIMILAR APPROVED WORDING. LABEL "ELECTRICAL ROOM" -621 MECHANICAL OUTSIDE (ROOM INSIDE TO RIGHT)
15615 | REMINDER: EXTENSION CORDS AND FLEXIBLE CORDS SHALL NOT BE A SUBSTITUTE FOR PERMANENT WIRING. EXTENSION CORDS SHALL BE USED ONLY WITH PORTABLE APPLIANCES. -CUSTODIAL ROOM Note: All extension cords and approved multi-plug adapters are to be Underwriters Laboratories (UL) listed or Factory Mutual (FM) approved items.
15616 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL OF THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY 3 YEARS. LAST AUDIBILITY TEST DATED: UNKNOWN PROVIDE WRITTEN DOCUMENTATION OF AUDIBILITY TESTING AND ANY DOCUMENTATION REGARDING REPAIRS OF ANY FAILURES
15617 | ALL VENT HOOD FIRE SUPPRESSION SYSTEMS INSTALLED IN COMMERCIAL KITCHENS SHALL BE INSPECTED AND SERVICE TAGGED NOT LESS THAN EVERY 6 MONTHS, AND AFTER ANY ACTIVATION OF THE SYSTEM, BY AN APPROVED FIRE PROTECTION EQUIPMENT COMPANY. ANSUL SYSTEM INSPECTION DATE (BI-ANNUALLY): DECEMBER 2018 EXPIRED PROVIDE BIANNUAL INSPECTION AND SERVICE TAG OF ALL VENT HOOD FIRE SUPPRESSION SYSTEMS
15618 | REPAINT THE FIRE LANE- RED
15619 | REPAIR/REPLACE CEILING TILES -230 MECHANICAL -621 MECHANICAL (ELECTRICAL ROOM ON RIGHT INSIDE)
15620 | REMINDER: ALL CURTAINS, DRAPERIES, HANGINGS AND OTHER DECORATIVE MATERIALS SHALL MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701 OR BE NONCOMBUSTIBLE. PROVIDE CERTIFICATE OF FLAME RESISTANCE (SEE FIRE CODE BELOW, 807.2) OR REMOVE ALL THAT DO NOT MEET THE CRITERIA.
15621 | AN APPROVED LICENSED MASTER ELECTRICIAN OR LICENSED ELECTRICAL SERVICE COMPANY SHALL TEST ALL EMERGENCY LIGHTING SYSTEMS ANNUALLY. LAST TEST DATE: UNKNOWN PROVIDE WRITTEN DOCUMENTATION OF TESTING AND RESULTS. ANY FAILURES OF THE EMERGENCY LIGHTING SYSTEM SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
15622 | BOILER CERTIFICATE OF OPERATIONS SHALL BE MAINTAINED ON PREMISES. PROVIDE CERTIFICATE FOR # 163928
15623 | IDENTIFIED ELECTRICAL HAZARDS SHALL BE ABATED. -HANGING WIRES, MECHANICAL 317
15624 | ADDRESS NUMBERS SHALL CONTRAST WITH THEIR BACKGROUND. CORRECT ADDRESS NUMBERS AS TO BE VISIBLE FROM THE STREET OR ROAD FRONTING THE PROPERTY
15625 | MAINTAIN ADEQUATE CLEARANCE TO ALL ELECTRICAL SERVICE EQUIPMENT AT ALL TIMES. MARK THE NECESSARY ELECTRICAL CLEARANCE -Room 358 -STORAGE SCIENCE ROOM 219, 306, elsewhere if needed
15626 | THE REQUIRED FIRE-RESISTANCE RATING OF FIRE-RESISTANCE-RATED CONSTRUCTION SHALL BE MAINTAINED. REPLACE MISSING/DAMAGED CEILING TILES -265 SPRINKLER ROOM
15627 | AN APPROVED HVAC COMPANY SHALL CONDUCT A FULL-FUNCTION TEST AND MAINTENANCE ON ALL FIRE DAMPERS AT LEAST EVERY 4 YEARS. PROVIDE DOCUMENTATION/REPORT FOR TESTING AND ALL NECESSARY REPAIRS.
15628 | PROVIDE SIGNAGE "SPRINKLER RISER" ON/BY BOTH INSIDE AND OUTSIDE DOORS WHERE THE SPRINKLER RISER IS LOCATED. -OUTSIDE ROOM -OUTSIDE ROOM BY GYM (BOTH DOORS)
15629 | CURRENT INFORMATION -FPS FIRE ALARM SYSTEM ANNUAL INSPECTION DATE: 7/13/2019 ACCEPTABLE BLUE TAG SPRINKLER SYSTEM INSPECTION DATE: 3/13/2019 ACCEPTABLE BLUE TAG (3) ANNUAL FIRE EXTINGUISHER INSPECTION DATE: 6/2019 ANSUL SYSTEM BI-ANNUAL INSPECTION DATE:7/2019
15630 | DOORS INTO ELECTRICAL CONTROL PANEL ROOMS SHALL BE MARKED WITH A PLAINLY VISIBLE AND LEGIBLE SIGN STATING 'ELECTRICAL ROOM' OR SIMILAR APPROVED WORDING. LABEL "ELECTRICAL/MECHANICAL ROOM" -OUTSIDE ROOM -ROOM 151 -STORAGE SCIENCE ROOM 219, 306
15631 | Multi-plug adapters (Surge protectors) are to be plugged directly into an electrical outlet. Extension cords and/or multi-plug adapts are not to be used in conjunction with other multi-plug adapters. -Room 360 (electrical floor outlet not working) Note: All extension cords and approved multi-plug adapters are to be Underwriters Laboratories (UL) listed or Factory Mutual (FM) approved items.
15632 | AN APPROVED LICENSED MASTER ELECTRICIAN OR LICENSED ELECTRICAL SERVICE COMPANY SHALL TEST ALL EMERGENCY LIGHTING SYSTEMS ANNUALLY. LAST TEST DATE: UNKNOWN PROVIDE WRITTEN DOCUMENTATION/REPORT OF TESTING AND RESULTS. ANY FAILURES OF THE EMERGENCY LIGHTING SYSTEM SHALL BE REPAIRED OR REPLACED AS SOON AS POSSIBLE.
15633 | REPAINT FIRE LANE THROUGHOUT SCHOOL
15634 | PROVIDE GAS TEST PERMIT CONDUCTED BY A LICENSED PLUMBER OR APPROVED GAS EQUIPMENT SERVICE COMPANY. GAS TEST PERMIT AND FINAL APPROVAL FORM SHALL BE OBTAINED FROM THE PLUMBER OR SERVICE COMPANY AND MAINTAINED ON THE PREMISES.
15635 | A LICENSED FIRE ALARM SERVICE COMPANY SHALL DO TEST OF ALL OF THE FIRE ALARM SYSTEM ANNUNCIATOR DEVICES NOT LESS THAN EVERY 3 YEARS. LAST AUDIBILITY TEST DATED: UNKNOWN PROVIDE WRITTEN DOCUMENTATION/REPORT OF AUDIBILITY TESTING AND ANY DOCUMENTATION REGARDING REPAIRS OF ANY FAILURES
15636 | A LICENSED SERVICE COMPANY SHALL CONDUCT HYDROSTATIC AND FLOW TESTS ON ALL FIRE DEPARTMENT CONNECTIONS EVERY 5 YEARS IN CONJUNCTION WITH THE STANDPIPE SYSTEM 5-YEAR TEST. PROVIDE DOCUMENTATION/REPORT AND BLUE TAG OF THE 5-YEAR TEST ON THE FIRE DEPARTMENT CONNECTION
15637 | PROVIDE REPORT OF TEST RESULTS IF DECORATIVE MATERIALS ARE TO MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701. CERTIFICATE OF FLAME RESISTANCE SHALL INDICATE THE COLOR AND/OR NUMBER FOR ALL DECORATIVE MATERIALS THROUGHOUT SCHOOL. -OLDER BLACK CURTAINS ON STAGE (NOTE:NEW BLACK CURTAINS UP TO DATE 7/19/2018)
15638 | REMINDER: ALL CURTAINS, DRAPERIES, HANGINGS AND OTHER DECORATIVE MATERIALS SHALL MEET THE FLAME PROPAGATION PERFORMANCE CRITERIA OF NFPA 701 OR BE NONCOMBUSTIBLE. PROVIDE CERTIFICATE OF FLAME RESISTANCE (SEE FIRE CODE BELOW, 807.2) OR REMOVE ALL THAT DO NOT MEET THE CRITERIA.
15639 | ALL EXIT SIGNS SHALL BE ILLUMINATED AT ALL TIMES. REPAIR EXIT SIGNS. -STAGE
15640 | PROVIDE PORTABLE FIRE EXTINGUISHER -LIBRARY 154
15641 | NoData
15642 | Copies of floor plans were missing out of Depository Box during inspection. Post inspection the plans have been added with picture attach to record.
15643 | 5 yr Pressure Gas Test is due
15644 | Need annual inspection performed on fire alarm system. Correct any issues if found.
15645 | Fire sprinkler system needs annual inspection. Correct any issues if found.
15646 | Need these signs on both gates to property. HFD on top and number of hydrants inside property on bottom. Read above code on size of sign and lettering.
15647 | Show copy of current access gate permit.
15648 | Show copy of current key box permit.
15649 | Show current copy of fire alarm permit.
15650 | Have fire hydrants tested by your fire sprinkler co. Show proof of test.
15651 | NoData
15652 | NoData
15653 | Provide a current annual fire alarm system test and current blue tag on the fire alarm panel.
15654 | Annual inspection tag is missing on the fire extinguisher located in the elevator room
15655 | Make all code violation corrections prior to the reinspection date noted on page 1 of the report. All buildings shall be maintained to their code standards as designated on their Certificate of Occupancy or designated as a vacant premises and safeguarded as such.
15656 | Verify that the existing elevator is equipped with emergency operation in accordance with ASME A17.3
15657 | Provide current audibility test documentation within the last 3 years for the fire alarm system.Test documentation must have one of two things to be acceptable. A) Must show each audibility device’s ambient decibel level and the decibel level when the device is active. The difference in DB level must fall within NFPA 72’s acceptable range for the device to pass the test. OR B) A document from their company on company’s letter head that has the following information – 1) Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all audibility devices passed the audibility test as required by NFPA 72. The Documentation should also contain the Company’s ACR#, the Tester’s certification #, and the date the test was performed.
15658 | Provide documentation for a current emergency egress light annual test.An approved licensed master electrician or licensed electrical service company shall test all emergency lighting systems annually. The battery units, whether of the acid or alkali type, shall be tested continuously for a minimum of 90 minutes.Failed devices shall be repaired or replaced as soon as possible. The test report / documentation shall have the date of the test, the master electrician, and/or company's certification number, and state that all devices passed the 90-minute test or if there were failed devices needing corrections. Provided device corrections report for the current egress light test dated
15659 | All key boxes / Knox boxes shall have the following items to be placed inside gate access keys (where applicable), a master key or all keys necessary to access to the main fire alarm panel, and small site map showing the location of the fire alarm panel, riser room, and / or elevator room (where these rooms exist).If a master key is not provided, a key or keys needed to access to the main fire alarm panel (or sub-panel if applicable) need to be placed in the 911 Key Box or Knox box. The occupant shall provide a Falcon padlock or Knox padlock for 911 key boxes. All key box items shall be provided for the inspecting fire code official tobe placed in the 911 Key box or Knox box at the time of re-inspection or before.The key box located at the main entrance needs: - A master key or all keys necessary to access to the main fire alarm panel- A small site map showing the location of the fire alarm paneland elevator room, and roof access points. The key box located on the exterior driveway entrance on the right side of the building needs are dependent on whether the occupant keeps the motorized gate or switched to a manual gate:- With motor: key box wired to motor controller with additional fail safe box padlock keys- No motor: keys for any padlocksMotorized access gates must also have permitted access gate plans and an access gate permit.
15660 | Put a durable sign on the Elevator Room door:Elevator Room
15661 | Make sure this sign is posted.
15662 | Replace ceiling tiles throughout where needed.
15663 | Evacuation Maps shall be posted in all areas normally occupied by students.The evacuation map should show: 1. You are Here 2. Primary evacuation route 3. Secondary evacuation route.The evacuation routes should be in two separate, distinguishable, and highly visible colors.The map should show a legend.Each Room shall have its own individual map.Review all rooms normally occupied by students and ensure that they have a correct map posted.
15664 | Students were occupying partial areas of the buildings of the Joplin Campus. Provide fire drill logs monthly.
15665 | Any curtains or decorative materials shall meet the NFPA 701 Flame Propagation Standard and have documentation.
15666 | If the system is an addressable / Intelligent system - provide the digital diagnostic reading showing the detectors status. If the system is conventional - test each device with synthetic smoke and provide documentation. The documentation is required to show: 1)Test date 2) Company’s ACR# 3) Tester’s FAL# 4) A statement that all smoke detector devices passed the sensitivity test as required by NFPA 72.
15667 | Provide documentation for all boilers that show to be active on the Texas Department of Licensing and Registration. All active boilers shall have a current Texas Certificate of Operation:201741 (Steam Master) - expired 8/5/19263522 (Raypak) - expired 4/12/18273617 (Raypak) - expired 12/20/19270033 (A.O. Smith) - all are current -exp. 2/1/21270034 (A.O. Smith)270035 (A.O. Smith)270036 (A.O. Smith)270037 (A.O. Smith)270038 (A.O. Smith)
15668 | Provide a current Elevator Permit. Documents for the Annual and Monthly tests shall be kept in the Fire Marshal's Binder.
15669 | The existing permits and Certificates of Occupancy show to be for the prior occupant. Provide Certificates of Occupancy Permits for all buildings on location designated as The Joplin School / St. Thomas / etc., not Harvard School of Law and Justice (Houston Independent School District). Obtain permits required:- Key Box K1- Assembly P2- Fire Alarm Permit shall be current
15670 | Ensure that all roof access doors on top of the roof and leading to the roof are readily operational and do not stick or are hard to open. All hardware shall be operational and meet code requirements, readily openable from the egress side without the use of a key or special knowledge or effort. The unlatching shall also require only one motion. Repair the door roof access West Stair / 3rd Floor / Building A, and all other doors where needed.
15671 | Doors designated as opening protectives in corridors / classrooms / are fire rated doors and should remain closed in non-sprinkled buildings. No door stops are allowed.
15672 | The existing permits and Certificates of Occupancy show to be for the prior occupant. Provide Certificates of Occupancy Permits for all buildings on location designated as The Joplin School / St. Thomas / etc., not Harvard School of Law and Justice (Houston Independent School District). Obtain permits required:- Key Box K1- Assembly P2- Fire Alarm Permit shall be current
15673 | All interior doors leading to roof access shall have a sign "Roof Access" meeting the code requirements.
15674 | The existing permits and Certificates of Occupancy show to be for the prior occupant. Provide Certificates of Occupancy Permits for all buildings on location designated as The Joplin School / St. Thomas / etc., not Harvard School of Law and Justice (Houston Independent School District). Obtain permits required:- Key Box K1- Assembly P2- Fire Alarm Permit shall be current
15675 | The existing permits and Certificates of Occupancy show to be for the prior occupant. Provide Certificates of Occupancy Permits for all buildings on location designated as The Joplin School / St. Thomas / etc., not Harvard School of Law and Justice (Houston Independent School District). Building designations on the Certificates of Occupancy must match the identification placard / stencil on each building.
15676 | Make sure occupant load signs are posted in all spaces that accommodate more than 50 people.
15677 | Ensure that all roof access doors on top of the roof and leading to the roof are readily operational and do not stick or are hard to open. All hardware shall be operational and meet code requirements, readily openable from the egress side without the use of a key or special knowledge or effort. The unlatching shall also require only one motion.
15678 | All interior doors leading to roof access shall have a sign "Roof Access" meeting the code requirements.
15679 | NoData
15680 | NoData
15681 | NO VIOLATIONS FOUND AT THIS TIME
15682 | NoData
15683 | NoData
15684 | Have the required annual inspection/testing performed by a certified fire protection company on both extinguishers, ensuring that new hang tags are placed. (Date on tags noted as 09/2018)
15685 | NoData
15686 | Repair or replace emergency light.Compliance: 30 calendar days.
15687 | NoData
15688 | NoData
15689 | NoData
15690 | NoData
15691 | Remount or replace missing extinguishers
15692 | 2nd floor, east side (sublet area) - move 2 extinguishes to outer aisles to provide spacing.
15693 | Aisles in warehouse must remain clear. Access to east end of warehouse blocked on S main aisle.
15694 | NoData
15695 | Yellow tags on risers missing 5 year hydro tests. Red tags must be corrected.
15696 | Red tag on fire alarm must be corrected. Mag locks tested annually unless removed, See 901.6
15697 | Please provide 5 yr hydro test of sprinkler system and have annual test performed
15698 | Please provide current audibility test for fire alarm
15699 | Please provide report of testing emergency lighting
15700 | Please provide current sprinkler hydro test
15701 | Please provide current hydro test for FDC
15702 | Fire pump requires annual test
15703 | Storage tank requires 5 year inspection and flow test
15704 | Please provide report of fire door test, required annually
15705 | HIGH-PILED COMBUSTIBLE STORAGE. Storage of combustible materials in closely packed piles or combustible materials on pallets, in racks or on shelves where the top of storage is greater than 12 feet (3658 mm) in height. When required by the fire code official, high-piled combustible storage also includes certain high-hazard commodities, such as rubber tires, Group A plastics, flammable liquids, idle pallets and similar commodities, where the top of storage is greater than 6 feet (1829 mm) in height.
15706 | Must provide protection of combustibles during hot works operation
15707 | Compressed gas cylinder must be secured
15708 | 3-way plugs NOT ALLOWED. Remove all multi-plug adapters.
15709 | Allowed power supplies must be directly connected to receptacle. NO DAISY CHAINING OF POWER SUPPLIES.
15710 | REMOVE all extension cords being used as permanent power sources. Extension cords plugged into power supplies also NOT ALLOWED.
15711 | Extension cords must be plugged into approved power source. (receptacle)
15712 | Please replace all ceiling tiles in office space area and correct missing drywall in NW area of warehouse
15713 | Remove Mag locks if not used
15714 | Extinguishers need to be visible and accessible.
15715 | Please provide a current sensitivity test for smoke detectors.
15716 | Aisles must be maintained for egress
15717 | Exit signs distances must not be greater than 100'
15718 | Electrical panels must have 36 in clearance.
15719 | Please obtain and post a valid C/O (Certificate of Occupancy)
15720 | H3 permits (hot works) required for welding & cutting operations. Area of operation must have combustibles protected per IFC 3504.1.1
15721 | Rack storage needs to be anchored to the floor. 12 foot height markings required to be clearly visible on racks if not applying for High-Pile storage
15722 | LP permit required for amount stored
15723 | Double keyed deadbolts on egress doors not allowed
15724 | All exit signs must be functional. Please fix broken and damaged exit signs.
15725 | Remove unused mag lock hardware from door.
15726 | NoData
15727 | NoData
15728 | PROVIDE AN HMIS FROM THE GUIDELINE PROVIDED. COMPLIANCE WITHIN 30 DAYS.
15729 | HAVE QUALIFIED ALARM COMPANY PERFORM ANNUAL TEST ON FIRE ALARM PANEL AND ANNUAL INSPECTION ON THE DRY CHEMICAL SYSTEM IN WAREHOUSE #28. COMPLIANCE WITHIN 30 DAYS.
15730 | LAST INSPECTION ON FIRE ALARM PANEL 11-19-2019
15731 | LAST EMERGENCY LIGHTING TEST FOUND IN FIRE MARSHAL BINDER----07-2016
15732 | LAST ANNUAL INSPECTION ON THE SPRINKLER SYSTEM-- 03-2018
15733 | NoData
15734 | Please identify the proper unit number on the outside of all electrical panels.
15735 | Please make sure all units have a type ABC portable fire extinguishers.
15736 | All units shall be provided a working smoke detector in all bedrooms and path of egress.
15737 | Gas test is required every 5 years by a licensed plumber.
15738 | Update fire safety plan and submit to inspector for approval.
15739 | 1) Add one standardized floor plan making a total of 3 sets per code. 2) Add top level re-entry to the elevator diagram per code.
15740 | Add one more elevator hoist way key making a total of two keys per code.
15741 | Cover junction box in fire pump room per code.
15742 | Go through electrical, and mechanical rooms and ensure fire rated resistance rating is maintained. Make additional corrections as needed per code.
15743 | Go through all stairways, electrical and mechanical rooms and ensure all fire doors close and latch from the open position per code.
15744 | Add one fire phone, making a total of 3 per code.
15745 | Install lock out tag out station so it is readily accessible.
15746 | HFC 901.6.2-RecordsFacility needs to provide inspector with the following report documents that show all systems have passed the appropriateinspection standards. If reports show test failure, all corrections to the system have to be performed prior to fire inspector signing off on safety survey. In addition to the test reports, provide a short letter from the fire protection equipment or life safety equipment service companies stating what testing / inspection was completed, whether or not the system is acceptable, red tagged, yellow tagged, or passed/failed. Do not provide billing invoices or checks paid. Long term deficiencies will require a letter of intent with a time line arrived at after consultation with the fire inspector. (Management shall obtain an acceptability letter for 3-5 year tests that do not have a letter currently on file).Certificate of Occupancy: Core of Building C of O onlyActive Fire Permits: Up to date and Paid.Fire Depository Box Keys Letter: A letter stating all Fire Depository Box keys work properly and have been checked for operation.Fire Marshal Training & Evacuation Letter: A letter stating all fire wardens, property management employees, staff and/or contract personnel have attended the proper training and building has conducted fire drills as per HFD Standards.Fire Alarm Permit: Sprinkler Percentage Letter and Form:Building System Test Documentation LSB # 2Electronic Locks-Semi AnnualSprinkler System- AnnualFire Alarm System Test- AnnualFire Extinguishers- AnnualFire Hoses- AnnualFire Pumps Flow Test- AnnualEmergency Power & Lighting- AnnualGenerator Test (ATS) - AnnualFire Alarm Audibility Test- 3 YearFire Hose Pressure Test- 3 yearFire Dampers- 4 YearFire Alarm Sensitivity- 5 YearFDC Test (Bldg. & Garage) - 5 YearPRV / PRD Test- 5 YearStair pressurization Test- 5 YearStandpipe System- 5 YearWater Supply Tank Inspection- 5 YearBoiler- PermitElevator-Annual PermitDry Partial or Full Trip TestGas Test- 5 YearCOMPLIANCE WITHIN 60 CALENDAR DAYS.
15747 | PERMITS - Permits the Inspector will be looking for are as follows:• Key Box Permit• Flammable and Combustible Permit• Fire Alarm Permit• Elevator Operating Permit• Boiler Permit• Other – Assembly, Access Gates, Batteries, etc.• Certificate of Occupancies• Fire Depository Box / Key Boxes• These are some but not all of the Permits available. • Present Permits that apply to facility Address listed • on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS.
15748 | LAST FIRE ALARM INSPECTION WAS ON 3-29-18. BRING UP TO CODE
15749 | LAST AUDIBILITY TEST WAS ON 5-10-17.THIS TEST IS EVERY 3 YEARS
15750 | LAST 5 YEAR HYDRO WAS DONE ON APRIL 2012. BRING UP TO CODE.
15751 | MAKE SURE EMERGENCY EVACUATION DIAGRAM IS POSTED IN EVERY ROOM NEXT TO EXIT DOOR
15752 | EXPIRES 5-8-20
15753 | FIRE ALARM PERMIT EXPIRED 1-9-20
15754 | LAST EMERGENCY LIGHTING TEST11-21-2019
15755 | LAST SPRINKLER RISER INSPECTION WAS DONE ON AUGUST 2018. BRING UP TO CODE.
15756 | LAST INSPECTION ON FIRE EXTINGUISHER 08-2019
15757 | NoData
15758 | Please renew both your access gate (a4) & key box (k1) permits with HPC office at 832-394-8811.
15759 | NoData
15760 | NoData
15761 | NoData
15762 | NoData
15763 | NoData
15764 | NoData
15765 | Replace the light cover in the gym storage room. - Led bulbs with shatter proof coatings are acceptable alternatives.
15766 | Make all code violation corrections prior to the re-inspection date noted on page 1 of the report.
15767 | Provide documentation for a current emergency egress light annual test.An approved licensed master electrician or licensed electrical service company shall test all emergency lighting systems annually. The battery units, whether of the acid or alkali type, shall be tested continuously for a minimum of 90 minutes.Failed devices shall be repaired or replaced as soon as possible. The test report / documentation shall have the date of the test, the master electrician, and/or company's certification number, and state that all devices passed the 90-minute test or if there were failed devices needing corrections.
15768 | Replace missing ceiling tiles where needed. - Office 1
15769 | Place a durable sign on the door leading to the fire alarm panel in office 1. Sign shall say "Fire Alarm Room"
15770 | - Apply for an assembly permit for Occupant load of 900. - Provide a current Fire Alarm Permit 1002 Washington - City of Houston Permitting Center
15771 | F-7 Permit is expired. Renew permit per code.
15772 | NoData
15773 | NoData
15774 | NoData
15775 | NoData
15776 | NoData
15777 | NoData
15778 | NoData
15779 | NoData
15780 | NoData
15781 | NoData
15782 | NoData
15783 | Have qualified sprinkler company address all red tag issues on your system near the pump house and bring the system back into compliance.Compliance by 4-30-2021
15784 | Last inspection 8/2020 - OK
15785 | Mount extinguishers in all classrooms (infant building)
15786 | Remove chains from perimeter gates.
15787 | Correct all violations within 30 calendar days.
15788 | Move diaper changing station that currently blocks pull station.
15789 | Correct/cover all open wiring splices (light ballasts).
15790 | Replace broken ceiling tile in classroom.
15791 | Evacuation maps OK
15792 | FACP showing ground fault/trouble. Return system to normal working status.
15793 | NoData
15794 | Failed to provide the report from the Fire Engineer to complete the inspection report.
15795 | NoData
15796 | NoData
15797 | NoData
15798 | ALL FIRE EXTINGUISHERS SHALL HAVE A CURRENT ANNUAL INSPECTION TAG BY AN APPROVED LICENSED FIRE PROTECTION EQUIPMENT COMPANY. COMPLIANCE WITHIN 30 DAYS.
15799 | Make sure that the LPG storage cabinet is locked and secured.Compliance within 30 days.
15800 | An annual and quarterly test of the fire suppression system must be performed and all deficiencies must be repaired or replaced. Approved tags must be affixed to the riser to indicating that the system is in operational readiness.Compliance within 30 days.
15801 | Fire alarm must tested and serviced annually by a licensed fire protection vendor.Compliance within 30 days.
15802 | A 5 year hydrostatic test must be performed on the suppression system. I was unable to find the 5 year tag with the most recent hydrostatic test performed within the past 5 years.Compliance within 30 days.
15803 | Aisle clearance and width must been maintained to for egress continuity.Compliance within 30 days.
15804 | Keys to give HFD access to the building must be placed in the 911 key box. During the follow up visit in 30 days, the keys will be tested and placed in key box.Compliance within 30 days.
15805 | NoData
15806 | NoData
15807 | Burgular Alarm permit is expired
15808 | There is too much artwork in the majority of the egress corridors because the decorative bulletin boards cover more than or near 50% of the walls. Downsize the boards to cover less than or equal to 20%.
15809 | An approved licensed master electrician or licensed electrical service company shall test all emergency lighting systems annually. The battery units, whether of the acid or alkali type, shall be tested continuously for a minimum of 90 minutes. Failed devices shall be corrected prior to the re-inspection. Provide dated documentation stating the master electrician and/or company's certification number, and that all devices passed the 90-minute test.
15810 | Keys needed for 911 Key boxes: - keys for gate doors near Rm114 and Rm100
15811 | Make all code violation corrections prior to the compliance date noted on page 1 of the report.
15812 | Make sure all yellow or red tags in the fire alarm panel box have a white tag or tags associated with them.
15813 | The ansul system semi-annual inspection is expired.
15814 | The K extinguisher tag is expired
15815 | Repair the intercom call buttons Rooms 331 and 332 according to the report
15816 | Remove combustible storage from all boiler rooms, mechanical rooms or electrical equipment rooms. - I.T. / Electrical room near the front reception desk- boxes and signs - Electrical / Custodial Room by the dumpsters - no storage allowed behind yellow line.
15817 | Extinguisher Hydro test log is needed in the Fire Marshal Binder
15818 | NoData
15819 | Remove the metal wired for the hanging decoration in the art room
15820 | Provide documentation that the college banner flags meet NFPA 701 requirements or remove the banner flags.
15821 | Evacuation Maps shall be posted in all areas normally occupied by students. The evacuation map should show: 1. You are Here 2. Primary evacuation route 3. Secondary evacuation route. The evacuation routes should be in two separate, distinguishable, and highly visible colors. The map should show a legend. Each Room shall have its own individual map. Review all rooms normally occupied by students, and ensure that they have a correct map posted.
15822 | Room 115 was locked and no key was available to open the room for inspection.
15823 | At least 1/2 Future fire alarms shall be of the obstructed kind.
15824 | Have all exit signs serviced and operable. Compliance within 30 days
15825 | NoData
15826 | NoData
15827 | Door to Electrical room must be labeled
15828 | COMPLIANCE DATE: 15 CALENDAR DAYS
15829 | AT THIS TIME YOUR (L1) FIRE PREVENTION PERMIT IS EXPIRED AND MUST BE UPDATED IMMEDIATELY.
15830 | NoData
15831 | NoData
15832 | NoData
15833 | Have exit signs serviced and operable.Compliance within 30 days.
15834 | Maintain a 3 ft. clearance from junction box and all electrical service equipment.Compliance within 30 days.
15835 | NoData
15836 | Failure to make corrections in timely manner
15837 | NoData
15838 | Building identification needs to be clearly marked on at least two sides - 1) End of building (North side) and 2) Road facing (West side)
15839 | Lock on failsafe box for automatic gate entrance not in compliance with a4 permit. Key for failsafe lock must be located in main gate keybox. Fire marshal must install this key - not accessible by client
15840 | Failure to make correction in a timely manner
15841 | NoData
15842 | Building identification needs to be clearly marked on at least two sides - 1) End of building (North side) and 2) Road facing (West side)
15843 | Lock on failsafe box for automatic gate entrance not in compliance with a4 permit. Key for failsafe lock must be located in main gate keybox. Fire marshal must install this key - not accessible by client
15844 | NoData
15845 | NoData
15846 | Fire watch agreement is needed while system is impaired/inoperable.
15847 | Have all open and exposed areas in junction box covered with approved covers.Compliance within 30 days.
15848 | All LP-gas cylinders must be secured in cabinet at all times.Compliance within 30 days.
15849 | NoData
15850 | NoData
15851 | NoData
15852 | NoData
15853 | NoData
15854 | NoData
15855 | The permit amount for oxidizing gas is &gt;504 cu. ft. on site. With 4 "H" bottles (2 oxygen, 2 nitrous) on site of min. 240 cu. ft. each, a C7: Compressed Gas annual operational permit must be obtained and posted on site(this is not a construction permit, but an operational permit that is required to be held by the occupant/business). Permits may be obtained at:Houston Fire Department's Permit Office1002 WashingtonHouston, Texas 77002832-394-8811www.houstonpermittingcenter.orgCompliance is required within 2 weeks: 3/19/2021
15856 | Tanks out of service must be properly safeguarded or removed in an approved manner.Compliance within 30 days.
15857 | NoData
15858 | Tanks not in use, within the past 30 days, must be safeguarded or removed in an approved manner.Compliance within 30 days.
15859 | NoData
15860 | NoData
15861 | NoData
15862 | NoData
15863 | All interior fire doors must be labeled both sides.FIRE DOOR - KEEP CLOSED
15864 | NoData
15865 | Fire alarm panel requires annual test. Last test date 2013
15866 | Test report of exit signs and exit lighting required
15867 | A number of exit signs in the building do not have a backup power source (battery) to maintain required illumination during power outage. Replace any signs not meeting specifications. Specifically found signs near units 382, 409, 411, 412, and 432. The given list is not exhaustive, all signs must be checked to ensure capability to remain lit. Also found a number of exit signs to be very weak or not working when testing. This will be addressed with required report. See 2.4.2.41/29/21 - light above A-395 not working
15868 | NoData
15869 | Test report of exits signs and exit lighting required
15870 | Please ensure all exit signs and lighting meet code
15871 | Exit directional arrow missing @ C-141
15872 | NoData
15873 | Test report of exit signs and exit lighting required
15874 | Please ensure all exit signs and lighting meet code
15875 | NoData
15876 | Test report of exit signs and exit lighting required
15877 | Please ensure all exit signs and lighting meet code
15878 | NoData
15879 | NoData
15880 | Ensure 3' clearance of all combustibles around electrical equipment/panels.
15881 | On both office exit doors place signage: This door to remain unlock while building is occupied.
15882 | Tori Chatagnier 713 600 4059
15883 | annual tag required. Relabel sprinkler cabinet sign.
15884 | provide access to pedestrian gate (key/codes/fob). place key in 911 keybox.
15885 | Show or obtain current k1 (keybox) permit
15886 | NoData
15887 | NoData
15888 | NoData
15889 | NoData
15890 | NoData
15891 | NoData
15892 | NoData
15893 | NoData
15894 | NoData
15895 | NoData
15896 | NoData
15897 | NoData
15898 | NoData
15899 | NoData
15900 | NoData
15901 | NoData
15902 | NoData
15903 | NoData
15904 | NoData
15905 | NoData
15906 | NoData
15907 | NoData
15908 | NoData
15909 | NoData
15910 | NoData
15911 | NoData
15912 | NoData
15913 | NoData
15914 | NoData
15915 | NoData
15916 | check all 1a:10bc fire extinguisher in all unit.
15917 | replace missing battery in smoke detector all unit
15918 | star epps 8326404444
15919 | replace unapproved lock on door.
15920 | Replace all metal inserts missing inside main electrical box in shop area
15921 | NoData
15922 | NoData
15923 | Remove all metal cans .tires and any other obstruction away from exit main door.
15924 | NoData
15925 | remove all trash and rubbish such as paper, plastics old tree branches wood boxes lumber and any other trash from permises
15926 | provide and install an emergency red box at entrance main gate along with a falcon lock and extra key from your gate lock
15927 | provide an approved metal can for the storage of gasoline U.L.or F.M. listed not over (5) gallons with out a permit. remove all unapproved plastic containers outside.
15928 | Label all electrical breakers in main electrical box
15929 | NoData
15930 | Apply for a certificate of occupancy from the bldg. dept 1002 Washington
15931 | provide and install on front door
15932 | provide and install a metal can for the storage of oily rags with a metal lid.
15933 | All doors shall be propertly identifide with the following words ,office storage room, rest rooms exc.
15934 | Apply for a flammable and combustible liquid permit type f7 from building department 10002 Washington fire permit section ,for the storage of waist oil over 60 gallons in one container.
15935 | Repair ASAP.
15936 | Repair ASAP.
15937 | NoData
15938 | NoData
15939 | NoData
15940 | NoData
15941 | NoData
15942 | NoData
15943 | NoData
15944 | NoData
15945 | NoData
15946 | NoData
15947 | NoData
15948 | Open junction boxes with wires exposed need to be covered.
15949 | Exit light needs to be repaired/replaced.
15950 | NoData
15951 | Compliance letter needed.
15952 | Steps to take for future yellow tags.
15953 | Sprinkler system, Fire alarm system, audibility test, sensitivity test, Fire Dampers, Fire pump flow test, Generator test, FDC, PRV, Stair pressurization test, Water supply tank inspection, and Gas Test.
15954 | Reminder: Adding a access key card.
15955 | Ceiling tiles need to be replaced.
15956 | Needs better identification to allow responding crews to easily find the door.
15957 | NoData
15958 | NoData
15959 | NoData
15960 | NoData
15961 | NoData
15962 | NoData
15963 | NoData
15964 | NoData
15965 | NoData
15966 | NoData
15967 | NoData
15968 | NoData
15969 | NoData
15970 | NoData
15971 | NoData
15972 | NoData
15973 | This is a general comment that is supposed to print out on the Expired Permit notification form. Entering this text to ensure that it works properly on the form.
15974 | NoData
15975 | NoData
15976 | Bedroom selections above???
15977 | Testing this violation to ensure that the comment prints off on the form and the notice.
15978 | The audibility tests required by code must be completed for alarms servicing the buildings addressed to 9254 and 9258 Park South View. If this service has already been completed, provide documentation from the alarm company. Any deficiencies identified during this maintenance must be corrected.
15979 | The 5 year hydrostatic maintenance must be completed for the system. All deficiencies found during this service must be corrected.
15980 | As required by code, the 5 year maintenance must be completed for the water tank in the pump room. Any deficiencies found during this service must be corrected.
15981 | The deficiencies requiring a yellow tag for the alarm panel servicing the building addressed to 9258, which is tied to the suppression system installed in building 9254, must be corrected.
15982 | Because there is an approved HAZMAT occupancy (H3) located in building 9254 Park South View, Suite 450 (Land N Sea), it is required that an alarm company technician be on-site during the alarm tests to ensure that the monitoring station is receiving a "Hazmat Alarm" signal and the Houston Fire Department is the responding agency for this signal, if the alarm is initiated from this suite.Documentation from the alarm company must be provided that the HAZMAT signal is being identified suite 450.
15983 | For Reference
15984 | The Hazardous Materials Management Plan included with this report must be filled out and stored in the Fire Department depository box in a weather proof packet.
15985 | Clearance in aisles must be maintained when not restocking. Ensure adequate aisle space is maintained.
15986 | Complete the HMIS included with this report to account for all Hazardous Materials on site.
15987 | The 3 year audibility testing is required for alarm panels located in building 2710, 2720 and 2730 Reed Rd. if this has been completed, a report from the alarm company may be sent for compliance. Any deficiencies noted during this maintenance must be corrected.
15988 | The alarm panel located in building 2720 Reed Rd has a 'TROUBLE' signal that must be addressed. Have any deficiencies restored for this system.Panels located in building 2710 and 2730 are in operational readiness condition.
15989 | FOR REFERENCE ONLY
15990 | All open wiring must be properly repaired.
15991 | Ceiling tiles and missing sheetrock by electrical room must be repaired or replaced as required by code.
15992 | Testing if this picture will print on report with the violation.
15993 | falcon locks are frozen and must be replaced. Unable to open properly.
15994 | NoData
15995 | comments for an expired permit. Making sure this prints on the permit renewal form
15996 | TEST AND REPAIR/REPLACE ALL EXIT SIGNS ENSURING ILLUMINATION ON BUILDING A/C POWER AS WELL AS BATTERY POWER WHEN THE TEAT BUTTON IS DEPRESSED.
15997 | EXTENSION CORDS ARE FOR USE WITH PORTABLE APPLIANCES AND SHALL NOT BE USED AS PERMANENT POWER. DISCONINUE USE OF EXTENSION CORDS EXCEPT FOR USE WITH PORTABLE APPLIANCES ONLY, ENSURING THEY ARE UNPLUGGED DAILY.
15998 | REMOVE ALL STORAGE FROM IN RONT OF THE ELECTRICAL PANELS ENSURING THAT THE ABOVE REFERENCED CLEARANCES ARE MAINTAINED.
15999 | RE-INSPECTION FEE ASSESSED DUE TO NON-COMPLIANCE WITH 30 DAY COMPLIANCE REQUIREMENT AS STIPULATED ON THE INITATIAL INSPECTION. FOLLOW UP IN 2 WKS.
16000 | TEST AND REPAIR/REPLACE ALL EXIT SIGNS ENSURING ILLUMINATION ON BUILDING A/C POWER AS WELL AS BATTERY POWER WHEN THE TEAT BUTTON IS DEPRESSED.
16001 | EXTENSION CORDS ARE FOR USE WITH PORTABLE APPLIANCES AND SHALL NOT BE USED AS PERMANENT POWER. DISCONINUE USE OF EXTENSION CORDS EXCEPT FOR USE WITH PORTABLE APPLIANCES ONLY, ENSURING THEY ARE UNPLUGGED DAILY.
16002 | REMOVE ALL STORAGE FROM IN RONT OF THE ELECTRICAL PANELS ENSURING THAT THE ABOVE REFERENCED CLEARANCES ARE MAINTAINED.
16003 | CITATION ISSUED FOR NON COMLIANCE WITH INSPECTION REPORT REQUIREMENTS, AS WELL AS FAILURE TO PAY RE-INSPECTION FEE.
16004 | TEST AND REPAIR/REPLACE ALL EXIT SIGNS ENSURING ILLUMINATION ON BUILDING A/C POWER AS WELL AS BATTERY POWER WHEN THE TEAT BUTTON IS DEPRESSED.
16005 | EXTENSION CORDS ARE FOR USE WITH PORTABLE APPLIANCES AND SHALL NOT BE USED AS PERMANENT POWER. DISCONINUE USE OF EXTENSION CORDS EXCEPT FOR USE WITH PORTABLE APPLIANCES ONLY, ENSURING THEY ARE UNPLUGGED DAILY.
16006 | REMOVE ALL STORAGE FROM IN RONT OF THE ELECTRICAL PANELS ENSURING THAT THE ABOVE REFERENCED CLEARANCES ARE MAINTAINED.
16007 | TEST AND REPAIR/REPLACE ALL EXIT SIGNS ENSURING ILLUMINATION ON BUILDING A/C POWER AS WELL AS BATTERY POWER WHEN THE TEAT BUTTON IS DEPRESSED.
16008 | REMOVE ALL STORAGE FROM IN RONT OF THE ELECTRICAL PANELS ENSURING THAT THE ABOVE REFERENCED CLEARANCES ARE MAINTAINED.
16009 | EXTENSION CORDS ARE FOR USE WITH PORTABLE APPLIANCES AND SHALL NOT BE USED AS PERMANENT POWER. DISCONINUE USE OF EXTENSION CORDS EXCEPT FOR USE WITH PORTABLE APPLIANCES ONLY, ENSURING THEY ARE UNPLUGGED DAILY.
16010 | TEST AND REPAIR/REPLACE ALL EXIT SIGNS ENSURING ILLUMINATION ON BUILDING A/C POWER AS WELL AS BATTERY POWER WHEN THE TEAT BUTTON IS DEPRESSED.
16011 | EXTENSION CORDS ARE FOR USE WITH PORTABLE APPLIANCES AND SHALL NOT BE USED AS PERMANENT POWER. DISCONINUE USE OF EXTENSION CORDS EXCEPT FOR USE WITH PORTABLE APPLIANCES ONLY, ENSURING THEY ARE UNPLUGGED DAILY.
16012 | REMOVE ALL STORAGE FROM IN RONT OF THE ELECTRICAL PANELS ENSURING THAT THE ABOVE REFERENCED CLEARANCES ARE MAINTAINED.
16013 | Make payment within 10 days to avoid additional fees and/ or citations.
16014 | NoData
16015 | MEMBERS OF THE FIRESAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR
16016 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR
16017 | Concerning fire drills during COVID-19, a link can befound by going to the "Resources" and then clicking on"Notices".https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/
16018 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL
16019 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS
16020 | Take the Fire Warden Certification class online through thefollowing link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottomto click on High-rise Fire Warden CertificationClass.Print out the certificate of completion and keep it in a safeplace where it can be accessed upon demand.
16021 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERALALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1
16022 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE
16023 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN
16024 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS, PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE
16025 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY
16026 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS, PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE
16027 | EVIDENCE OF INCOMPLETE ORNON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONINGSYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRECODE
16028 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED
16029 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED
16030 | NoData
16031 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
16032 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS
16033 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTIONFEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90DAYS
16034 | NoData
16035 | MEMBERS OF THE FIRESAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR
16036 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR
16037 | Concerning fire drills during COVID-19, a link can befound by going to the "Resources" and then clicking on"Notices".https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/
16038 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL
16039 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS
16040 | Take the Fire Warden Certification class online through thefollowing link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottomto click on High-rise Fire Warden CertificationClass.Print out the certificate of completion and keep it in a safeplace where it can be accessed upon demand.
16041 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERALALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1
16042 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE
16043 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN
16044 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS, PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE
16045 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY
16046 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS, PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE
16047 | EVIDENCE OF INCOMPLETE ORNON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONINGSYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRECODE
16048 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED
16049 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED
16050 | NoData
16051 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
16052 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS
16053 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTIONFEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90DAYS
16054 | NoData
16055 | MEMBERS OF THE FIRESAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATE SIGNED BY THE FIREMARSHAL OR AN APPROVED INSTRUCTOR
16056 | EACHMEMBER OF THE FIRE SAFETY TEAM (FIRE WARDENS) SHALL POSSESS A CERTIFICATESIGNED BY THE FIRE MARSHAL OR AN APPROVED INSTRUCTOR
16057 | Concerning fire drills during COVID-19, a link can befound by going to the "Resources" and then clicking on"Notices".https://www.houstonhighriseflst.org/conducting-fire-drills-during-covid-19-crisis/
16058 | HIGH-RISE SAFETY PLAN APPROVAL BY THE FIRECODE OFFICIAL IS DEPENDENTUPON SUCCESSFUL COMPLETION OF THREE COMPONENTS- CONSULTATION, CERTIFICATION OF ALL FIRE WARDENS AND COMPLETION OF ASUPERVISED FIRE DRILL
16059 | ATTENDANCEAT A HIGH-RISE CERTIFICATION CLASS IS REQUIRED FOR ALL HIGH-RISE FIRE WARDENS
16060 | Take the Fire Warden Certification class online through thefollowing link:https://www.houstonhighriseflst.org/Click on the link, they will to click on Courses and then scroll all the way to the bottomto click on High-rise Fire Warden CertificationClass.Print out the certificate of completion and keep it in a safeplace where it can be accessed upon demand.
16061 | APPROVALOF A FIRE SAFETY PLAN BY THE CODE OFFICIAL IS CONTINGENT UPON SUCCESSFULCOMPLETION OF SEVERALALL COMPONENTS; ONE OF WHICH IS THE SUBMISSION OF ACOMPLETED STANDARD FIRE SAFETY PLAN WITH AN ADEQUATE NUMBER OF TRAINED FIREWARDENS LISTED IN 18.4.1
16062 | THE CERTIFICATE OF COMPLETION OF FIREWARDEN TRAINING IS VALID FOR A PERIOD OF 5 YEARS FROM THE CLASS DATE
16063 | PLEASE CONTINUE TO CONDUCT FIRE DRILLS ANDKEEP A RECORD OF WHO DID/DID NOT PARTICIPATE. KEEP DOCUMENTATION FOR WHEN WEREVIEW AND DISCUSS IN THE NEAR FUTURE PLEASE SCAN AND SEND THE MOST RECENTAPPROVAL LETTER , FIRE WARDEN TRAINING LIST AND FIRE SAFETY PLAN
16064 | NOTIFICATION MUST BE MADE WHENEVER SYSTEMS (FIRE PROTECTION OR LIFE SAFETY ARE PLACED OUT OF SERVICE FOR EMERGENCY OR NON-SCHEDULED REPAIRS, REPLACEMENT, SERVICE OR FIRE DRILLS THE FIRE DEPARTMENT SHALL AGAIN BE NOTIFIED WHEN THE SYSTEM IS RESTORED TO NORMAL OPERATIONAL STATUS FYI PERTAINING TO INFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS, PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE
16065 | READ AND REVIEW LSB STANDARD 6;FULL COMPLIANCE OF PROVIDING A PROPERLYSUPPLIED FIRE DEPOSITORY BOXIS REQUIRED IMMEDIATELY
16066 | FYI PERTAINING TOINFORMATION NEEDED WHEN NOTIFYING HFD OEC DURING SYSTEM REPAIRS AND/OR SERVICE WHEN RE-ROOFING OR CONDUCTING ROOF REPAIRS, IMMEDIATELY NOTIFY INSPECTOR KIMBALL DIRECTLY AT 832.216.7574; FAILURE TO HAVE A STANDBY IN PLACE WHEN LPG IS ON SITE, OR OPEN FLAMES ARE PRESENT WILL RESULT IN CITATIONS TO THE BUILDING MANAGER, ENGINEER AND ROOFING COMPANY PERTAINING TO ROOF OPERATIONS ON HIGH-RISE BUILDINGS, PERMITS MAY BE NECESSARY. IF LPG IS TRANSPORTED THROUGH THE BUILDING OR IF TORCHES AND/OR TAR IS UTILIZED FOR ROOFING OPERATIONS, A STAND-BY MUST BE IN PLACE
16067 | EVIDENCE OF INCOMPLETE ORNON-FUNCTIONING SYSTEMS ON SITE MUST BE MAINTAINED OR REMOVED; ALL FUNCTIONINGSYSTEMS MUST BE MAINTAINED AND INSPECTED AT INTERVALS ACCORDING TO THE FIRECODE
16068 | SUBMIT A FIRE DEPOSITORY KEYBOX LETTER; THIS IS A LETTER STATING ALL KEYS / KEY FOBS / KEY CARDS IN THEFIRE DEPOSITORY BOX ARE CURRENT, WORK PROPERLY AND HAVE BEEN CHECKED FOR OPERATION;THIS LETTER MUST BE WRITTEN ON COMPANY LETTERHEAD AND SIGNED
16069 | FACILITY NEEDS TO PROVIDE INSPECTOR WITH THEFOLLOWING DOCUMENTS THAT SHOW ALL SYSTEMS HAVE PASSED THE APPROPRIATEINSPECTION STANDARDS. IF REPORTS INDICATE TEST FAILURE, ALL CORRECTIONS TO THESYSTEM MUST BE PERFORMED PRIOR TO THE FIRE INSPECTOR SIGNING OFF ON THEINSPECTION REPORT.PROVIDE A SHORT LETTER WRITTEN BY THE FIRE PROTECTION EQUIPMENT OR LIFESAFETY EQUIPMENT SERVICE COMPANIES STATING WHAT TESTING/INSPECTION WASCOMPLETED, WETHER OR NOT IT PASSED/IS ACCEPTABLE/BLUE TAGGED, RED TAGGED,YELLOWTAGGED OR FAILED. DO NOT PROVIDE TEST REPORTS, BILLING INVOICES OR CHECKS PAID. PERMITS FOR THE FIRE ALARM, ELEVATORS, BOILERS AND GAS TEST DO NOT REQUIREA LETTER – PROVIDE A PHOTOCOPY OF THESE PERMITS.Long term deficiencies will require a letter ofintent with a time line arrived at after consultation with the fireinspector. (Management shall obtain anacceptability letter for 3-5 year tests that do not have a letter currently onfile)."Certificate of Occupancy: Core of Building C of O only - REQUIRED"Active Fire Permits: Up to date and Paid - REQUIRED"Fire Depository Box Keys Letter: A letter stating all Fire DepositoryBox keys work properly and have been checked for operation - REQUIRED"Fire Marshal Training &amp; Evacuation Letter: A letter stating all firewardens, property management employees, staff and/or contract personnel haveattended the proper training and building has conducted fire drills as per HFDStandards - REQUIRED"Fire Alarm Permit - Annual -REQUIRED"Sprinkler Percentage Letter and Form (included in report) - REQUIRED"Electronic Locks -Semi Annual - REQUIRED"Sprinkler System - Annual - REQUIRED"Fire Alarm System Test - Annual - REQUIRED"Fire Extinguishers - Annual - REQUIRED"Fire Hoses – Annual - REQUIRED "Fire Pumps Flow Test - Annual - REQUIRED"Emergency Power &amp; Lighting - Annual - REQUIRED"Generator Test (ATS) - Annual - REQUIRED"Fire Alarm Audibility Test - 3 Year - REQUIRED"Fire Hose Pressure Test - 3 year - REQUIRED " Fire Dampers - 4 Year - REQUIRED"Fire Alarm Sensitivity - 2 Year - REQUIRED"FDC Test (Bldg. &amp; Garage) - 5 Year - REQUIRED"PRV / PRD Test - 5 Year - REQUIRED"Stair pressurization Test - 5 Year - REQUIRED"Standpipe System - 5 Year - REQUIRED"Water Supply Tank Inspection - 5 Year - REQUIRED"Boiler Permit – REQUIRED IF BOILER ON SITE "Elevator Permit - Annual - REQUIRED"Dry Partial or Full Trip Test - REQUIRED"Gas Test - 5 Year - REQUIRED IF GAS ON SITE"FireFighter Phones or Emergency Responder Radio Coverage - REQUIRED
16070 | NoData
16071 | YOUR ATTENTION IS RESPECTFULLY CALLED TOTHE VIOLATIONS OF THE PROVISIONS OF THE CITY OF HOUSTON FIRE CODE AS INDICATEDHEREIN, ON THE PREMISES LOCATED AT THE ADDRESS LISTED. THIS INSPECTION REPORTMAY NOT REVEAL ALL FIRE CODE VIOLATIONS. ADDITIONAL VIOLATIONS MAY BEDISCOVERED DURING SUBSEQUENT VISITS. THE ISSUANCE OF A FIRE INSPECTION REPORTIS NOT REQUIRED PRIOR TO THE ISSUANCE OF A CITATION, SUMMONS OR OTHERENFORCEMENT ACTION. THE FIRE INSPECTOR MAY ISSUE CITATIONS UPON ARRIVAL FORFIRE CODE VIOLATIONS THAT ARE AN IMMEDIATE LIFE SAFETY HAZARD
16072 | PERMITS THEINSPECTOR WILL BE LOOKING FOR ARE AS FOLLOWS:Key Box Permit -Flammable and Combustible Permit -Fire Alarm Permit -Elevator Operating Permit -Boiler Permit -Other – Assembly, Access Gates, Batteries, etc. -Certificate of Occupancies -Fire Depository Box Permit - These are some but not all of the Permits available. Present Permits that apply to facility Address listed on Notice. COMPLIANCE WITHIN 60 CALENDAR DAYS
16073 | CITATIONS WILL BE WRITTEN AFTER 2 REINSPECTIONFEES HAVE BEEN ASSESSED OR IF COMPLIANCE IS DISREGARDED OR NOT MET WITHIN 90DAYS
16074 | NoData
16075 | FOR REFERENCE ONLY
16076 | Ceiling tiles and missing sheetrock by electrical room must be repaired or replaced as required by code.
16077 | falcon locks are frozen and must be replaced. Unable to open properly.
16078 | All open wiring must be properly repaired.
16079 | Testing if this picture will print on report with the violation.
16080 | Testing the reinspection fee for this report to ensure that a fee is added and that the report and THIS commentary prints out correctly
16081 | TESTING THE REPORT PRINTOUT FOR VARIOUS ENTRIES OF TEST IN THE COMMENTARY FIELD:This is text that has be directly typed into the comments field for the violation. Spacing from the above heading, ALL CAPS, bolding test, underlining important information,and italicizing are all being utilized on this direct entry. Below "copy and paste" commentary is used.Below is a copy and pasted from a PDF (amendment) which is how we copy and paste from NFPA and various standards:404.2 Where required. When required by the fire code official, and where local fire marshal approvals are required by regulatory agencies, an approved fire safety and evacuation plan shall be prepared and maintained for the following occupancies and buildings.Below is the same PDF copy and paste - but it was put into NOTEPAD and then recopied and pasted404.2 Where required. When required by the fire code official, and where local fire marshal approvals are required by regulatory agencies, an approved fire safety and evacuation plan shall be prepared and maintained for the following occupancies and buildings.
16082 | This is a test violation to see an inspection all the way thru
16083 | Forgot this code existed. Should have included in my report for holmes road
16084 | NoData
16085 | NoData
16086 | NoData
16087 | NoData
16088 | NoData
16089 | NoData
16090 | NoData
16091 | NoData